## Cable
float | Shortname | Unom | Price | R | X | C | Tan_delta | R0 | X0 | C0 | Inom0 | G1 | Inom1 | G2 | Inom2 | G3 | Inom3 | Ik1s | TR | TInom | TIk1s | Frequency | VoP | Preference | R_C | X_C | R_CC_N | X_CC_N | R_CC_T | X_CC_T | R_E | X_E | R_CE | X_CE | R_H | X_H | R_CH_N | X_CH_N | R_CH_T | X_CH_T | R_HH_N | X_HH_N | R_HH_T | X_HH_T | R_HE | X_HE | Inom_E | Ik1s_E | Inom_H | Ik1s_H
|  | kV | EUR/m | Ohm/km | Ohm/km | µF/km |  | Ohm/km | Ohm/km | µF/km | A | Km/W | A | Km/W | A | Km/W | A | kA | °C | °C | °C | Hz | m/µs |  | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | Ohm/km | A | kA | A | kA
4* 50 VMvK/Alk | 50 Al | 0.75 | 16 | 0.641 | 0.085 | 0.54 | 0.07 | 2.56 | 0.3 | 0.32 | 105 | 0.5 | 135 | 0.75 | 125 | 1 | 115 | 4.2 | 20 | 55 | 160 | 50 | 150 | 0 | 0.6903 | 0.8314 | 0.0495 | 0.7561 | 0.0492 | 0.7343
4* 50 VMvKh/Alk 4*2,5 | 50 Al; 2,5 | 0.75 | 18 | 0.641 | 0.085 | 0.54 | 0.07 | 2.56 | 0.3 | 0.32 | 105 | 0.5 | 135 | 0.75 | 125 | 1 | 115 | 4.2 | 20 | 55 | 160 | 50 | 150 | 0 | 0.6904 | 0.8316 | 0.0495 | 0.7559 | 0.0492 | 0.7339 |  |  |  |  | 6.9825 | 0.9204 | 0.0497 | 0.7765 | 0.049 | 0.7256 | 0.0489 | 0.7316 | 0.0487 | 0.7099 |  |  |  |  | 36 | 0.44
4* 50 VMvKh/Alk 4*6 | 50 Al; 6 | 0.75 | 20 | 0.641 | 0.085 | 0.54 | 0.07 | 2.56 | 0.3 | 0.32 | 105 | 0.5 | 135 | 0.75 | 125 | 1 | 115 | 4.2 | 20 | 55 | 160 | 50 | 150 | 0 | 0.6904 | 0.8315 | 0.0495 | 0.7559 | 0.0492 | 0.7339 |  |  |  |  | 2.9395 | 0.8939 | 0.0497 | 0.7718 | 0.049 | 0.723 | 0.0489 | 0.7295 | 0.0487 | 0.7078 |  |  |  |  | 52 | 1.05
4* 95 VMvK/Alk | 95 Al | 0.75 | 20 | 0.32 | 0.082 | 0.66 | 0.07 | 1.28 | 0.29 | 0.4 | 165 | 0.5 | 215 | 0.75 | 195 | 1 | 180 | 7.9 | 20 | 55 | 160 | 50 | 150 | 0 | 0.3692 | 0.8128 | 0.0495 | 0.741 | 0.0488 | 0.7189
4* 95 VMvKh/Alk 4*2,5 | 95 Al; 2,5 | 0.75 | 22 | 0.32 | 0.082 | 0.66 | 0.07 | 1.28 | 0.29 | 0.4 | 165 | 0.5 | 215 | 0.75 | 195 | 1 | 180 | 7.9 | 20 | 55 | 160 | 50 | 150 | 0 | 0.3692 | 0.813 | 0.0495 | 0.7409 | 0.0488 | 0.7189 |  |  |  |  | 6.9838 | 0.9234 | 0.05 | 0.7612 | 0.0484 | 0.7105 | 0.0483 | 0.7164 | 0.0479 | 0.6947 |  |  |  |  | 36 | 0.44
4* 95 VMvKh/Alk 4*6 | 95 Al; 6 | 0.75 | 24 | 0.32 | 0.082 | 0.66 | 0.07 | 1.28 | 0.29 | 0.4 | 165 | 0.5 | 215 | 0.75 | 195 | 1 | 180 | 7.9 | 20 | 55 | 160 | 50 | 150 | 0 | 0.3692 | 0.8129 | 0.0495 | 0.7409 | 0.0488 | 0.7189 |  |  |  |  | 2.9413 | 0.8976 | 0.05 | 0.7632 | 0.0484 | 0.7116 | 0.0482 | 0.7183 | 0.0479 | 0.6966 |  |  |  |  | 52 | 1.05
4*150 VMvK/Alk | 150 Al | 0.75 | 25 | 0.206 | 0.079 | 0.72 | 0.07 | 0.82 | 0.28 | 0.43 | 220 | 0.5 | 285 | 0.75 | 255 | 1 | 235 | 12.5 | 20 | 55 | 160 | 50 | 150 | 0 | 0.255 | 0.8 | 0.0495 | 0.731 | 0.0484 | 0.7091
4*150 VMvKh/Alk 4*2,5 | 150 Al; 2,5 | 0.75 | 27 | 0.206 | 0.079 | 0.72 | 0.07 | 0.82 | 0.28 | 0.43 | 220 | 0.5 | 285 | 0.75 | 255 | 1 | 235 | 12.5 | 20 | 55 | 160 | 50 | 150 | 0 | 0.255 | 0.8001 | 0.0495 | 0.731 | 0.0484 | 0.7091 |  |  |  |  | 6.9857 | 0.923 | 0.0503 | 0.7497 | 0.0476 | 0.6997 | 0.0475 | 0.705 | 0.0468 | 0.6834 |  |  |  |  | 36 | 0.44
4*150 VMvKh/Alk 4*6 | 150 Al; 6 | 0.75 | 29 | 0.206 | 0.079 | 0.72 | 0.07 | 0.82 | 0.28 | 0.43 | 220 | 0.5 | 285 | 0.75 | 255 | 1 | 235 | 12.5 | 20 | 55 | 160 | 50 | 150 | 0 | 0.255 | 0.8 | 0.0495 | 0.731 | 0.0484 | 0.7091 |  |  |  |  | 2.9434 | 0.8985 | 0.0504 | 0.7526 | 0.0476 | 0.7014 | 0.0474 | 0.7077 | 0.0467 | 0.6861 |  |  |  |  | 52 | 1.05
4* 50 VVMvKsas/Alk | 50 Al | 0.75 | 18 | 0.641 | 0.085 | 0.54 | 0.07 | 1.64 | 0.15 | 0.32 | 110 | 0.5 | 140 | 0.75 | 130 | 1 | 120 | 4.3 | 20 | 55 | 160 | 50 | 150 | 0 | 0.6904 | 0.864 | 0.0496 | 0.7884 | 0.0489 | 0.7665 | 0.7426 | 0.7551 | 0.0495 | 0.7559 | [12 empty] | 100 | 3
4* 50 VVMvKhsas/Alk 4*2,5 | 50 Al; 2,5 | 0.75 | 20 | 0.641 | 0.085 | 0.54 | 0.07 | 1.64 | 0.15 | 0.32 | 110 | 0.5 | 140 | 0.75 | 130 | 1 | 120 | 4.3 | 20 | 55 | 160 | 50 | 150 | 0 | 0.6904 | 0.864 | 0.0496 | 0.7885 | 0.0489 | 0.7664 | 0.7426 | 0.755 | 0.0495 | 0.7559 | 6.9839 | 0.9528 | 0.0504 | 0.809 | 0.0486 | 0.7582 | 0.049 | 0.7642 | 0.048 | 0.7426 | 0.0495 | 0.7559 | 100 | 3 | 36 | 0.44
4* 50 VVMvKhsas/Alk 4*6 | 50 Al; 6 | 0.75 | 22 | 0.641 | 0.085 | 0.54 | 0.07 | 1.64 | 0.15 | 0.32 | 110 | 0.5 | 140 | 0.75 | 130 | 1 | 120 | 4.3 | 20 | 55 | 160 | 50 | 150 | 0 | 0.6904 | 0.8639 | 0.0497 | 0.7885 | 0.0489 | 0.7665 | 0.7426 | 0.7551 | 0.0495 | 0.7559 | 2.9411 | 0.9259 | 0.0504 | 0.8042 | 0.0486 | 0.7556 | 0.049 | 0.76 | 0.0479 | 0.7384 | 0.0495 | 0.7559 | 100 | 3 | 52 | 1.05
4* 95 VVMvKsas/Alk | 95 Al | 0.75 | 23 | 0.32 | 0.082 | 0.66 | 0.07 | 0.91 | 0.15 | 0.4 | 170 | 0.5 | 220 | 0.75 | 200 | 1 | 185 | 6 | 20 | 55 | 160 | 50 | 150 | 0 | 0.3692 | 0.8413 | 0.0499 | 0.7695 | 0.0485 | 0.7475 | 0.5446 | 0.7401 | 0.0495 | 0.7409 | [12 empty] | 150 | 4.2
4* 95 VVMvKhsas/Alk 4*2,5 | 95 Al; 2,5 | 0.75 | 25 | 0.32 | 0.082 | 0.66 | 0.07 | 0.91 | 0.15 | 0.4 | 170 | 0.5 | 220 | 0.75 | 200 | 1 | 185 | 6 | 20 | 55 | 160 | 50 | 150 | 0 | 0.3692 | 0.8413 | 0.0499 | 0.7695 | 0.0485 | 0.7475 | 0.5446 | 0.7402 | 0.0495 | 0.7409 | 6.9862 | 0.9507 | 0.0512 | 0.7895 | 0.048 | 0.7391 | 0.0485 | 0.7449 | 0.0468 | 0.7234 | 0.0495 | 0.7409 | 150 | 4.2 | 36 | 0.44
4* 95 VVMvKhsas/Alk 4*6 | 95 Al; 6 | 0.75 | 27 | 0.32 | 0.082 | 0.66 | 0.07 | 0.91 | 0.15 | 0.4 | 170 | 0.5 | 220 | 0.75 | 200 | 1 | 185 | 6 | 20 | 55 | 160 | 50 | 150 | 0 | 0.3693 | 0.8413 | 0.0499 | 0.7695 | 0.0485 | 0.7475 | 0.5446 | 0.7402 | 0.0495 | 0.7409 | 2.9435 | 0.9256 | 0.0512 | 0.7916 | 0.048 | 0.7402 | 0.0485 | 0.7469 | 0.0468 | 0.7254 | 0.0495 | 0.7409 | 150 | 4.2 | 52 | 1.05
4*150 VVMvKsas/Alk | 150 Al | 0.75 | 29 | 0.206 | 0.079 | 0.72 | 0.07 | 0.6 | 0.15 | 0.43 | 225 | 0.5 | 290 | 0.75 | 260 | 1 | 240 | 8.5 | 20 | 55 | 160 | 50 | 150 | 0 | 0.2553 | 0.8266 | 0.0501 | 0.7583 | 0.0481 | 0.7367 | 0.3961 | 0.7303 | 0.0495 | 0.731 | [12 empty] | 200 | 6
4*150 VVMvKhsas/Alk 4*2,5 | 150 Al; 2,5 | 0.75 | 31 | 0.206 | 0.079 | 0.72 | 0.07 | 0.6 | 0.15 | 0.43 | 225 | 0.5 | 290 | 0.75 | 260 | 1 | 240 | 8.5 | 20 | 55 | 160 | 50 | 150 | 0 | 0.2553 | 0.827 | 0.0501 | 0.7582 | 0.048 | 0.7365 | 0.396 | 0.7302 | 0.0495 | 0.731 | 6.9895 | 0.9496 | 0.0523 | 0.7766 | 0.047 | 0.7271 | 0.0479 | 0.7323 | 0.0451 | 0.711 | 0.0495 | 0.731 | 200 | 6 | 36 | 0.44
4*150 VVMvKhsas/Alk 4*6 | 150 Al; 6 | 0.75 | 33 | 0.206 | 0.079 | 0.72 | 0.07 | 0.6 | 0.15 | 0.43 | 225 | 0.5 | 290 | 0.75 | 260 | 1 | 240 | 8.5 | 20 | 55 | 160 | 50 | 150 | 0 | 0.2554 | 0.827 | 0.0501 | 0.7582 | 0.048 | 0.7365 | 0.396 | 0.7302 | 0.0495 | 0.731 | 2.9469 | 0.9247 | 0.0523 | 0.7796 | 0.0471 | 0.7288 | 0.0478 | 0.735 | 0.0452 | 0.7137 | 0.0495 | 0.731 | 200 | 6 | 52 | 1.05
4*240 VVMvKsas/Alk | 240 Al | 0.75 | 36 | 0.129 | 0.073 | 0.78 | 0.07 | 0.4 | 0.15 | 0.46 | 285 | 0.5 | 365 | 0.75 | 330 | 1 | 300 | 15 | 20 | 55 | 160 | 50 | 150 | 0 | 0.17 | 0.81 | 0.05 | 0.75 | 0.048 | 0.73 | 0.27 | 0.72 | 0.0495 | 0.72 | [12 empty] | 250 | 9
4*240 VVMvKhsas/Alk 4*6 | 240 Al; 6 | 0.75 | 40 | 0.129 | 0.073 | 0.78 | 0.07 | 0.4 | 0.15 | 0.46 | 285 | 0.5 | 365 | 0.75 | 330 | 1 | 300 | 15 | 20 | 55 | 160 | 50 | 150 | 0 | 0.17 | 0.81 | 0.05 | 0.75 | 0.048 | 0.73 | 0.27 | 0.72 | 0.0495 | 0.72 | 2.9469 | 0.9247 | 0.0523 | 0.7796 | 0.0471 | 0.7288 | 0.0478 | 0.735 | 0.0452 | 0.7137 | 0.0495 | 0.731 | 250 | 9 | 52 | 1.05
4* 50 VGVMvK/Alk | 50 Al | 0.75 | 16 | 0.641 | 0.085 | 0.54 | 0.07 | 2.56 | 0.3 | 0.32 | 115 | 0.5 | 150 | 0.75 | 135 | 1 | 125 | 4.2 | 20 | 55 | 160 | 50 | 150 | 0 | 0.6903 | 0.8314 | 0.0495 | 0.7561 | 0.0492 | 0.7343
4* 50 VGVMvKh/Alk 4*2,5 | 50 Al; 2,5 | 0.75 | 18 | 0.641 | 0.085 | 0.54 | 0.07 | 2.56 | 0.3 | 0.32 | 115 | 0.5 | 150 | 0.75 | 135 | 1 | 125 | 4.2 | 20 | 55 | 160 | 50 | 150 | 0 | 0.6904 | 0.8316 | 0.0495 | 0.7559 | 0.0492 | 0.7339 |  |  |  |  | 6.9825 | 0.9204 | 0.0497 | 0.7765 | 0.049 | 0.7256 | 0.0489 | 0.7316 | 0.0487 | 0.7099 |  |  |  |  | 36 | 0.44
4* 50 VGVMvKh/Alk 4*6 | 50 Al; 6 | 0.75 | 20 | 0.641 | 0.085 | 0.54 | 0.07 | 2.56 | 0.3 | 0.32 | 115 | 0.5 | 150 | 0.75 | 135 | 1 | 125 | 4.2 | 20 | 55 | 160 | 50 | 150 | 0 | 0.6904 | 0.8315 | 0.0495 | 0.7559 | 0.0492 | 0.7339 |  |  |  |  | 2.9395 | 0.8939 | 0.0497 | 0.7718 | 0.049 | 0.723 | 0.0489 | 0.7295 | 0.0487 | 0.7078 |  |  |  |  | 52 | 1.05
4* 95 VGVMvK/Alk | 95 Al | 0.75 | 20 | 0.32 | 0.082 | 0.66 | 0.07 | 1.28 | 0.29 | 0.4 | 175 | 0.5 | 230 | 0.75 | 210 | 1 | 195 | 7.9 | 20 | 55 | 160 | 50 | 150 | 0 | 0.3692 | 0.8128 | 0.0495 | 0.741 | 0.0488 | 0.7189
4* 95 VGVMvKh/Alk 4*2,5 | 95 Al; 2,5 | 0.75 | 22 | 0.32 | 0.082 | 0.66 | 0.07 | 1.28 | 0.29 | 0.4 | 175 | 0.5 | 230 | 0.75 | 210 | 1 | 195 | 7.9 | 20 | 55 | 160 | 50 | 150 | 0 | 0.3692 | 0.813 | 0.0495 | 0.7409 | 0.0488 | 0.7189 |  |  |  |  | 6.9838 | 0.9234 | 0.05 | 0.7612 | 0.0484 | 0.7105 | 0.0483 | 0.7164 | 0.0479 | 0.6947 |  |  |  |  | 36 | 0.44
4* 95 VGVMvKh/Alk 4*6 | 95 Al; 6 | 0.75 | 24 | 0.32 | 0.082 | 0.66 | 0.07 | 1.28 | 0.29 | 0.4 | 175 | 0.5 | 230 | 0.75 | 210 | 1 | 195 | 7.9 | 20 | 55 | 160 | 50 | 150 | 0 | 0.3692 | 0.8129 | 0.0495 | 0.7409 | 0.0488 | 0.7189 |  |  |  |  | 2.9413 | 0.8976 | 0.05 | 0.7632 | 0.0484 | 0.7116 | 0.0482 | 0.7183 | 0.0479 | 0.6966 |  |  |  |  | 52 | 1.05
4*150 VGVMvK/Alk | 150 Al | 0.75 | 25 | 0.206 | 0.079 | 0.72 | 0.07 | 0.82 | 0.28 | 0.43 | 230 | 0.5 | 300 | 0.75 | 270 | 1 | 250 | 12.5 | 20 | 55 | 160 | 50 | 150 | 0 | 0.255 | 0.8 | 0.0495 | 0.731 | 0.0484 | 0.7091
4*150 VGVMvKh/Alk 4*2,5 | 150 Al; 2,5 | 0.75 | 27 | 0.206 | 0.079 | 0.72 | 0.07 | 0.82 | 0.28 | 0.43 | 230 | 0.5 | 300 | 0.75 | 270 | 1 | 250 | 12.5 | 20 | 55 | 160 | 50 | 150 | 0 | 0.255 | 0.8001 | 0.0495 | 0.731 | 0.0484 | 0.7091 |  |  |  |  | 6.9857 | 0.923 | 0.0503 | 0.7497 | 0.0476 | 0.6997 | 0.0475 | 0.705 | 0.0468 | 0.6834 |  |  |  |  | 36 | 0.44
4*150 VGVMvKh/Alk 4*6 | 150 Al; 6 | 0.75 | 29 | 0.206 | 0.079 | 0.72 | 0.07 | 0.82 | 0.28 | 0.43 | 230 | 0.5 | 300 | 0.75 | 270 | 1 | 250 | 12.5 | 20 | 55 | 160 | 50 | 150 | 0 | 0.255 | 0.8 | 0.0495 | 0.731 | 0.0484 | 0.7091 |  |  |  |  | 2.9434 | 0.8985 | 0.0504 | 0.7526 | 0.0476 | 0.7014 | 0.0474 | 0.7077 | 0.0467 | 0.6861 |  |  |  |  | 52 | 1.05
4* 16 VGVMvKas/Alk | 16 Al | 0.75 | 8 | 1.91 | 0.096 | 0.43 | 0.07 | 4.65 | 0.16 | 0.26 | 60 | 0.5 | 75 | 0.75 | 70 | 1 | 65 | 1.3 | 20 | 55 | 160 | 50 | 150 | 0 | 1.9531 | 0.8962 | 0.0495 | 0.814 | 0.0493 | 0.7923 | 1.8096 | 0.7758 | 0.0495 | 0.7766 | [12 empty] | 50 | 1.5
4* 16 VGVMvKhas/Alk 4*1,5 | 16 Al; 1,5 | 0.75 | 10 | 1.91 | 0.096 | 0.43 | 0.07 | 4.65 | 0.16 | 0.26 | 60 | 0.5 | 75 | 0.75 | 70 | 1 | 65 | 1.3 | 20 | 55 | 160 | 50 | 150 | 0 | 1.953 | 0.8963 | 0.0495 | 0.814 | 0.0493 | 0.7923 | 1.8096 | 0.7758 | 0.0495 | 0.7766 | 11.6027 | 0.9696 | 0.0498 | 0.837 | 0.0493 | 0.7861 | 0.0494 | 0.7937 | 0.0491 | 0.772 | 0.0495 | 0.7765 | 50 | 1.5 | 20 | 0.26
4* 50 VGVMvKas/Alk | 50 Al | 0.75 | 18 | 0.641 | 0.085 | 0.54 | 0.07 | 1.65 | 0.15 | 0.32 | 115 | 0.5 | 150 | 0.75 | 135 | 1 | 125 | 4.3 | 20 | 55 | 160 | 50 | 150 | 0 | 0.6898 | 0.8615 | 0.0496 | 0.7833 | 0.0488 | 0.7616 | 0.7509 | 0.7592 | 0.0495 | 0.7601 | [12 empty] | 100 | 3
4* 50 VGVMvKhas/Alk 4*2,5 | 50 Al; 2,5 | 0.75 | 20 | 0.641 | 0.085 | 0.54 | 0.07 | 1.65 | 0.15 | 0.32 | 115 | 0.5 | 150 | 0.75 | 135 | 1 | 125 | 4.3 | 20 | 55 | 160 | 50 | 150 | 0 | 0.6898 | 0.8615 | 0.0496 | 0.7833 | 0.0488 | 0.7616 | 0.7509 | 0.7593 | 0.0495 | 0.7601 | 6.9847 | 0.9541 | 0.0505 | 0.806 | 0.0486 | 0.7552 | 0.0491 | 0.7625 | 0.048 | 0.7409 | 0.0495 | 0.7601 | 100 | 3 | 36 | 0.44
GPLK 4*6 Curm | 6 Cu | 0.75 | 3 | 3.061 | 0.1 | 0.2 | 0.003 | 7.82 | 0.18 | 0.12 | 35 | 0.5 | 55 | 0.75 | 52 | 1 | 50 | 0.7 | 20 | 55 | 160 | 50 | 167 | 0 | 3.1107 | 0.92439 | 0.04947 | 0.83081 | 0.04935 | 0.80922 | 3.3426 | 0.79779 | 0.04947 | 0.79983 | [12 empty] | 21 | 1.7
GPLKh 4*6 Curm 4*1 | 6 Cu; 1 | 0.75 | 4 | 3.061 | 0.1 | 0.2 | 0.003 | 7.82 | 0.18 | 0.12 | 35 | 0.5 | 55 | 0.75 | 52 | 1 | 50 | 0.7 | 20 | 55 | 160 | 50 | 167 | 0 | 3.1107 | 0.92439 | 0.04948 | 0.83103 | 0.04935 | 0.80919 | 3.3426 | 0.79785 | 0.04947 | 0.79983 | 17.3907 | 0.97965 | 0.04961 | 0.85025 | 0.04935 | 0.8008 | 0.04945 | 0.80693 | 0.04921 | 0.78506 | 0.04947 | 0.79992 | 21 | 1.7 | 15 | 0.18
GPLKh 4*6 Curm 4*2,5 | 6 Cu; 2,5 | 0.75 | 5 | 3.061 | 0.1 | 0.2 | 0.003 | 7.82 | 0.18 | 0.12 | 35 | 0.5 | 55 | 0.75 | 52 | 1 | 50 | 0.7 | 20 | 55 | 160 | 50 | 167 | 0 | 3.1107 | 0.92439 | 0.04948 | 0.83103 | 0.04936 | 0.80919 | 3.3426 | 0.79782 | 0.04947 | 0.79983 | 6.9824 | 0.95163 | 0.04962 | 0.85025 | 0.04935 | 0.8008 | 0.04945 | 0.80693 | 0.04921 | 0.78503 | 0.04947 | 0.79992 | 21 | 1.7 | 48 | 0.44
GPLK 4*10 Curm | 10 Cu | 0.75 | 7 | 1.837 | 0.088 | 0.277 | 0.003 | 5.22 | 0.19 | 0.17 | 47 | 0.5 | 75 | 0.75 | 70 | 1 | 65 | 1.3 | 20 | 55 | 160 | 50 | 167 | 0 | 1.8863 | 0.90965 | 0.04949 | 0.82231 | 0.04933 | 0.80054 | 2.9705 | 0.7918 | 0.04947 | 0.79284 | [12 empty] | 24 | 2
GPLKh 4*10 Curm 4*2,5 | 10 Cu; 2,5 | 0.75 | 9 | 1.837 | 0.088 | 0.277 | 0.003 | 5.22 | 0.19 | 0.17 | 47 | 0.5 | 75 | 0.75 | 70 | 1 | 65 | 1.3 | 20 | 55 | 160 | 50 | 167 | 0 | 1.8863 | 0.90961 | 0.0495 | 0.82231 | 0.04934 | 0.80057 | 2.9705 | 0.79184 | 0.04947 | 0.79284 | 6.9825 | 0.95278 | 0.04966 | 0.84147 | 0.04933 | 0.79206 | 0.04946 | 0.79806 | 0.04915 | 0.77635 | 0.04947 | 0.79284 | 24 | 2 | 48 | 0.44
GPLK 4*16 Curm | 16 Cu | 0.75 | 9 | 1.148 | 0.079 | 0.35 | 0.003 | 3.6 | 0.21 | 0.21 | 62 | 0.5 | 100 | 0.75 | 92 | 1 | 85 | 2.1 | 20 | 55 | 160 | 50 | 167 | 0 | 1.1977 | 0.89499 | 0.04951 | 0.81268 | 0.04929 | 0.79091 | 2.8676 | 0.78852 | 0.04947 | 0.78962 | [12 empty] | 25 | 2.1
GPLKh 4*16 Curm 4*2,5 | 16 Cu; 2,5 | 0.75 | 11 | 1.148 | 0.079 | 0.35 | 0.003 | 3.6 | 0.21 | 0.21 | 62 | 0.5 | 100 | 0.75 | 92 | 1 | 85 | 2.1 | 20 | 55 | 160 | 50 | 167 | 0 | 1.1977 | 0.89502 | 0.04952 | 0.81265 | 0.04929 | 0.79091 | 2.8676 | 0.78852 | 0.04947 | 0.78962 | 6.9826 | 0.95298 | 0.04972 | 0.83577 | 0.04931 | 0.78472 | 0.04946 | 0.79226 | 0.0491 | 0.77052 | 0.04946 | 0.78946 | 25 | 2.1 | 48 | 0.44
GPLK 4*25 Curm | 25 Cu | 0.75 | 14 | 0.726 | 0.076 | 0.47 | 0.003 | 2.38 | 0.21 | 0.28 | 84 | 0.5 | 135 | 0.75 | 125 | 1 | 115 | 3.3 | 20 | 55 | 160 | 50 | 167 | 0 | 0.77553 | 0.875 | 0.04955 | 0.79806 | 0.04924 | 0.77632 | 2.3414 | 0.77425 | 0.04947 | 0.7756 | [12 empty] | 36 | 3
GPLKh 4*25 Curm 4*2,5 | 25 Cu; 2,5 | 0.75 | 16 | 0.726 | 0.076 | 0.47 | 0.003 | 2.38 | 0.21 | 0.28 | 84 | 0.5 | 135 | 0.75 | 125 | 1 | 115 | 3.3 | 20 | 55 | 160 | 50 | 167 | 0 | 0.77554 | 0.87497 | 0.04955 | 0.79809 | 0.04925 | 0.77629 | 2.3414 | 0.77422 | 0.04947 | 0.7756 | 6.9828 | 0.95247 | 0.04982 | 0.81977 | 0.04927 | 0.76922 | 0.04946 | 0.77607 | 0.04896 | 0.75449 | 0.04947 | 0.77563 | 36 | 3 | 48 | 0.44
GPLK 4*35 Cusvm | 35 Cu | 0.75 | 18 | 0.532 | 0.074 | 0.54 | 0.003 | 1.8 | 0.21 | 0.32 | 100 | 0.5 | 160 | 0.75 | 145 | 1 | 135 | 4.6 | 20 | 55 | 160 | 50 | 167 | 0 | 0.58154 | 0.86488 | 0.0496 | 0.79256 | 0.0492 | 0.77079 | 2.0438 | 0.76951 | 0.04947 | 0.77076 | [12 empty] | 40 | 3.2
GPLKh 4*35 Cusvm 4*2,5 | 35 Cu; 2,5 | 0.75 | 20 | 0.532 | 0.074 | 0.54 | 0.003 | 1.8 | 0.21 | 0.32 | 100 | 0.5 | 160 | 0.75 | 145 | 1 | 135 | 4.6 | 20 | 55 | 160 | 50 | 167 | 0 | 0.58154 | 0.86488 | 0.04961 | 0.7926 | 0.0492 | 0.77082 | 2.0438 | 0.76951 | 0.04947 | 0.77076 | 6.983 | 0.95272 | 0.04993 | 0.81295 | 0.04925 | 0.763 | 0.04947 | 0.76944 | 0.04882 | 0.74777 | 0.04947 | 0.77079 | 40 | 3.2 | 48 | 0.44
GPLKh 4*35 Cusvm 4*6 | 35 Cu; 6 | 0.75 | 24 | 0.532 | 0.074 | 0.54 | 0.003 | 1.8 | 0.21 | 0.32 | 100 | 0.5 | 160 | 0.75 | 145 | 1 | 135 | 4.6 | 20 | 55 | 160 | 50 | 167 | 0 | 0.58158 | 0.86488 | 0.04962 | 0.7926 | 0.04921 | 0.77082 | 2.0438 | 0.76951 | 0.04947 | 0.77076 | 2.9384 | 0.92586 | 0.04994 | 0.81295 | 0.04925 | 0.763 | 0.04947 | 0.76944 | 0.04882 | 0.74777 | 0.04947 | 0.77079 | 40 | 3.2 | 58 | 1.06
GPLK 4*50 Cusvm | 50 Cu | 0.75 | 25 | 0.387 | 0.072 | 0.61 | 0.003 | 1.3 | 0.19 | 0.37 | 125 | 0.5 | 190 | 0.75 | 175 | 1 | 160 | 6.5 | 20 | 55 | 160 | 50 | 167 | 0 | 0.4362 | 0.84668 | 0.04962 | 0.77886 | 0.04891 | 0.75652 | 1.5058 | 0.76095 | 0.04947 | 0.76208 | [12 empty] | 49 | 4
GPLKh 4*50 Cusvm 4*6 | 50 Cu; 6 | 0.75 | 29 | 0.387 | 0.072 | 0.61 | 0.003 | 1.3 | 0.19 | 0.37 | 125 | 0.5 | 190 | 0.75 | 175 | 1 | 160 | 6.5 | 20 | 55 | 160 | 50 | 167 | 0 | 0.43623 | 0.84672 | 0.04963 | 0.77889 | 0.04892 | 0.75649 | 1.5058 | 0.76089 | 0.04947 | 0.76208 | 2.9388 | 0.92604 | 0.05017 | 0.80198 | 0.04905 | 0.7497 | 0.04942 | 0.75668 | 0.04841 | 0.73497 | 0.04947 | 0.76214 | 49 | 4 | 58 | 1.06
GPLK 4*70 Cusvm | 70 Cu | 0.75 | 32 | 0.269 | 0.07 | 0.63 | 0.003 | 0.94 | 0.19 | 0.38 | 155 | 0.5 | 240 | 0.75 | 220 | 1 | 200 | 9.1 | 20 | 55 | 160 | 50 | 167 | 0 | 0.31797 | 0.83811 | 0.04974 | 0.77537 | 0.04881 | 0.75325 | 1.3369 | 0.75699 | 0.04947 | 0.75815 | [12 empty] | 55 | 4.5
GPLKh 4*70 Cusvm 4*6 | 70 Cu; 6 | 0.75 | 36 | 0.269 | 0.07 | 0.63 | 0.003 | 0.94 | 0.19 | 0.38 | 155 | 0.5 | 240 | 0.75 | 220 | 1 | 200 | 9.1 | 20 | 55 | 160 | 50 | 167 | 0 | 0.318 | 0.83817 | 0.04975 | 0.77531 | 0.04882 | 0.75316 | 1.3369 | 0.75696 | 0.04947 | 0.75815 | 2.9392 | 0.92604 | 0.0504 | 0.79617 | 0.04901 | 0.74471 | 0.04943 | 0.75058 | 0.04805 | 0.72903 | 0.04947 | 0.75815 | 55 | 4.5 | 58 | 1.06
GPLK 4*95 Cusvm | 95 Cu | 0.75 | 36 | 0.195 | 0.069 | 0.64 | 0.003 | 0.7 | 0.19 | 0.38 | 190 | 0.5 | 290 | 0.75 | 265 | 1 | 240 | 12.4 | 20 | 55 | 160 | 50 | 167 | 0 | 0.2451 | 0.82859 | 0.04987 | 0.76736 | 0.04861 | 0.74531 | 1.1307 | 0.7498 | 0.04947 | 0.75096 | [12 empty] | 66 | 5.4
GPLKh 4*95 Cusvm 4*6 | 95 Cu; 6 | 0.75 | 40 | 0.195 | 0.069 | 0.64 | 0.003 | 0.7 | 0.19 | 0.38 | 190 | 0.5 | 290 | 0.75 | 265 | 1 | 240 | 12.4 | 20 | 55 | 160 | 50 | 167 | 0 | 0.24793 | 0.82859 | 0.04987 | 0.76727 | 0.04861 | 0.74528 | 1.1307 | 0.74987 | 0.04947 | 0.75096 | 2.9397 | 0.92586 | 0.05072 | 0.7876 | 0.04888 | 0.73651 | 0.04943 | 0.74223 | 0.04758 | 0.72065 | 0.04947 | 0.75093 | 66 | 5.4 | 58 | 1.06
GPLK 4*120 Cusvm | 120 Cu | 0.75 | 41 | 0.152 | 0.069 | 0.69 | 0.003 | 0.55 | 0.19 | 0.41 | 220 | 0.5 | 330 | 0.75 | 300 | 1 | 275 | 15.6 | 20 | 55 | 160 | 50 | 167 | 0 | 0.20135 | 0.82025 | 0.04996 | 0.75833 | 0.04833 | 0.73625 | 0.90582 | 0.74196 | 0.04947 | 0.743 | [12 empty] | 83 | 6.8
GPLKh 4*120 Cusvm 4*6 | 120 Cu; 6 | 0.75 | 45 | 0.152 | 0.069 | 0.69 | 0.003 | 0.55 | 0.19 | 0.41 | 220 | 0.5 | 330 | 0.75 | 300 | 1 | 275 | 15.6 | 20 | 55 | 160 | 50 | 167 | 0 | 0.20135 | 0.82019 | 0.04996 | 0.75833 | 0.04834 | 0.73625 | 0.90582 | 0.74193 | 0.04947 | 0.743 | 2.9402 | 0.92584 | 0.05107 | 0.77947 | 0.04871 | 0.72805 | 0.04942 | 0.73411 | 0.04711 | 0.71265 | 0.04947 | 0.743 | 83 | 6.8 | 58 | 1.06
GPLK 4*150 Cusvm | 150 Cu | 0.75 | 45 | 0.125 | 0.068 | 0.75 | 0.003 | 0.45 | 0.19 | 0.45 | 255 | 0.5 | 375 | 0.75 | 340 | 1 | 310 | 19.5 | 20 | 55 | 160 | 50 | 167 | 0 | 0.17415 | 0.81303 | 0.05008 | 0.75208 | 0.04812 | 0.73009 | 0.79257 | 0.73628 | 0.04947 | 0.73728 | [12 empty] | 96 | 7.8
GPLKh 4*150 Cusvm 4*6 | 150 Cu; 6 | 0.75 | 49 | 0.125 | 0.068 | 0.75 | 0.003 | 0.45 | 0.19 | 0.45 | 255 | 0.5 | 375 | 0.75 | 340 | 1 | 310 | 19.5 | 20 | 55 | 160 | 50 | 167 | 0 | 0.17418 | 0.81306 | 0.05009 | 0.75208 | 0.04812 | 0.73009 | 0.79258 | 0.73628 | 0.04947 | 0.73728 | 2.9407 | 0.92572 | 0.05139 | 0.77335 | 0.0486 | 0.72192 | 0.04943 | 0.72799 | 0.04667 | 0.70665 | 0.04946 | 0.73728 | 96 | 7.8 | 58 | 1.06
GPLK 4*185 Cusvm | 185 Cu | 0.75 | 49 | 0.107 | 0.068 | 0.9 | 0.003 | 0.39 | 0.18 | 0.54 | 300 | 0.5 | 420 | 0.75 | 380 | 1 | 350 | 24 | 20 | 55 | 160 | 50 | 167 | 0 | 0.15601 | 0.80291 | 0.05023 | 0.744 | 0.04784 | 0.72223 | 0.64878 | 0.72864 | 0.04947 | 0.72958 | [12 empty] | 119 | 9.7
GPLKh 4*185 Cusvm 4*6 | 185 Cu; 6 | 0.75 | 53 | 0.107 | 0.068 | 0.9 | 0.003 | 0.39 | 0.18 | 0.54 | 300 | 0.5 | 420 | 0.75 | 380 | 1 | 350 | 24 | 20 | 55 | 160 | 50 | 167 | 0 | 0.15604 | 0.80294 | 0.05023 | 0.744 | 0.04784 | 0.7222 | 0.64878 | 0.72861 | 0.04947 | 0.72958 | 2.9415 | 0.92543 | 0.05183 | 0.76514 | 0.0484 | 0.71381 | 0.04941 | 0.71972 | 0.046 | 0.69864 | 0.04947 | 0.72961 | 119 | 9.7 | 58 | 1.06
GPLK 4*240 Cusvm | 240 Cu | 0.75 | 55 | 0.081 | 0.067 | 0.95 | 0.003 | 0.3 | 0.18 | 0.57 | 350 | 0.5 | 470 | 0.75 | 430 | 1 | 400 | 31 | 20 | 55 | 160 | 50 | 167 | 0 | 0.13023 | 0.79574 | 0.05057 | 0.73916 | 0.04761 | 0.71783 | 0.58201 | 0.72398 | 0.04947 | 0.72493 | [12 empty] | 134 | 10.9
GPLKh 4*240 Cusvm 4*6 | 240 Cu; 6 | 0.75 | 59 | 0.081 | 0.067 | 0.95 | 0.003 | 0.3 | 0.18 | 0.57 | 350 | 0.5 | 470 | 0.75 | 430 | 1 | 400 | 31 | 20 | 55 | 160 | 50 | 167 | 0 | 0.13029 | 0.79583 | 0.05057 | 0.73909 | 0.04758 | 0.71773 | 0.58202 | 0.72398 | 0.04947 | 0.72493 | 2.9423 | 0.92536 | 0.05242 | 0.75929 | 0.04831 | 0.70853 | 0.04947 | 0.71393 | 0.04517 | 0.69326 | 0.04947 | 0.72489 | 134 | 10.9 | 58 | 1.06
Vulto 3x2,5 Cu | 2,5 Cu | 0.75 | 4.5 | 7.41 | 0.107 | 0.156 | 0.004 | 28.31 | 0.16 | 0.09 | 32 | 0.5 | 55 | 0.75 | 48 | 1 | 44 | 0.44 | 20 | 90 | 160 | 50 | 0 | 0 | 7.393 | 0.9581 | 0.0494 | 0.862 | 0.0494 | 0.8624 | 7.0498 | 0.8436 | 0.0495 | 0.8438 | [12 empty] | 10 | 0.35
Vulto 4x2,5 Cu | 2,5 Cu | 0.75 | 5 | 7.41 | 0.119 | 0.162 | 0.004 | 16.46 | 0.36 | 0.1 | 32 | 0.5 | 55 | 0.75 | 48 | 1 | 44 | 0.44 | 20 | 90 | 160 | 50 | 0 | 0 | 7.4698 | 0.9622 | 0.0495 | 0.8679 | 0.0494 | 0.8458 | 6.781 | 0.8438 | 0.0495 | 0.8383 | [12 empty] | 10 | 0.35
Vulto 4x4 Cu | 4 Cu | 0.75 | 6 | 4.61 | 0.113 | 0.172 | 0.004 | 10.5 | 0.26 | 0.1 | 42 | 0.5 | 70 | 0.75 | 61 | 1 | 56 | 0.7 | 20 | 90 | 160 | 50 | 0 | 0 | 4.6899 | 0.9425 | 0.0495 | 0.8534 | 0.0494 | 0.8318 | 4.3151 | 0.8265 | 0.0495 | 0.8279 | [12 empty] | 16 | 0.6
Vulto 4x6 Cu | 6 Cu | 0.75 | 7 | 3.08 | 0.107 | 0.186 | 0.004 | 7.1 | 0.22 | 0.11 | 54 | 0.5 | 86 | 0.75 | 76 | 1 | 69 | 1.05 | 20 | 90 | 160 | 50 | 0 | 0 | 3.1313 | 0.9282 | 0.0495 | 0.8435 | 0.0493 | 0.8218 | 2.9093 | 0.818 | 0.0495 | 0.8191 | [12 empty] | 24 | 0.85
Vulto 4x10 Cu | 10 Cu | 0.75 | 9 | 1.83 | 0.063 | 0.229 | 0.004 | 4.22 | 0.24 | 0.14 | 75 | 0.5 | 115 | 0.75 | 101 | 1 | 92 | 1.75 | 20 | 90 | 160 | 50 | 0 | 0 | 1.8789 | 0.9055 | 0.0495 | 0.8271 | 0.0492 | 0.8054 | 1.7736 | 0.805 | 0.0495 | 0.8064 | [12 empty] | 40 | 1.4
Vulta 4x10 Cu | 10 Cu | 0.75 | 9 | 1.83 | 0.1 | 0.229 | 0.004 | 4.5 | 0.14 | 0.14 | 75 | 0.5 | 115 | 0.75 | 101 | 1 | 92 | 1.75 | 20 | 90 | 160 | 50 | 0 | 0 | 1.879 | 0.9033 | 0.0495 | 0.8252 | 0.0492 | 0.8035 | 1.7798 | 0.7987 | 0.0495 | 0.8002 | [12 empty] | 40 | 1.4
Vulta 4x16 Cu | 16 Cu | 0.75 | 12 | 1.15 | 0.097 | 0.264 | 0.004 | 2.83 | 0.13 | 0.16 | 100 | 0.5 | 149 | 0.75 | 131 | 1 | 119 | 2.2 | 20 | 90 | 160 | 50 | 0 | 0 | 1.2007 | 0.8892 | 0.0496 | 0.8143 | 0.049 | 0.7926 | 1.1328 | 0.7899 | 0.0495 | 0.7912 | [12 empty] | 62 | 2.3
Vulta 4x25 Cu | 25 Cu | 0.75 | 18 | 0.727 | 0.094 | 0.291 | 0.004 | 2.04 | 0.16 | 0.17 | 127 | 0.5 | 190 | 0.75 | 168 | 1 | 152 | 4.4 | 20 | 90 | 160 | 50 | 0 | 0 | 0.7766 | 0.8751 | 0.0496 | 0.7999 | 0.049 | 0.7782 | 1.1368 | 0.7778 | 0.0495 | 0.779 | [12 empty] | 78 | 3.6
Vulta 4x35 Cusv | 35 Cu | 0.75 | 20 | 0.525 | 0.1 | 0.286 | 0.004 | 1.59 | 0.15 | 0.17 | 158 | 0.5 | 229 | 0.75 | 203 | 1 | 183 | 6.1 | 20 | 90 | 160 | 50 | 0 | 0 | 0.5745 | 0.8616 | 0.0496 | 0.7973 | 0.0489 | 0.7751 | 1.1325 | 0.7788 | 0.0495 | 0.7798 | [12 empty] | 95 | 5
Vulta 4x50 Cusv | 50 Cu | 0.75 | 25 | 0.387 | 0.085 | 0.308 | 0.004 | 1.14 | 0.14 | 0.18 | 192 | 0.5 | 271 | 0.75 | 239 | 1 | 216 | 8.8 | 20 | 90 | 160 | 50 | 0 | 0 | 0.4369 | 0.8538 | 0.0496 | 0.7886 | 0.0485 | 0.7663 | 0.7426 | 0.7711 | 0.0495 | 0.7719 | [12 empty] | 112 | 7.2
Vulta 4x70 Cusv | 70 Cu | 0.75 | 32 | 0.27 | 0.072 | 0.357 | 0.004 | 0.8 | 0.14 | 0.21 | 246 | 0.5 | 335 | 0.75 | 296 | 1 | 267 | 12.3 | 20 | 90 | 160 | 50 | 0 | 0 | 0.3187 | 0.8427 | 0.0497 | 0.779 | 0.0481 | 0.7568 | 0.5446 | 0.7622 | 0.0495 | 0.7629 | [12 empty] | 138 | 10
Vulta 4x95 Cusv | 95 Cu | 0.75 | 36 | 0.194 | 0.069 | 0.391 | 0.004 | 0.57 | 0.13 | 0.23 | 298 | 0.5 | 397 | 0.75 | 350 | 1 | 317 | 16.6 | 20 | 90 | 160 | 50 | 0 | 0 | 0.2431 | 0.8329 | 0.0498 | 0.7715 | 0.0475 | 0.7496 | 0.3961 | 0.7561 | 0.0495 | 0.7566 | [12 empty] | 164 | 13.6
Vulta 4x120 Cusv | 120 Cu | 0.75 | 50 | 0.155 | 0.066 | 0.417 | 0.004 | 0.46 | 0.13 | 0.25 | 346 | 0.5 | 451 | 0.75 | 398 | 1 | 360 | 21 | 20 | 90 | 160 | 50 | 0 | 0 | 0.2038 | 0.8263 | 0.0499 | 0.7658 | 0.0472 | 0.7441 | 0.3383 | 0.7505 | 0.0495 | 0.751 | [12 empty] | 182 | 17.2
Vulta 4x150 Cusv | 150 Cu | 0.75 | 60 | 0.126 | 0.063 | 0.436 | 0.004 | 0.38 | 0.13 | 0.26 | 399 | 0.5 | 510 | 0.75 | 450 | 1 | 407 | 26.3 | 20 | 90 | 160 | 50 | 0 | 0 | 0.1745 | 0.8187 | 0.0499 | 0.7583 | 0.0466 | 0.7368 | 0.2805 | 0.7438 | 0.0495 | 0.7442 | [12 empty] | 211 | 21.5
Vulta 4x185 Cusv | 185 Cu | 0.75 | 70 | 0.103 | 0.063 | 0.45 | 0.004 | 0.31 | 0.13 | 0.27 | 456 | 0.5 | 572 | 0.75 | 505 | 1 | 456 | 32.4 | 20 | 90 | 160 | 50 | 0 | 0 | 0.1508 | 0.8118 | 0.0503 | 0.7514 | 0.0462 | 0.7304 | 0.2321 | 0.7364 | 0.0495 | 0.7357 | [12 empty] | 238 | 26.5
Vulta 4x240 Cusv | 240 Cu | 0.75 | 90 | 0.08 | 0.063 | 0.462 | 0.004 | 0.25 | 0.13 | 0.28 | 538 | 0.5 | 660 | 0.75 | 583 | 1 | 527 | 42 | 20 | 90 | 160 | 50 | 0 | 0 | 0.1278 | 0.8012 | 0.0502 | 0.7424 | 0.0452 | 0.7221 | 0.1939 | 0.7278 | 0.0495 | 0.7284 | [12 empty] | 273 | 34.3
4* 10 Cu VOYMvKasmb | 10 Cu | 0.75 | 9 | 1.83 | 0.063 | 0.229 | 0.004 | 4.22 | 0.24 | 0.14 | 75 | 0.5 | 115 | 0.75 | 101 | 1 | 92 | 1.75 | 20 | 90 | 160 | 50 | 0 | 0 | 1.8789 | 0.9055 | 0.0495 | 0.8271 | 0.0492 | 0.8054 | 1.7736 | 0.805 | 0.0495 | 0.8064 | [12 empty] | 40 | 1.4
4* 16 Cu VGYMvKasmb | 16 Cu | 0.75 | 12 | 1.15 | 0.097 | 0.264 | 0.004 | 2.83 | 0.13 | 0.16 | 100 | 0.5 | 149 | 0.75 | 131 | 1 | 119 | 2.2 | 20 | 90 | 160 | 50 | 0 | 0 | 1.2007 | 0.8892 | 0.0496 | 0.8143 | 0.049 | 0.7926 | 1.1328 | 0.7899 | 0.0495 | 0.7912 | [12 empty] | 62 | 2.3
4x1*185 Cu YMvKmb trefoil | 185 Cu | 1 | 0 | 0.1 | 0.17 | 0.45 | 0.004 | 0.4 | 0.6 | 0.27 | 535 | 0.5 | 438 | 0.75 | 395 | 1 | 371 | 21.2 | 20 | 90 | 160 | 50 | 0 | 0
4x1*185 Cu YMvKmb flat | 185 Cu | 1 | 0 | 0.1 | 0.17 | 0.45 | 0.004 | 0.4 | 0.6 | 0.45 | 625 | 0.5 | 444 | 0.75 | 400 | 1 | 376 | 21.2 | 20 | 90 | 160 | 50 | 0 | 0
4x1*240 Cu YMvKmb trefoil | 240 Cu | 1 | 0 | 0.08 | 0.16 | 0.46 | 0.004 | 0.32 | 0.56 | 0.28 | 630 | 0.5 | 505 | 0.75 | 455 | 1 | 428 | 27.5 | 20 | 90 | 160 | 50 | 0 | 0
4x1*240 Cu YMvKmb flat | 240 Cu | 1 | 0 | 0.08 | 0.16 | 0.46 | 0.004 | 0.32 | 0.56 | 0.46 | 730 | 0.5 | 505 | 0.75 | 455 | 1 | 428 | 27.5 | 20 | 90 | 160 | 50 | 0 | 0
4x1*300 Cu YMvKmb trefoil | 300 Cu | 1 | 0 | 0.065 | 0.15 | 0.47 | 0.004 | 0.26 | 0.53 | 0.28 | 720 | 0.5 | 566 | 0.75 | 510 | 1 | 479 | 34.4 | 20 | 90 | 160 | 50 | 0 | 0
4x1*300 Cu YMvKmb flat | 300 Cu | 1 | 0 | 0.065 | 0.15 | 0.47 | 0.004 | 0.26 | 0.53 | 0.47 | 825 | 0.5 | 560 | 0.75 | 505 | 1 | 475 | 34.4 | 20 | 90 | 160 | 50 | 0 | 0
4x2.5 YMvK/Cur | 2.5 Cu | 1 | 0 | 7.41 | 0.104 | 0.143 | 0.004 | 29.64 | 0.414 | 0.0858 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45 | 20 | 90 | 250 | 50 | 0 | 0
4x4 YMvK/Cur | 4 Cu | 1 | 0 | 4.61 | 0.097 | 0.15 | 0.004 | 18.44 | 0.389 | 0.09 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 20 | 90 | 250 | 50 | 0 | 0
4x6 YMvK/Cur | 6 Cu | 1 | 0 | 3.08 | 0.093 | 0.185 | 0.004 | 12.32 | 0.372 | 0.111 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89 | 20 | 90 | 250 | 50 | 0 | 0
4x10 YMvK/Cur | 10 Cu | 1 | 0 | 1.83 | 0.0951 | 0.185 | 0.004 | 7.32 | 0.3804 | 0.111 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 1.34 | 20 | 90 | 250 | 50 | 0 | 0
4x16 YMvK/Cur | 16 Cu | 1 | 0 | 1.15 | 0.0894 | 0.212 | 0.004 | 4.6 | 0.3576 | 0.1272 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2.24 | 20 | 90 | 250 | 50 | 0 | 0
4x25 YMvK/CurST | 25 Cu | 1 | 0 | 0.727 | 0.0878 | 0.227 | 0.004 | 2.908 | 0.3512 | 0.1362 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 20 | 90 | 250 | 50 | 0 | 0
4x35 YMvK/CusST | 35 Cu | 1 | 0 | 0.524 | 0.085 | 0.209 | 0.004 | 2.096 | 0.34 | 0.1254 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 20 | 90 | 250 | 50 | 0 | 0
4x50 YMvK/CusST | 50 Cu | 1 | 0 | 0.387 | 0.0846 | 0.215 | 0.004 | 1.548 | 0.3384 | 0.129 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8 | 20 | 90 | 250 | 50 | 0 | 0
4x70 YMvK/CusST | 70 Cu | 1 | 0 | 0.268 | 0.0824 | 0.242 | 0.004 | 1.072 | 0.3296 | 0.1452 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 20 | 90 | 250 | 50 | 0 | 0
4x95 YMvK/CusST | 95 Cu | 1 | 0 | 0.193 | 0.082 | 0.263 | 0.004 | 0.772 | 0.328 | 0.1578 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 20 | 90 | 250 | 50 | 0 | 0
4x120 YMvK/CusST | 120 Cu | 1 | 0 | 0.153 | 0.0805 | 0.275 | 0.004 | 0.612 | 0.322 | 0.165 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 13.86 | 20 | 90 | 250 | 50 | 0 | 0
4x150 YMvK/CusST | 150 Cu | 1 | 0 | 0.124 | 0.0805 | 0.281 | 0.004 | 0.496 | 0.322 | 0.1686 | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 21.5 | 20 | 90 | 250 | 50 | 0 | 0
4x185 YMvK/CusST | 185 Cu | 1 | 0 | 0.0991 | 0.0803 | 0.284 | 0.004 | 0.3964 | 0.3212 | 0.1704 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 21.2 | 20 | 90 | 250 | 50 | 0 | 0
4x240 YMvK/CusST | 240 Cu | 1 | 0 | 0.0754 | 0.0799 | 0.297 | 0.004 | 0.3016 | 0.3196 | 0.1782 | 538 | 0 | 0 | 0 | 0 | 0 | 0 | 27.5 | 20 | 90 | 250 | 50 | 0 | 0
4x300 YMvK/CusST | 300 Cu | 1 | 0 | 0.0601 | 0.0798 | 0.31 | 0.004 | 0.2404 | 0.3192 | 0.192 | 621 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 20 | 90 | 250 | 50 | 0 | 0
4x1*10 YMvK/Cur quadrofoil | 10 Cu | 1 | 0 | 1.83 | 0.143 | 0.185 | 0.004 | 7.32 | 0.572 | 0.111 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 1.34 | 20 | 90 | 250 | 50 | 0 | 0
4x1*10 YMvK/Cur flat | 10 Cu | 1 | 0 | 1.83 | 0.143 | 0.185 | 0.004 | 7.32 | 0.572 | 0.185 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 1.34 | 20 | 90 | 250 | 50 | 0 | 0
4x1*16 YMvK/Cur quadrofoil | 16 Cu | 1 | 0 | 1.15 | 0.133 | 0.212 | 0.004 | 4.6 | 0.532 | 0.1272 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 2.24 | 20 | 90 | 250 | 50 | 0 | 0
4x1*16 YMvK/Cur flat | 16 Cu | 1 | 0 | 1.15 | 0.133 | 0.212 | 0.004 | 4.6 | 0.532 | 0.212 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 2.24 | 20 | 90 | 250 | 50 | 0 | 0
4x1*25 YMvK/CurST quadrofoil | 25 Cu | 1 | 0 | 0.727 | 0.119 | 0.227 | 0.004 | 2.908 | 0.476 | 0.1362 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 20 | 90 | 250 | 50 | 0 | 0
4x1*25 YMvK/CurST flat | 25 Cu | 1 | 0 | 0.727 | 0.119 | 0.227 | 0.004 | 2.908 | 0.476 | 0.227 | 141 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 20 | 90 | 250 | 50 | 0 | 0
4x1*35 YMvK/CurST quadrofoil | 35 Cu | 1 | 0 | 0.524 | 0.113 | 0.209 | 0.004 | 2.096 | 0.452 | 0.1254 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 20 | 90 | 250 | 50 | 0 | 0
4x1*35 YMvK/CurST flat | 35 Cu | 1 | 0 | 0.524 | 0.113 | 0.209 | 0.004 | 2.096 | 0.452 | 0.209 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 20 | 90 | 250 | 50 | 0 | 0
4x1*50 YMvK/CurST quadrofoil | 50 Cu | 1 | 0 | 0.387 | 0.11 | 0.215 | 0.004 | 1.548 | 0.44 | 0.129 | 207 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2 | 20 | 90 | 250 | 50 | 0 | 0
4x1*50 YMvK/CurST flat | 50 Cu | 1 | 0 | 0.387 | 0.11 | 0.215 | 0.004 | 1.548 | 0.44 | 0.215 | 216 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2 | 20 | 90 | 250 | 50 | 0 | 0
4x1*70 YMvK/CurST quadrofoil | 70 Cu | 1 | 0 | 0.268 | 0.102 | 0.242 | 0.004 | 1.072 | 0.408 | 0.1452 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 20 | 90 | 250 | 50 | 0 | 0
4x1*70 YMvK/CurST flat | 70 Cu | 1 | 0 | 0.268 | 0.102 | 0.242 | 0.004 | 1.072 | 0.408 | 0.242 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 20 | 90 | 250 | 50 | 0 | 0
4x1*95 YMvK/CurST quadrofoil | 95 Cu | 1 | 0 | 0.193 | 0.099 | 0.263 | 0.004 | 0.772 | 0.396 | 0.1578 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6 | 20 | 90 | 250 | 50 | 0 | 0
4x1*95 YMvK/CurST flat | 95 Cu | 1 | 0 | 0.193 | 0.099 | 0.263 | 0.004 | 0.772 | 0.396 | 0.263 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6 | 20 | 90 | 250 | 50 | 0 | 0
4x1*120 YMvK/CurST quadrofoil | 120 Cu | 1 | 0 | 0.153 | 0.097 | 0.275 | 0.004 | 0.612 | 0.388 | 0.165 | 383 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9 | 20 | 90 | 250 | 50 | 0 | 0
4x1*120 YMvK/CurST flat | 120 Cu | 1 | 0 | 0.153 | 0.097 | 0.275 | 0.004 | 0.612 | 0.388 | 0.275 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9 | 20 | 90 | 250 | 50 | 0 | 0
4x1*150 YMvK/CurST quadrofoil | 150 Cu | 1 | 0 | 0.124 | 0.097 | 0.281 | 0.004 | 0.496 | 0.388 | 0.1686 | 444 | 0 | 0 | 0 | 0 | 0 | 0 | 16.8 | 20 | 90 | 250 | 50 | 0 | 0
4x1*150 YMvK/CurST flat | 150 Cu | 1 | 0 | 0.124 | 0.097 | 0.281 | 0.004 | 0.496 | 0.388 | 0.281 | 464 | 0 | 0 | 0 | 0 | 0 | 0 | 16.8 | 20 | 90 | 250 | 50 | 0 | 0
4x1*185 YMvK/CurST quadrofoil | 185 Cu | 1 | 0 | 0.099 | 0.096 | 0.284 | 0.004 | 0.396 | 0.384 | 0.1704 | 510 | 0 | 0 | 0 | 0 | 0 | 0 | 21.2 | 20 | 90 | 250 | 50 | 0 | 0
4x1*185 YMvK/CurST flat | 185 Cu | 1 | 0 | 0.099 | 0.096 | 0.284 | 0.004 | 0.396 | 0.384 | 0.284 | 533 | 0 | 0 | 0 | 0 | 0 | 0 | 21.2 | 20 | 90 | 250 | 50 | 0 | 0
4x1*240 YMvK/CurST quadrofoil | 240 Cu | 1 | 0 | 0.075 | 0.094 | 0.297 | 0.004 | 0.3 | 0.376 | 0.1782 | 607 | 0 | 0 | 0 | 0 | 0 | 0 | 34.2 | 20 | 90 | 250 | 50 | 0 | 0
4x1*240 YMvK/CurST flat | 240 Cu | 1 | 0 | 0.075 | 0.094 | 0.297 | 0.004 | 0.3 | 0.376 | 0.297 | 634 | 0 | 0 | 0 | 0 | 0 | 0 | 34.2 | 20 | 90 | 250 | 50 | 0 | 0
4x1*300 YMvK/CurST quadrofoil | 300 Cu | 1 | 0 | 0.06 | 0.091 | 0.31 | 0.004 | 0.24 | 0.364 | 0.192 | 703 | 0 | 0 | 0 | 0 | 0 | 0 | 34.4 | 20 | 90 | 250 | 50 | 0 | 0
4x1*300 YMvK/CurST flat | 300 Cu | 1 | 0 | 0.06 | 0.091 | 0.31 | 0.004 | 0.24 | 0.364 | 0.31 | 736 | 0 | 0 | 0 | 0 | 0 | 0 | 34.4 | 20 | 90 | 250 | 50 | 0 | 0
4x1*400 YMvK/CurST quadrofoil | 400 Cu | 1 | 0 | 0.047 | 0.0877 | 0.32 | 0.004 | 0.188 | 0.3508 | 0.192 | 823 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 20 | 90 | 250 | 50 | 0 | 0
4x1*400 YMvK/CurST flat | 400 Cu | 1 | 0 | 0.047 | 0.0877 | 0.32 | 0.004 | 0.188 | 0.3508 | 0.32 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 20 | 90 | 250 | 50 | 0 | 0
3* 25 AL GPLK 8/10 | 25 Al | 10 | 0 | 1.2 | 0.097 | 0.23 | 0.003 | 5.61 | 0.16 | 0.14 | 57 | 0.5 | 93 | 0.75 | 86 | 1 | 80 | 2.1 | 20 | 50 | 160 | 50 | 167 | 0 | 1.3792 | 0.8754 | 0.0492 | 0.7781 | 0.0492 | 0.7781 | 1.3353 | 0.7588 | 0.0495 | 0.7621 | [12 empty] | 40
3* 35 AL GPLK 8/10 | 35 Al | 10 | 0 | 0.868 | 0.093 | 0.26 | 0.003 | 4.97 | 0.15 | 0.16 | 69 | 0.5 | 110 | 0.75 | 105 | 1 | 97 | 3 | 20 | 50 | 160 | 50 | 167 | 0 | 1.0142 | 0.8703 | 0.0493 | 0.7755 | 0.0493 | 0.7755 | 1.2942 | 0.7573 | 0.0495 | 0.7601 | [12 empty] | 49
3* 50 AL GPLK 8/10 | 50 Al | 10 | 0 | 0.641 | 0.088 | 0.28 | 0.003 | 4.28 | 0.15 | 0.17 | 83 | 0.5 | 135 | 0.75 | 125 | 1 | 115 | 4.3 | 20 | 50 | 160 | 50 | 167 | 0 | 0.7621 | 0.8575 | 0.0492 | 0.766 | 0.0492 | 0.7666 | 1.103 | 0.7498 | 0.0495 | 0.7527 | [12 empty] | 58
3* 70 AL GPLK 8/10 | 70 Al | 10 | 0 | 0.443 | 0.085 | 0.31 | 0.003 | 3.6 | 0.14 | 0.19 | 105 | 0.5 | 165 | 0.75 | 150 | 1 | 140 | 6 | 20 | 50 | 160 | 50 | 167 | 0 | 0.5423 | 0.8506 | 0.0492 | 0.762 | 0.0491 | 0.7606 | 0.9972 | 0.7458 | 0.0495 | 0.7493 | [12 empty] | 70
3* 95 AL GPLK 8/10 | 95 Al | 10 | 0 | 0.321 | 0.082 | 0.34 | 0.003 | 3.01 | 0.13 | 0.2 | 125 | 0.5 | 205 | 0.75 | 185 | 1 | 170 | 8.1 | 20 | 50 | 160 | 50 | 167 | 0 | 0.4051 | 0.8396 | 0.0491 | 0.7565 | 0.0491 | 0.7577 | 0.9069 | 0.7419 | 0.0495 | 0.7461 | [12 empty] | 79
3*120 AL GPLK 8/10 | 120 Al | 10 | 0 | 0.254 | 0.08 | 0.38 | 0.003 | 2.64 | 0.13 | 0.23 | 145 | 0.5 | 235 | 0.75 | 215 | 1 | 200 | 10.2 | 20 | 50 | 160 | 50 | 167 | 0 | 0.3301 | 0.8362 | 0.0491 | 0.7572 | 0.0491 | 0.7566 | 0.8336 | 0.7396 | 0.0495 | 0.743 | [12 empty] | 87
3*150 AL GPLK 8/10 | 150 Al | 10 | 0 | 0.207 | 0.078 | 0.42 | 0.003 | 2.38 | 0.12 | 0.25 | 165 | 0.5 | 265 | 0.75 | 240 | 1 | 220 | 12.8 | 20 | 50 | 160 | 50 | 167 | 0 | 0.278 | 0.8263 | 0.049 | 0.7488 | 0.0491 | 0.7501 | 0.7388 | 0.7347 | 0.0495 | 0.7373 | [12 empty] | 100
3*185 AL GPLK 8/10 | 185 Al | 10 | 0 | 0.166 | 0.076 | 0.45 | 0.003 | 2.11 | 0.12 | 0.27 | 195 | 0.5 | 305 | 0.75 | 275 | 1 | 255 | 15.8 | 20 | 50 | 160 | 50 | 167 | 0 | 0.232 | 0.8174 | 0.049 | 0.7431 | 0.049 | 0.7431 | 0.6868 | 0.7313 | 0.0495 | 0.7346 | [12 empty] | 109
3*240 AL GPLK 8/10 | 240 Al | 10 | 0 | 0.127 | 0.074 | 0.5 | 0.003 | 1.81 | 0.11 | 0.3 | 230 | 0.5 | 355 | 0.75 | 320 | 1 | 295 | 20.4 | 20 | 50 | 160 | 50 | 167 | 0 | 0.1879 | 0.8097 | 0.0489 | 0.7376 | 0.0489 | 0.7377 | 0.5933 | 0.725 | 0.0495 | 0.7272 | [12 empty] | 128
3*300 AL GPLK 8/10 | 300 Al | 10 | 0 | 0.103 | 0.073 | 0.55 | 0.003 | 1.6 | 0.11 | 0.33 | 265 | 0.5 | 400 | 0.75 | 355 | 1 | 330 | 26 | 20 | 50 | 160 | 50 | 167 | 0
3*400 AL GPLK 8/10 | 400 Al | 10 | 0 | 0.081 | 0.071 | 0.6 | 0.003 | 1.32 | 0.1 | 0.36 | 305 | 0.5 | 450 | 0.75 | 400 | 1 | 375 | 34 | 20 | 50 | 160 | 50 | 167 | 0
3* 25 AL GPLK 10/10 | 25 Al | 10 | 0 | 1.2 | 0.099 | 0.22 | 0.003 | 5.09 | 0.16 | 0.13 | 57 | 0.5 | 88 | 0.75 | 82 | 1 | 77 | 2.1 | 20 | 50 | 160 | 50 | 167 | 0
3* 35 AL GPLK 10/10 | 35 Al | 10 | 0 | 0.868 | 0.094 | 0.25 | 0.003 | 4.33 | 0.16 | 0.15 | 69 | 0.5 | 105 | 0.75 | 99 | 1 | 93 | 3.8 | 20 | 50 | 160 | 50 | 167 | 0
3* 50 AL GPLK 10/10 | 50 Al | 10 | 0 | 0.641 | 0.09 | 0.27 | 0.003 | 3.65 | 0.15 | 0.16 | 82 | 0.5 | 130 | 0.75 | 120 | 1 | 110 | 4.3 | 20 | 50 | 160 | 50 | 167 | 0
3* 70 AL GPLK 10/10 | 70 Al | 10 | 0 | 0.443 | 0.086 | 0.3 | 0.003 | 3.01 | 0.14 | 0.18 | 105 | 0.5 | 155 | 0.75 | 145 | 1 | 135 | 6 | 20 | 50 | 160 | 50 | 167 | 0
3* 95 AL GPLK 10/10 | 95 Al | 10 | 0 | 0.321 | 0.083 | 0.33 | 0.003 | 2.6 | 0.13 | 0.2 | 125 | 0.5 | 190 | 0.75 | 175 | 1 | 165 | 8.1 | 20 | 50 | 160 | 50 | 167 | 0
3*120 AL GPLK 10/10 | 120 Al | 10 | 0 | 0.254 | 0.081 | 0.36 | 0.003 | 2.34 | 0.13 | 0.22 | 145 | 0.5 | 220 | 0.75 | 205 | 1 | 190 | 10.2 | 20 | 50 | 160 | 50 | 167 | 0
3*150 AL GPLK 10/10 | 150 Al | 10 | 0 | 0.207 | 0.079 | 0.39 | 0.003 | 2.08 | 0.12 | 0.23 | 165 | 0.5 | 250 | 0.75 | 230 | 1 | 215 | 12.8 | 20 | 50 | 160 | 50 | 167 | 0
3*185 AL GPLK 10/10 | 185 Al | 10 | 0 | 0.166 | 0.077 | 0.42 | 0.003 | 1.92 | 0.12 | 0.25 | 190 | 0.5 | 290 | 0.75 | 265 | 1 | 245 | 15.8 | 20 | 50 | 160 | 50 | 167 | 0
3*240 AL GPLK 10/10 | 240 Al | 10 | 0 | 0.127 | 0.075 | 0.47 | 0.003 | 1.6 | 0.11 | 0.28 | 225 | 0.5 | 340 | 0.75 | 310 | 1 | 285 | 20.4 | 20 | 50 | 160 | 50 | 167 | 0
3*300 AL GPLK 10/10 | 300 Al | 10 | 0 | 0.103 | 0.074 | 0.52 | 0.003 | 1.43 | 0.11 | 0.31 | 255 | 0.5 | 385 | 0.75 | 345 | 1 | 320 | 26 | 20 | 50 | 160 | 50 | 167 | 0
3*400 AL GPLK 10/10 | 400 Al | 10 | 0 | 0.081 | 0.072 | 0.57 | 0.003 | 1.18 | 0.1 | 0.34 | 295 | 0.5 | 435 | 0.75 | 390 | 1 | 360 | 34 | 20 | 50 | 160 | 50 | 167 | 0
3* 25 CU GPLK 8/10 | 25 Cu | 10 | 0 | 0.727 | 0.097 | 0.23 | 0.003 | 5.13 | 0.16 | 0.14 | 74 | 0.5 | 120 | 0.75 | 110 | 1 | 105 | 3.2 | 20 | 50 | 160 | 50 | 167 | 0 | 0.86276 | 0.87538 | 0.04916 | 0.77808 | 0.04916 | 0.77808 | 1.3353 | 0.75878 | 0.04946 | 0.76208 | [12 empty] | 52
3* 35 CU GPLK 8/10 | 35 Cu | 10 | 0 | 0.524 | 0.093 | 0.26 | 0.003 | 4.63 | 0.15 | 0.16 | 89 | 0.5 | 145 | 0.75 | 135 | 1 | 125 | 4.5 | 20 | 50 | 160 | 50 | 167 | 0 | 0.63536 | 0.87028 | 0.04926 | 0.77548 | 0.04926 | 0.77548 | 1.2942 | 0.75728 | 0.04946 | 0.76008 | [12 empty] | 53
3* 50 CU GPLK 8/10 | 50 Cu | 10 | 0 | 0.387 | 0.088 | 0.28 | 0.003 | 4.03 | 0.15 | 0.17 | 110 | 0.5 | 175 | 0.75 | 160 | 1 | 150 | 6.5 | 20 | 50 | 160 | 50 | 167 | 0 | 0.48206 | 0.85748 | 0.04916 | 0.76598 | 0.04916 | 0.76658 | 1.103 | 0.74978 | 0.04946 | 0.75268 | [12 empty] | 64
3* 70 CU GPLK 8/10 | 70 Cu | 10 | 0 | 0.269 | 0.085 | 0.31 | 0.003 | 3.43 | 0.14 | 0.19 | 135 | 0.5 | 215 | 0.75 | 195 | 1 | 180 | 9 | 20 | 50 | 160 | 50 | 167 | 0 | 0.34926 | 0.85058 | 0.04916 | 0.76198 | 0.04906 | 0.76058 | 0.99716 | 0.74578 | 0.04946 | 0.74928 | [12 empty] | 71
3* 95 CU GPLK 8/10 | 95 Cu | 10 | 0 | 0.194 | 0.082 | 0.34 | 0.003 | 2.89 | 0.13 | 0.2 | 165 | 0.5 | 265 | 0.75 | 240 | 1 | 225 | 12.3 | 20 | 50 | 160 | 50 | 167 | 0 | 0.26516 | 0.83956 | 0.04906 | 0.75646 | 0.04906 | 0.75766 | 0.90686 | 0.74186 | 0.04946 | 0.74606 | [12 empty] | 79
3*120 CU GPLK 8/10 | 120 Cu | 10 | 0 | 0.154 | 0.08 | 0.38 | 0.003 | 2.54 | 0.13 | 0.23 | 190 | 0.5 | 305 | 0.75 | 275 | 1 | 255 | 15.5 | 20 | 50 | 160 | 50 | 167 | 0 | 0.22116 | 0.8362 | 0.04906 | 0.7572 | 0.04906 | 0.7566 | 0.83356 | 0.7396 | 0.04946 | 0.743 | [12 empty] | 87
3*150 CU GPLK 8/10 | 150 Cu | 10 | 0 | 0.125 | 0.078 | 0.42 | 0.003 | 2.3 | 0.12 | 0.25 | 215 | 0.5 | 340 | 0.75 | 310 | 1 | 285 | 19.4 | 20 | 50 | 160 | 50 | 167 | 0 | 0.18796 | 0.82628 | 0.04896 | 0.74878 | 0.04906 | 0.75008 | 0.73876 | 0.73468 | 0.04946 | 0.73728 | [12 empty] | 100
3*185 CU GPLK 8/10 | 185 Cu | 10 | 0 | 0.101 | 0.076 | 0.45 | 0.003 | 2.05 | 0.12 | 0.27 | 250 | 0.5 | 390 | 0.75 | 350 | 1 | 320 | 23.9 | 20 | 50 | 160 | 50 | 167 | 0 | 0.16096 | 0.81741 | 0.04896 | 0.74311 | 0.04896 | 0.74311 | 0.68676 | 0.73131 | 0.04946 | 0.73461 | [12 empty] | 109
3*240 CU GPLK 8/10 | 240 Cu | 10 | 0 | 0.078 | 0.074 | 0.5 | 0.003 | 1.76 | 0.11 | 0.3 | 295 | 0.5 | 455 | 0.75 | 410 | 1 | 375 | 31 | 20 | 50 | 160 | 50 | 167 | 0 | 0.13286 | 0.80971 | 0.04886 | 0.73761 | 0.04886 | 0.73771 | 0.59326 | 0.72501 | 0.04946 | 0.72721 | [12 empty] | 128
3*300 CU GPLK 8/10 | 300 Cu | 10 | 0 | 0.063 | 0.073 | 0.55 | 0.003 | 1.56 | 0.11 | 0.33 | 335 | 0.5 | 500 | 0.75 | 445 | 1 | 420 | 38 | 20 | 50 | 160 | 50 | 167 | 0
3*400 CU GPLK 8/10 | 400 Cu | 10 | 0 | 0.049 | 0.071 | 0.6 | 0.003 | 1.29 | 0.1 | 0.36 | 385 | 0.5 | 555 | 0.75 | 495 | 1 | 470 | 50 | 20 | 50 | 160 | 50 | 167 | 0
3* 25 CU GPLK 10/10 | 25 Cu | 10 | 0 | 0.727 | 0.099 | 0.22 | 0.003 | 4.62 | 0.16 | 0.13 | 73 | 0.5 | 110 | 0.75 | 105 | 1 | 99 | 3.2 | 20 | 50 | 160 | 50 | 167 | 0
3* 35 CU GPLK 10/10 | 35 Cu | 10 | 0 | 0.524 | 0.094 | 0.25 | 0.003 | 3.99 | 0.16 | 0.15 | 88 | 0.5 | 135 | 0.75 | 125 | 1 | 120 | 4.5 | 20 | 50 | 160 | 50 | 167 | 0
3* 50 CU GPLK 10/10 | 50 Cu | 10 | 0 | 0.387 | 0.09 | 0.27 | 0.003 | 3.4 | 0.15 | 0.16 | 105 | 0.5 | 160 | 0.75 | 150 | 1 | 140 | 6.5 | 20 | 50 | 160 | 50 | 167 | 0
3* 70 CU GPLK 10/10 | 70 Cu | 10 | 0 | 0.269 | 0.086 | 0.3 | 0.003 | 2.84 | 0.14 | 0.18 | 130 | 0.5 | 200 | 0.75 | 185 | 1 | 170 | 9 | 20 | 50 | 160 | 50 | 167 | 0
3* 95 CU GPLK 10/10 | 95 Cu | 10 | 0 | 0.194 | 0.083 | 0.33 | 0.003 | 2.47 | 0.13 | 0.2 | 160 | 0.5 | 245 | 0.75 | 225 | 1 | 210 | 12.3 | 20 | 50 | 160 | 50 | 167 | 0
3*120 CU GPLK 10/10 | 120 Cu | 10 | 0 | 0.154 | 0.081 | 0.36 | 0.003 | 2.24 | 0.13 | 0.22 | 185 | 0.5 | 285 | 0.75 | 265 | 1 | 245 | 15.5 | 20 | 50 | 160 | 50 | 167 | 0
3*150 CU GPLK 10/10 | 150 Cu | 10 | 0 | 0.125 | 0.079 | 0.39 | 0.003 | 1.99 | 0.12 | 0.23 | 210 | 0.5 | 320 | 0.75 | 295 | 1 | 275 | 19.4 | 20 | 50 | 160 | 50 | 167 | 0
3*185 CU GPLK 10/10 | 185 Cu | 10 | 0 | 0.101 | 0.077 | 0.42 | 0.003 | 1.85 | 0.12 | 0.25 | 245 | 0.5 | 365 | 0.75 | 335 | 1 | 310 | 23.9 | 20 | 50 | 160 | 50 | 167 | 0
3*240 CU GPLK 10/10 | 240 Cu | 10 | 0 | 0.078 | 0.075 | 0.47 | 0.003 | 1.55 | 0.11 | 0.28 | 285 | 0.5 | 430 | 0.75 | 390 | 1 | 365 | 31 | 20 | 50 | 160 | 50 | 167 | 0
3*300 CU GPLK 10/10 | 300 Cu | 10 | 0 | 0.063 | 0.074 | 0.52 | 0.003 | 1.39 | 0.11 | 0.31 | 325 | 0.5 | 495 | 0.75 | 425 | 1 | 405 | 38 | 20 | 50 | 160 | 50 | 167 | 0
3*400 CU GPLK 10/10 | 400 Cu | 10 | 0 | 0.049 | 0.072 | 0.57 | 0.003 | 1.15 | 0.1 | 0.34 | 370 | 0.5 | 530 | 0.75 | 475 | 1 | 455 | 50 | 20 | 50 | 160 | 50 | 167 | 0
3x1* 50 AL XLPE 6/10 trefoil | 50 Al | 10 | 0 | 0.641 | 0.141 | 0.24 | 0.004 | 1.34 | 0.08 | 0.24 | 185 | 0.5 | 190 | 0.75 | 155 | 1 | 140 | 4.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1* 50 AL XLPE 6/10 flat | 50 Al | 10 | 0 | 0.641 | 0.199 | 0.24 | 0.004 | 1.34 | 0.08 | 0.24 | 220 | 0.5 | 200 | 0.75 | 165 | 1 | 145 | 4.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1* 95 AL XLPE 6/10 trefoil | 95 Al | 10 | 0 | 0.32 | 0.126 | 0.3 | 0.004 | 1.02 | 0.07 | 0.3 | 285 | 0.5 | 270 | 0.75 | 225 | 1 | 200 | 9 | 20 | 90 | 250 | 50 | 150 | 0
3x1* 95 AL XLPE 6/10 flat | 95 Al | 10 | 0 | 0.32 | 0.184 | 0.3 | 0.004 | 1.02 | 0.07 | 0.3 | 330 | 0.5 | 285 | 0.75 | 235 | 1 | 205 | 9 | 20 | 90 | 250 | 50 | 150 | 0
3x1*150 AL XLPE 6/10 trefoil | 150 Al | 10 | 0 | 0.205 | 0.118 | 0.36 | 0.004 | 0.91 | 0.06 | 0.36 | 370 | 0.5 | 345 | 0.75 | 285 | 1 | 250 | 14.3 | 20 | 90 | 250 | 50 | 150 | 0
3x1*150 AL XLPE 6/10 flat | 150 Al | 10 | 0 | 0.205 | 0.176 | 0.36 | 0.004 | 0.91 | 0.06 | 0.36 | 430 | 0.5 | 355 | 0.75 | 295 | 1 | 255 | 14.3 | 20 | 90 | 250 | 50 | 150 | 0
3x1*240 AL XLPE 6/10 trefoil | 240 Al | 10 | 0 | 0.126 | 0.109 | 0.43 | 0.004 | 0.83 | 0.05 | 0.43 | 500 | 0.5 | 445 | 0.75 | 370 | 1 | 320 | 22.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1*240 AL XLPE 6/10 flat | 240 Al | 10 | 0 | 0.126 | 0.168 | 0.43 | 0.004 | 0.83 | 0.05 | 0.43 | 580 | 0.5 | 455 | 0.75 | 375 | 1 | 325 | 22.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1*400 AL XLPE 6/10 trefoil | 400 Al | 10 | 0 | 0.08 | 0.102 | 0.52 | 0.004 | 0.78 | 0.05 | 0.52 | 660 | 0.5 | 560 | 0.75 | 460 | 1 | 400 | 38 | 20 | 90 | 250 | 50 | 150 | 0
3x1*400 AL XLPE 6/10 flat | 400 Al | 10 | 0 | 0.08 | 0.16 | 0.52 | 0.004 | 0.78 | 0.05 | 0.52 | 730 | 0.5 | 540 | 0.75 | 440 | 1 | 380 | 38 | 20 | 90 | 250 | 50 | 150 | 0
3x1*630 AL XLPE 6/10 trefoil | 630 Al | 10 | 0 | 0.049 | 0.095 | 0.64 | 0.004 | 0.75 | 0.04 | 0.64 | 890 | 0.5 | 700 | 0.75 | 580 | 1 | 510 | 59.9 | 20 | 90 | 250 | 50 | 150 | 0
3x1*630 AL XLPE 6/10 flat | 630 Al | 10 | 0 | 0.049 | 0.153 | 0.64 | 0.004 | 0.75 | 0.04 | 0.64 | 930 | 0.5 | 660 | 0.75 | 540 | 1 | 470 | 59.9 | 20 | 90 | 250 | 50 | 150 | 0
3x1* 50 AL XLPE 8,7/15 trefoil | 50 Al | 15 | 0 | 0.641 | 0.146 | 0.19 | 0.004 | 1.34 | 0.09 | 0.19 | 185 | 0.5 | 190 | 0.75 | 155 | 1 | 140 | 4.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1* 50 AL XLPE 8,7/15 flat | 50 Al | 15 | 0 | 0.641 | 0.204 | 0.19 | 0.004 | 1.34 | 0.09 | 0.19 | 220 | 0.5 | 200 | 0.75 | 165 | 1 | 145 | 4.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1* 95 AL XLPE 8,7/15 trefoil | 95 Al | 15 | 0 | 0.32 | 0.13 | 0.24 | 0.004 | 1.02 | 0.07 | 0.24 | 285 | 0.5 | 270 | 0.75 | 225 | 1 | 200 | 9 | 20 | 90 | 250 | 50 | 150 | 0
3x1* 95 AL XLPE 8,7/15 flat | 95 Al | 15 | 0 | 0.32 | 0.188 | 0.24 | 0.004 | 1.02 | 0.07 | 0.24 | 330 | 0.5 | 285 | 0.75 | 235 | 1 | 205 | 9 | 20 | 90 | 250 | 50 | 150 | 0
3x1*150 AL XLPE 8,7/15 trefoil | 150 Al | 15 | 0 | 0.205 | 0.121 | 0.28 | 0.004 | 0.91 | 0.07 | 0.28 | 370 | 0.5 | 345 | 0.75 | 285 | 1 | 250 | 14.3 | 20 | 90 | 250 | 50 | 150 | 0
3x1*150 AL XLPE 8,7/15 flat | 150 Al | 15 | 0 | 0.205 | 0.179 | 0.28 | 0.004 | 0.91 | 0.07 | 0.28 | 430 | 0.5 | 355 | 0.75 | 295 | 1 | 255 | 14.3 | 20 | 90 | 250 | 50 | 150 | 0
3x1*240 AL XLPE 8,7/15 trefoil | 240 Al | 15 | 0 | 0.126 | 0.113 | 0.33 | 0.004 | 0.83 | 0.06 | 0.33 | 500 | 0.5 | 445 | 0.75 | 370 | 1 | 320 | 22.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1*240 AL XLPE 8,7/15 flat | 240 Al | 15 | 0 | 0.126 | 0.171 | 0.33 | 0.004 | 0.83 | 0.06 | 0.33 | 580 | 0.5 | 455 | 0.75 | 375 | 1 | 325 | 22.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1*400 AL XLPE 8,7/15 trefoil | 400 Al | 15 | 0 | 0.08 | 0.105 | 0.4 | 0.004 | 0.78 | 0.05 | 0.4 | 660 | 0.5 | 560 | 0.75 | 460 | 1 | 400 | 38 | 20 | 90 | 250 | 50 | 150 | 0
3x1*400 AL XLPE 8,7/15 flat | 400 Al | 15 | 0 | 0.08 | 0.163 | 0.4 | 0.004 | 0.78 | 0.05 | 0.4 | 730 | 0.5 | 540 | 0.75 | 440 | 1 | 380 | 38 | 20 | 90 | 250 | 50 | 150 | 0
3x1*630 AL XLPE 8,7/15 trefoil | 630 Al | 15 | 0 | 0.049 | 0.098 | 0.49 | 0.004 | 0.75 | 0.04 | 0.49 | 890 | 0.5 | 700 | 0.75 | 580 | 1 | 510 | 59.9 | 20 | 90 | 250 | 50 | 150 | 0
3x1*630 AL XLPE 8,7/15 flat | 630 Al | 15 | 0 | 0.049 | 0.156 | 0.49 | 0.004 | 0.75 | 0.04 | 0.49 | 930 | 0.5 | 660 | 0.75 | 540 | 1 | 470 | 59.9 | 20 | 90 | 250 | 50 | 150 | 0
3x1* 95 AL XLPE 12/20 trefoil | 95 Al | 20 | 0 | 0.32 | 0.134 | 0.21 | 0.004 | 1.02 | 0.08 | 0.21 | 285 | 0.5 | 275 | 0.75 | 230 | 1 | 200 | 9.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1* 95 AL XLPE 12/20 flat | 95 Al | 20 | 0 | 0.32 | 0.192 | 0.21 | 0.004 | 1.02 | 0.08 | 0.21 | 330 | 0.5 | 290 | 0.75 | 240 | 1 | 210 | 9.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1*150 AL XLPE 12/20 trefoil | 150 Al | 20 | 0 | 0.205 | 0.125 | 0.24 | 0.004 | 0.91 | 0.07 | 0.24 | 375 | 0.5 | 345 | 0.75 | 290 | 1 | 250 | 14.3 | 20 | 90 | 250 | 50 | 150 | 0
3x1*150 AL XLPE 12/20 flat | 150 Al | 20 | 0 | 0.205 | 0.183 | 0.24 | 0.004 | 0.91 | 0.07 | 0.24 | 430 | 0.5 | 360 | 0.75 | 300 | 1 | 260 | 14.3 | 20 | 90 | 250 | 50 | 150 | 0
3x1*240 AL XLPE 12/20 trefoil | 240 Al | 20 | 0 | 0.126 | 0.116 | 0.29 | 0.004 | 0.83 | 0.06 | 0.29 | 500 | 0.5 | 450 | 0.75 | 375 | 1 | 325 | 22.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1*240 AL XLPE 12/20 flat | 240 Al | 20 | 0 | 0.126 | 0.174 | 0.29 | 0.004 | 0.83 | 0.06 | 0.29 | 580 | 0.5 | 450 | 0.75 | 370 | 1 | 325 | 22.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1*400 AL XLPE 12/20 trefoil | 400 Al | 20 | 0 | 0.08 | 0.108 | 0.34 | 0.004 | 0.78 | 0.05 | 0.34 | 660 | 0.5 | 560 | 0.75 | 465 | 1 | 405 | 38.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1*400 AL XLPE 12/20 flat | 400 Al | 20 | 0 | 0.08 | 0.166 | 0.34 | 0.004 | 0.78 | 0.05 | 0.34 | 720 | 0.5 | 550 | 0.75 | 450 | 1 | 390 | 38.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1*630 AL XLPE 12/20 trefoil | 630 Al | 20 | 0 | 0.049 | 0.101 | 0.42 | 0.004 | 0.75 | 0.05 | 0.42 | 890 | 0.5 | 710 | 0.75 | 590 | 1 | 510 | 59.9 | 20 | 90 | 250 | 50 | 150 | 0
3x1*630 AL XLPE 12/20 flat | 630 Al | 20 | 0 | 0.049 | 0.159 | 0.42 | 0.004 | 0.75 | 0.05 | 0.42 | 930 | 0.5 | 670 | 0.75 | 550 | 1 | 475 | 59.9 | 20 | 90 | 250 | 50 | 150 | 0
3x1*800 AL XLPE 12/20 trefoil | 800 Al | 20 | 0 | 0.038 | 0.099 | 0.46 | 0.004 | 0.72 | 0.04 | 0.46 | 1020 | 0.5 | 800 | 0.75 | 665 | 1 | 575 | 74 | 20 | 90 | 250 | 50 | 150 | 0
3x1*800 AL XLPE 12/20 flat | 800 Al | 20 | 0 | 0.038 | 0.153 | 0.46 | 0.004 | 0.72 | 0.04 | 0.46 | 1100 | 0.5 | 750 | 0.75 | 625 | 1 | 540 | 74 | 20 | 90 | 250 | 50 | 150 | 0
3x1*150 AL XLPE 18/30 trefoil | 150 Al | 30 | 0 | 0.205 | 0.134 | 0.19 | 0.004 | 0.91 | 0.08 | 0.19 | 375 | 0.5 | 350 | 0.75 | 290 | 1 | 255 | 14.3 | 20 | 90 | 250 | 50 | 150 | 0
3x1*150 AL XLPE 18/30 flat | 150 Al | 30 | 0 | 0.205 | 0.192 | 0.19 | 0.004 | 0.91 | 0.08 | 0.19 | 425 | 0.5 | 365 | 0.75 | 305 | 1 | 265 | 14.3 | 20 | 90 | 250 | 50 | 150 | 0
3x1*240 AL XLPE 18/30 trefoil | 240 Al | 30 | 0 | 0.126 | 0.123 | 0.22 | 0.004 | 0.83 | 0.07 | 0.22 | 510 | 0.5 | 455 | 0.75 | 380 | 1 | 330 | 22.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1*240 AL XLPE 18/30 flat | 240 Al | 30 | 0 | 0.126 | 0.181 | 0.22 | 0.004 | 0.83 | 0.07 | 0.22 | 570 | 0.5 | 470 | 0.75 | 385 | 1 | 335 | 22.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1*400 AL XLPE 18/30 trefoil | 400 Al | 30 | 0 | 0.08 | 0.115 | 0.26 | 0.004 | 0.43 | 0.06 | 0.26 | 670 | 0.5 | 570 | 0.75 | 470 | 1 | 410 | 38.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1*400 AL XLPE 18/30 flat | 400 Al | 30 | 0 | 0.08 | 0.173 | 0.26 | 0.004 | 0.43 | 0.06 | 0.26 | 720 | 0.5 | 560 | 0.75 | 455 | 1 | 395 | 38.8 | 20 | 90 | 250 | 50 | 150 | 0
3x1*630 AL XLPE 18/30 trefoil | 630 Al | 30 | 0 | 0.049 | 0.106 | 0.31 | 0.004 | 0.4 | 0.05 | 0.31 | 890 | 0.5 | 720 | 0.75 | 600 | 1 | 520 | 59.9 | 20 | 90 | 250 | 50 | 150 | 0
3x1*630 AL XLPE 18/30 flat | 630 Al | 30 | 0 | 0.049 | 0.164 | 0.31 | 0.004 | 0.4 | 0.05 | 0.31 | 920 | 0.5 | 680 | 0.75 | 550 | 1 | 480 | 59.9 | 20 | 90 | 250 | 50 | 150 | 0
3* 50 CU XLPE 6/10 | 50 Cu | 10 | 0 | 0.387 | 0.11 | 0.26 | 0.004 | 2.5 | 0.14 | 0.26 | 210 | 0.5 | 245 | 0.75 | 205 | 1 | 180 | 6.5 | 20 | 90 | 250 | 50 | 150 | 0
3* 95 CU XLPE 6/10 | 95 Cu | 10 | 0 | 0.194 | 0.099 | 0.32 | 0.004 | 2.3 | 0.13 | 0.32 | 315 | 0.5 | 355 | 0.75 | 295 | 1 | 255 | 12.3 | 20 | 90 | 250 | 50 | 150 | 0
3*150 CU XLPE 6/10 | 150 Cu | 10 | 0 | 0.126 | 0.093 | 0.38 | 0.004 | 2.24 | 0.12 | 0.38 | 405 | 0.5 | 440 | 0.75 | 365 | 1 | 320 | 19.4 | 20 | 90 | 250 | 50 | 150 | 0
3*185 CU XLPE 6/10 | 185 Cu | 10 | 0 | 0.101 | 0.091 | 0.41 | 0.004 | 2.22 | 0.11 | 0.41 | 465 | 0.5 | 495 | 0.75 | 415 | 1 | 360 | 25 | 20 | 90 | 250 | 50 | 150 | 0
3*240 CU XLPE 6/10 | 240 Cu | 10 | 0 | 0.078 | 0.088 | 0.43 | 0.004 | 2.19 | 0.11 | 0.43 | 530 | 0.5 | 550 | 0.75 | 460 | 1 | 400 | 31 | 20 | 90 | 250 | 50 | 150 | 0
3* 50 CU XLPE 8,7/15 | 50 Cu | 15 | 0 | 0.387 | 0.117 | 0.21 | 0.004 | 2.5 | 0.14 | 0.21 | 210 | 0.5 | 245 | 0.75 | 205 | 1 | 180 | 6.5 | 20 | 90 | 250 | 50 | 150 | 0
3* 95 CU XLPE 8,7/15 | 95 Cu | 15 | 0 | 0.194 | 0.105 | 0.26 | 0.004 | 2.3 | 0.13 | 0.26 | 315 | 0.5 | 355 | 0.75 | 295 | 1 | 255 | 12.3 | 20 | 90 | 250 | 50 | 150 | 0
3*150 CU XLPE 8,7/15 | 150 Cu | 15 | 0 | 0.126 | 0.098 | 0.31 | 0.004 | 2.24 | 0.12 | 0.31 | 405 | 0.5 | 440 | 0.75 | 365 | 1 | 320 | 19.4 | 20 | 90 | 250 | 50 | 150 | 0
3* 50 CU XLPE 12/20 | 50 Cu | 20 | 0 | 0.387 | 0.123 | 0.18 | 0.004 | 2.5 | 0.13 | 0.18 | 215 | 0.5 | 250 | 0.75 | 210 | 1 | 180 | 6.5 | 20 | 90 | 250 | 50 | 150 | 0
3* 95 CU XLPE 12/20 | 95 Cu | 20 | 0 | 0.194 | 0.11 | 0.23 | 0.004 | 2.3 | 0.13 | 0.23 | 320 | 0.5 | 355 | 0.75 | 295 | 1 | 260 | 12.3 | 20 | 90 | 250 | 50 | 150 | 0
3*150 CU XLPE 12/20 | 150 Cu | 20 | 0 | 0.126 | 0.103 | 0.26 | 0.004 | 2.24 | 0.13 | 0.26 | 410 | 0.5 | 440 | 0.75 | 365 | 1 | 320 | 19.4 | 20 | 90 | 250 | 50 | 150 | 0
3* 95 AL Kudi 6/10 | 95 Al | 10 | 0 | 0.322 | 0.102 | 0.32 | 0.004 | 1.07 | 0.11 | 0.32 | 250 | 0.5 | 239 | 0.75 | 215 | 1 | 202 | 8.9 | 20 | 90 | 250 | 50 | 150 | 0 | 0.3706 | 0.8429 | 0.0484 | 0.7377 | 0.0485 | 0.7375 | 0.2971 | 0.7324 | 0.0495 | 0.732
3*150 AL Kudi 6/10 | 150 Al | 10 | 0 | 0.208 | 0.093 | 0.37 | 0.004 | 0.96 | 0.11 | 0.37 | 330 | 0.5 | 311 | 0.75 | 280 | 1 | 263 | 14.1 | 20 | 90 | 250 | 50 | 150 | 0 | 0.2564 | 0.8299 | 0.0485 | 0.7337 | 0.0486 | 0.7348 | 0.2969 | 0.7277 | 0.0495 | 0.7278
3*185 AL 6/10 | 185 Al | 10 | 0 | 0.167 | 0.091 | 0.41 | 0.004 | 0.92 | 0.11 | 0.41 | 395 | 0.5 | 355 | 0.75 | 320 | 1 | 300 | 18.3 | 20 | 90 | 250 | 50 | 150 | 0 | 0.2158 | 0.8219 | 0.0487 | 0.7294 | 0.0487 | 0.7302 | 0.297 | 0.7226 | 0.0495 | 0.7227
3*240 AL Kudi 6/10 | 240 Al | 10 | 0 | 0.126 | 0.089 | 0.45 | 0.004 | 0.88 | 0.1 | 0.45 | 455 | 0.5 | 400 | 0.75 | 360 | 1 | 338 | 22.6 | 20 | 90 | 250 | 50 | 150 | 0 | 0.1752 | 0.8138 | 0.0488 | 0.7251 | 0.0488 | 0.7256 | 0.297 | 0.7175 | 0.0495 | 0.7175
3x1*630 CU XLPE 6/10 trefoil | 630 Cu | 10 | 0 | 0.0345 | 0.0892 | 0.72 | 0.004 | 0.3 | 0.05 | 0.72 | 1070 | 0.5 | 770 | 0.75 | 630 | 1 | 550 | 90 | 20 | 90 | 250 | 50 | 150 | 0
3x1*630 CU XLPE 6/10 flat | 630 Cu | 10 | 0 | 0.0315 | 0.1602 | 0.72 | 0.004 | 0.3 | 0.05 | 0.72 | 1070 | 0.5 | 670 | 0.75 | 550 | 1 | 480 | 90 | 20 | 90 | 250 | 50 | 150 | 0
3x1*800 CU XLPE 6/10 trefoil | 800 Cu | 10 | 0 | 0.0293 | 0.0877 | 0.8 | 0.004 | 0.3 | 0.04 | 0.8 | 1200 | 0.5 | 840 | 0.75 | 690 | 1 | 600 | 114 | 20 | 90 | 250 | 50 | 150 | 0
3x1*800 CU XLPE 6/10 flat | 800 Cu | 10 | 0 | 0.0261 | 0.1551 | 0.8 | 0.004 | 0.3 | 0.05 | 0.8 | 1180 | 0.5 | 720 | 0.75 | 590 | 1 | 510 | 114 | 20 | 90 | 250 | 50 | 150 | 0
3x1*1000 CU XLPE 6/10 trefoil | 1000 Cu | 10 | 0 | 0.0257 | 0.086 | 0.89 | 0.004 | 0.3 | 0.04 | 0.89 | 1340 | 0.5 | 900 | 0.75 | 740 | 1 | 640 | 143 | 20 | 90 | 250 | 50 | 150 | 0
3x1*1000 CU XLPE 6/10 flat | 1000 Cu | 10 | 0 | 0.0222 | 0.1502 | 0.89 | 0.004 | 0.3 | 0.05 | 0.89 | 1300 | 0.5 | 770 | 0.75 | 630 | 1 | 540 | 143 | 20 | 90 | 250 | 50 | 150 | 0
3x1*1200 CU XLPE 6/10 trefoil | 1200 Cu | 10 | 0 | 0.0174 | 0.0828 | 1.05 | 0.004 | 0.2 | 0.04 | 1.05 | 1590 | 0.5 | 1030 | 0.75 | 840 | 1 | 730 | 172 | 20 | 90 | 250 | 50 | 150 | 0
3x1*1200 CU XLPE 6/10 flat | 1200 Cu | 10 | 0 | 0.0164 | 0.1437 | 1.05 | 0.004 | 0.2 | 0.04 | 1.05 | 1450 | 0.5 | 840 | 0.75 | 680 | 1 | 590 | 172 | 20 | 90 | 250 | 50 | 150 | 0
3x1*1400 CU XLPE 6/10 trefoil | 1400 Cu | 10 | 0 | 0.0155 | 0.0826 | 1.15 | 0.004 | 0.2 | 0.04 | 1.15 | 1740 | 0.5 | 1090 | 0.75 | 890 | 1 | 770 | 200 | 20 | 90 | 250 | 50 | 150 | 0
3x1*1400 CU XLPE 6/10 flat | 1400 Cu | 10 | 0 | 0.0144 | 0.1402 | 1.15 | 0.004 | 0.2 | 0.04 | 1.15 | 1560 | 0.5 | 880 | 0.75 | 720 | 1 | 620 | 200 | 20 | 90 | 250 | 50 | 150 | 0
3x1*1600 CU XLPE 6/10 trefoil | 1600 Cu | 10 | 0 | 0.0142 | 0.0814 | 1.21 | 0.004 | 0.1 | 0.04 | 1.21 | 1850 | 0.5 | 1140 | 0.75 | 930 | 1 | 805 | 229 | 20 | 90 | 250 | 50 | 150 | 0
3x1*1600 CU XLPE 6/10 flat | 1600 Cu | 10 | 0 | 0.013 | 0.1378 | 1.21 | 0.004 | 0.1 | 0.04 | 1.21 | 1640 | 0.5 | 920 | 0.75 | 750 | 1 | 650 | 229 | 20 | 90 | 250 | 50 | 150 | 0
3x1*2000 CU XLPE 6/10 trefoil | 2000 Cu | 10 | 0 | 0.0123 | 0.0809 | 1.29 | 0.004 | 0.1 | 0.04 | 1.29 | 2010 | 0.5 | 1200 | 0.75 | 980 | 1 | 850 | 286 | 20 | 90 | 250 | 50 | 150 | 0
3x1*2000 CU XLPE 6/10 flat | 2000 Cu | 10 | 0 | 0.011 | 0.1353 | 1.29 | 0.004 | 0.1 | 0.04 | 1.29 | 1760 | 0.5 | 960 | 0.75 | 780 | 1 | 680 | 286 | 20 | 90 | 250 | 50 | 150 | 0
3* 35 CU GPLK 18/30 | 35 Cu | 30 | 0 | 0.56 | 0.16 | 0.19 | 0.003 | 4.26 | 0.27 | 0.19 | 105 | 0.5 | 120 | 0.75 | 112 | 1 | 105 | 4.5 | 40 | 40 | 160 | 50 | 167 | 0
3* 50 CU GPLK 18/30 | 50 Cu | 30 | 0 | 0.4 | 0.15 | 0.21 | 0.003 | 3.52 | 0.26 | 0.21 | 125 | 0.5 | 150 | 0.75 | 140 | 1 | 130 | 6.5 | 40 | 40 | 160 | 50 | 167 | 0
3* 70 CU GPLK 18/30 | 70 Cu | 30 | 0 | 0.28 | 0.14 | 0.23 | 0.003 | 2.97 | 0.22 | 0.23 | 150 | 0.5 | 180 | 0.75 | 170 | 1 | 160 | 9 | 40 | 40 | 160 | 50 | 167 | 0
3* 95 CU GPLK 18/30 | 95 Cu | 30 | 0 | 0.21 | 0.13 | 0.26 | 0.003 | 2.67 | 0.21 | 0.26 | 180 | 0.5 | 215 | 0.75 | 200 | 1 | 190 | 12.3 | 40 | 40 | 160 | 50 | 167 | 0
3*120 CU GPLK 18/30 | 120 Cu | 30 | 0 | 0.17 | 0.13 | 0.28 | 0.003 | 2.47 | 0.21 | 0.28 | 205 | 0.5 | 245 | 0.75 | 225 | 1 | 210 | 15.5 | 40 | 40 | 160 | 50 | 167 | 0
3*150 CU GPLK 18/30 | 150 Cu | 30 | 0 | 0.14 | 0.13 | 0.3 | 0.003 | 2.23 | 0.2 | 0.3 | 235 | 0.5 | 280 | 0.75 | 260 | 1 | 240 | 19.4 | 40 | 40 | 160 | 50 | 167 | 0
3*185 CU GPLK 18/30 | 185 Cu | 30 | 0 | 0.12 | 0.12 | 0.32 | 0.003 | 2.2 | 0.18 | 0.32 | 265 | 0.5 | 315 | 0.75 | 290 | 1 | 270 | 23.9 | 40 | 40 | 160 | 50 | 167 | 0
3*240 CU GPLK 18/30 | 240 Cu | 30 | 0 | 0.093 | 0.12 | 0.36 | 0.003 | 1.85 | 0.18 | 0.36 | 305 | 0.5 | 365 | 0.75 | 335 | 1 | 315 | 31 | 40 | 40 | 160 | 50 | 167 | 0

## Cable (2)
Name | mantel | Uo | Unom | #geleiders | geleiderdoorsnede | geleidermateriaal | aardschermdoorsnede | formatie | ks | xs² | ys | kp | xp² | yp' | dc | s | (dc/s)² | yp | Info | Shortname | Price | Rdc | R | X | C | Tan_delta | R0 | X0 | C0 | Inom0 | G1 | Inom1 | G2 | Inom2 | G3 | Inom3 | Ik1s | TR | TInom | TIk1s | Frequency | VoP
|  | kV | kV |  | mm² |  | mm² | [7 empty] | mm | mm |  |  |  |  | EUR/m | Ohm/km | Ohm/km | Ohm/km | µF/km |  | Ohm/km | Ohm/km | µF/km | A | Km/W | A | Km/W | A | Km/W | A | kA | °C | °C | °C | Hz | m/µs
3x1*25 Cu + as16 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 25 | Cu | 16 | flat | 1 | 0.17285 | 0.00015559 | 1 | 0.17285 | 0.00015559 | 6 | 27 | 0.049383 | 3.368e-05 |  | 25 Cu |  | 0.727 | 0.727 | 0.246 | 0.22 | 0.004 | 4.1 | 0.78 | 0.22 | 195 | 0.5 | 158 | 0.75 | 150 | 1 | 143 | 3.6 | 20 | 90 | 250 | 50 | 150
3x1*35 Cu + as16 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 35 | Cu | 16 | flat | 1 | 0.23982 | 0.00029947 | 1 | 0.23982 | 0.00029947 | 7.1 | 28 | 0.064298 | 8.4446e-05 |  | 35 Cu |  | 0.524 | 0.524 | 0.231 | 0.24 | 0.004 | 3.9 | 0.76 | 0.24 | 235 | 0.5 | 184 | 0.75 | 175 | 1 | 166 | 5 | 20 | 90 | 250 | 50 | 150
3x1*50 Cu + as25 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 50 | Cu | 25 | flat | 1 | 0.32471 | 0.00054892 | 1 | 0.32471 | 0.00054892 | 8.2 | 29 | 0.079952 | 0.00019251 |  | 50 Cu |  | 0.387 | 0.387 | 0.224 | 0.26 | 0.004 | 2.6 | 0.74 | 0.26 | 280 | 0.5 | 215 | 0.75 | 205 | 1 | 195 | 7.2 | 20 | 90 | 250 | 50 | 150
3x1*70 Cu + as25 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 70 | Cu | 25 | flat | 1 | 0.46889 | 0.0011441 | 1 | 0.46889 | 0.0011441 | 9.9 | 30 | 0.1089 | 0.00054644 |  | 70 Cu |  | 0.268 | 0.268 | 0.214 | 0.3 | 0.004 | 2.5 | 0.72 | 0.3 | 350 | 0.5 | 257 | 0.75 | 245 | 1 | 233 | 10 | 20 | 90 | 250 | 50 | 150
3x1*95 Cu + as25 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 95 | Cu | 25 | flat | 1 | 0.65111 | 0.0022041 | 1 | 0.65111 | 0.0022041 | 11.5 | 32 | 0.12915 | 0.0012455 | 186100 | 95 Cu |  | 0.193 | 0.194 | 0.206 | 0.33 | 0.004 | 2.354 | 0.699 | 0.33 | 425 | 0.5 | 305 | 0.75 | 290 | 1 | 276 | 13.6 | 20 | 90 | 250 | 50 | 150
3x1*120 Cu + as25 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 120 | Cu | 25 | flat | 1 | 0.82133 | 0.0035036 | 1 | 0.82133 | 0.0035036 | 13 | 34 | 0.14619 | 0.0022332 |  | 120 Cu |  | 0.153 | 0.154 | 0.2 | 0.36 | 0.004 | 2.3 | 0.67 | 0.36 | 485 | 0.5 | 341 | 0.75 | 325 | 1 | 309 | 17.2 | 20 | 90 | 250 | 50 | 150
3x1*150 Cu + as25 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 150 | Cu | 25 | flat | 1 | 1.0134 | 0.0053262 | 1 | 1.0134 | 0.0053262 | 14.5 | 35 | 0.17163 | 0.0039669 | 186101 | 150 Cu |  | 0.124 | 0.125 | 0.194 | 0.39 | 0.004 | 2.265 | 0.649 | 0.39 | 550 | 0.5 | 378 | 0.75 | 360 | 1 | 342 | 21.5 | 20 | 90 | 250 | 50 | 150
3x1*185 Cu + as25 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 185 | Cu | 25 | flat | 1 | 1.268 | 0.008319 | 1 | 1.268 | 0.008319 | 16.1 | 37 | 0.18934 | 0.0067712 |  | 185 Cu |  | 0.0991 | 0.101 | 0.189 | 0.42 | 0.004 | 2.24 | 0.63 | 0.42 | 625 | 0.5 | 420 | 0.75 | 400 | 1 | 380 | 26.5 | 20 | 90 | 250 | 50 | 150
3x1*240 Cu + as25 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 240 | Cu | 25 | flat | 1 | 1.6666 | 0.014301 | 1 | 1.6666 | 0.014301 | 18.6 | 39 | 0.22746 | 0.013732 | 186102 | 240 Cu |  | 0.0754 | 0.0775 | 0.182 | 0.47 | 0.004 | 2.204 | 0.598 | 0.47 | 730 | 0.5 | 478 | 0.75 | 455 | 1 | 432 | 34.3 | 20 | 90 | 250 | 50 | 150
3x1*300 Cu + as35 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 300 | Cu | 35 | flat | 1 | 2.0909 | 0.022363 | 1 | 2.0909 | 0.022363 | 20.6 | 41 | 0.25244 | 0.02323 |  | 300 Cu |  | 0.0601 | 0.0628 | 0.177 | 0.51 | 0.004 | 1.7 | 0.58 | 0.51 | 825 | 0.5 | 530 | 0.75 | 505 | 1 | 480 | 42.9 | 20 | 90 | 250 | 50 | 150
3x1*400 Cu + as50 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 400 | Cu | 50 | flat | 1 | 2.6737 | 0.036156 | 1 | 2.6737 | 0.036156 | 24 | 45 | 0.28444 | 0.040551 | 186103 | 400 Cu |  | 0.047 | 0.0506 | 0.172 | 0.58 | 0.004 | 1.142 | 0.551 | 0.58 | 880 | 0.5 | 541 | 0.75 | 515 | 1 | 489 | 57.2 | 20 | 90 | 250 | 50 | 150
3x1*500 Cu + as50 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 500 | Cu | 50 | flat | 1 | 3.4334 | 0.058524 | 1 | 3.4334 | 0.058524 | 27.2 | 48 | 0.32111 | 0.069383 | 186104 | 500 Cu |  | 0.0366 | 0.0413 | 0.166 | 0.64 | 0.004 | 1.129 | 0.528 | 0.64 | 985 | 0.5 | 588 | 0.75 | 560 | 1 | 532 | 71.5 | 20 | 90 | 250 | 50 | 150
3x1*630 Cu + as50 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 630 | Cu | 50 | flat | 1 | 4.4404 | 0.094898 | 1 | 4.4404 | 0.094898 | 31.1 | 52 | 0.3577 | 0.11356 | 186105 | 630 Cu |  | 0.0283 | 0.0342 | 0.16 | 0.72 | 0.004 | 1.123 | 0.5 | 0.72 | 1095 | 0.5 | 646 | 0.75 | 615 | 1 | 584 | 90.1 | 20 | 90 | 250 | 50 | 150
3x1*25 Cu + as16 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 25 | Cu | 16 | trefoil | 1 | 0.17285 | 0.00015559 | 1 | 0.17285 | 0.00015559 | 6 | 27 | 0.049383 | 3.368e-05 |  | 25 Cu |  | 0.727 | 0.727 | 0.153 | 0.22 | 0.004 | 4.1 | 0.46 | 0.22 | 160 | 0.5 | 142 | 0.75 | 135 | 1 | 128 | 3.6 | 20 | 90 | 250 | 50 | 150
3x1*35 Cu + as16 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 35 | Cu | 16 | trefoil | 1 | 0.23982 | 0.00029947 | 1 | 0.23982 | 0.00029947 | 7.1 | 28 | 0.064298 | 8.4446e-05 |  | 35 Cu |  | 0.524 | 0.524 | 0.144 | 0.24 | 0.004 | 3.9 | 0.44 | 0.24 | 195 | 0.5 | 173 | 0.75 | 165 | 1 | 157 | 5 | 20 | 90 | 250 | 50 | 150
3x1*50 Cu + as25 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 50 | Cu | 25 | trefoil | 1 | 0.32471 | 0.00054892 | 1 | 0.32471 | 0.00054892 | 8.2 | 29 | 0.079952 | 0.00019251 |  | 50 Cu |  | 0.387 | 0.387 | 0.138 | 0.26 | 0.004 | 2.6 | 0.42 | 0.26 | 235 | 0.5 | 200 | 0.75 | 190 | 1 | 181 | 7.2 | 20 | 90 | 250 | 50 | 150
3x1*70 Cu + as25 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 70 | Cu | 25 | trefoil | 1 | 0.46889 | 0.0011441 | 1 | 0.46889 | 0.0011441 | 9.9 | 30 | 0.1089 | 0.00054644 |  | 70 Cu |  | 0.268 | 0.268 | 0.129 | 0.3 | 0.004 | 2.5 | 0.4 | 0.3 | 295 | 0.5 | 247 | 0.75 | 235 | 1 | 223 | 10 | 20 | 90 | 250 | 50 | 150
3x1*95 Cu + as25 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 95 | Cu | 25 | trefoil | 1 | 0.65111 | 0.0022041 | 1 | 0.65111 | 0.0022041 | 11.5 | 32 | 0.12915 | 0.0012455 | 186100 | 95 Cu |  | 0.193 | 0.194 | 0.123 | 0.33 | 0.004 | 2.354 | 0.385 | 0.33 | 355 | 0.5 | 294 | 0.75 | 280 | 1 | 266 | 13.6 | 20 | 90 | 250 | 50 | 150
3x1*120 Cu + as25 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 120 | Cu | 25 | trefoil | 1 | 0.82133 | 0.0035036 | 1 | 0.82133 | 0.0035036 | 13 | 34 | 0.14619 | 0.0022332 |  | 120 Cu |  | 0.153 | 0.154 | 0.119 | 0.36 | 0.004 | 2.3 | 0.37 | 0.36 | 410 | 0.5 | 331 | 0.75 | 315 | 1 | 299 | 17.2 | 20 | 90 | 250 | 50 | 150
3x1*150 Cu + as25 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 150 | Cu | 25 | trefoil | 1 | 1.0134 | 0.0053262 | 1 | 1.0134 | 0.0053262 | 14.5 | 35 | 0.17163 | 0.0039669 | 186101 | 150 Cu |  | 0.124 | 0.125 | 0.114 | 0.39 | 0.004 | 2.266 | 0.352 | 0.39 | 465 | 0.5 | 368 | 0.75 | 350 | 1 | 333 | 21.5 | 20 | 90 | 250 | 50 | 150
3x1*185 Cu + as25 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 185 | Cu | 25 | trefoil | 1 | 1.268 | 0.008319 | 1 | 1.268 | 0.008319 | 16.1 | 37 | 0.18934 | 0.0067712 |  | 185 Cu |  | 0.0991 | 0.101 | 0.111 | 0.42 | 0.004 | 2.24 | 0.34 | 0.42 | 535 | 0.5 | 415 | 0.75 | 395 | 1 | 375 | 26.5 | 20 | 90 | 250 | 50 | 150
3x1*240 Cu + as25 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 240 | Cu | 25 | trefoil | 1 | 1.6666 | 0.014301 | 1 | 1.6666 | 0.014301 | 18.6 | 39 | 0.22746 | 0.013732 | 186102 | 240 Cu |  | 0.0754 | 0.0775 | 0.106 | 0.47 | 0.004 | 2.205 | 0.317 | 0.47 | 630 | 0.5 | 478 | 0.75 | 455 | 1 | 432 | 34.3 | 20 | 90 | 250 | 50 | 150
3x1*300 Cu + as35 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 300 | Cu | 35 | trefoil | 1 | 2.0909 | 0.022363 | 1 | 2.0909 | 0.022363 | 20.6 | 41 | 0.25244 | 0.02323 |  | 300 Cu |  | 0.0601 | 0.0628 | 0.103 | 0.51 | 0.004 | 1.7 | 0.3 | 0.51 | 720 | 0.5 | 536 | 0.75 | 510 | 1 | 485 | 42.9 | 20 | 90 | 250 | 50 | 150
3x1*400 Cu + as50 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 400 | Cu | 50 | trefoil | 1 | 2.6737 | 0.036156 | 1 | 2.6737 | 0.036156 | 24 | 45 | 0.28444 | 0.040551 | 186103 | 400 Cu |  | 0.047 | 0.0506 | 0.099 | 0.58 | 0.004 | 1.143 | 0.286 | 0.58 | 825 | 0.5 | 588 | 0.75 | 560 | 1 | 532 | 57.2 | 20 | 90 | 250 | 50 | 150
3x1*500 Cu + as50 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 500 | Cu | 50 | trefoil | 1 | 3.4334 | 0.058524 | 1 | 3.4334 | 0.058524 | 27.2 | 48 | 0.32111 | 0.069383 | 186104 | 500 Cu |  | 0.0366 | 0.0413 | 0.095 | 0.64 | 0.004 | 1.131 | 0.277 | 0.64 | 940 | 0.5 | 662 | 0.75 | 630 | 1 | 599 | 71.5 | 20 | 90 | 250 | 50 | 150
3x1*630 Cu + as50 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 630 | Cu | 50 | trefoil | 1 | 4.4404 | 0.094898 | 1 | 4.4404 | 0.094898 | 31.1 | 52 | 0.3577 | 0.11356 | 186105 | 630 Cu |  | 0.0283 | 0.0342 | 0.092 | 0.72 | 0.004 | 1.126 | 0.265 | 0.72 | 1070 | 0.5 | 735 | 0.75 | 700 | 1 | 665 | 90.1 | 20 | 90 | 250 | 50 | 150
3x1*70 Al + as25 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 70 | Al | 25 | flat | 1 | 0.28367 | 0.00041895 | 1 | 0.28367 | 0.00041895 | 9.1 | 30 | 0.092011 | 0.00016932 | 186000 | 70 Al |  | 0.443 | 0.443 | 0.226 | 0.28 | 0.004 | 2.7 | 0.758 | 0.28 | 270 | 0.5 | 205 | 0.75 | 195 | 1 | 185 | 6.6 | 20 | 90 | 250 | 50 | 150
3x1*95 Al + as25 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 95 | Al | 25 | flat | 1 | 0.3927 | 0.00080267 | 1 | 0.3927 | 0.00080267 | 10.8 | 31 | 0.12137 | 0.0004282 | 186001 | 95 Al |  | 0.32 | 0.32 | 0.218 | 0.31 | 0.004 | 2.505 | 0.72 | 0.31 | 330 | 0.5 | 242 | 0.75 | 230 | 1 | 219 | 8.9 | 20 | 90 | 250 | 50 | 150
3x1*120 Al + as25 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 120 | Al | 25 | flat | 1 | 0.49669 | 0.0012836 | 1 | 0.49669 | 0.0012836 | 12.1 | 33 | 0.13444 | 0.00075788 |  | 120 Al |  | 0.253 | 0.254 | 0.212 | 0.34 | 0.004 | 2.45 | 0.7 | 0.34 | 380 | 0.5 | 273 | 0.75 | 260 | 1 | 247 | 11.3 | 20 | 90 | 250 | 50 | 150
3x1*150 Al + as25 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 150 | Al | 25 | flat | 1 | 0.61002 | 0.0019351 | 1 | 0.61002 | 0.0019351 | 13.3 | 34 | 0.15302 | 0.001299 | 186002 | 150 Al |  | 0.206 | 0.207 | 0.207 | 0.36 | 0.004 | 2.41 | 0.677 | 0.36 | 430 | 0.5 | 299 | 0.75 | 285 | 1 | 271 | 14.1 | 20 | 90 | 250 | 50 | 150
3x1*185 Al + as25 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 185 | Al | 25 | flat | 1 | 0.76624 | 0.0030505 | 1 | 0.76624 | 0.0030505 | 14.9 | 35 | 0.18123 | 0.0024204 |  | 185 Al |  | 0.164 | 0.165 | 0.202 | 0.4 | 0.004 | 2.35 | 0.65 | 0.4 | 495 | 0.5 | 336 | 0.75 | 320 | 1 | 304 | 17.4 | 20 | 90 | 250 | 50 | 150
3x1*240 Al + as25 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 240 | Al | 25 | flat | 1 | 1.0053 | 0.0052417 | 1 | 1.0053 | 0.0052417 | 17.1 | 38 | 0.2025 | 0.0046176 | 186003 | 240 Al |  | 0.125 | 0.126 | 0.195 | 0.44 | 0.004 | 2.267 | 0.623 | 0.44 | 580 | 0.5 | 383 | 0.75 | 365 | 1 | 347 | 22.6 | 20 | 90 | 250 | 50 | 150
3x1*300 Al + as35 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 300 | Al | 35 | flat | 1 | 1.2566 | 0.0081709 | 1 | 1.2566 | 0.0081709 | 19.1 | 40 | 0.22801 | 0.0080354 |  | 300 Al |  | 0.1 | 0.102 | 0.19 | 0.48 | 0.004 | 1.7 | 0.6 | 0.48 | 660 | 0.5 | 431 | 0.75 | 410 | 1 | 390 | 28.2 | 20 | 90 | 250 | 50 | 150
3x1*400 Al + as50 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 400 | Al | 50 | flat | 1 | 1.6152 | 0.013442 | 1 | 1.6152 | 0.013442 | 21.7 | 42 | 0.26694 | 0.015237 | 186004 | 400 Al |  | 0.0778 | 0.08 | 0.186 | 0.53 | 0.004 | 1.181 | 0.581 | 0.53 | 735 | 0.5 | 457 | 0.75 | 435 | 1 | 413 | 37.6 | 20 | 90 | 250 | 50 | 150
3x1*500 Al + as50 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 500 | Al | 50 | flat | 1 | 2.0771 | 0.022073 | 1 | 2.0771 | 0.022073 | 24.6 | 45 | 0.29884 | 0.027266 |  | 500 Al |  | 0.0605 | 0.0635 | 0.18 | 0.59 | 0.004 | 1.16 | 0.56 | 0.59 | 835 | 0.5 | 504 | 0.75 | 480 | 1 | 456 | 47 | 20 | 90 | 250 | 50 | 150
3x1*630 Al + as50 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 630 | Al | 50 | flat | 1 | 2.6794 | 0.036305 | 1 | 2.6794 | 0.036305 | 27.9 | 48 | 0.33785 | 0.048546 | 186006 | 630 Al |  | 0.0469 | 0.0509 | 0.174 | 0.66 | 0.004 | 1.142 | 0.529 | 0.66 | 940 | 0.5 | 557 | 0.75 | 530 | 1 | 504 | 59.2 | 20 | 90 | 250 | 50 | 150
3x1*800 Al + as50 YMeKrvas 6/10 flat | YMeKrvas | 6 | 10 | 3x1 | 800 | Al | 50 | flat | 1 | 3.4241 | 0.05822 | 1 | 3.4241 | 0.05822 | 31.5 | 52 | 0.36696 | 0.079254 | 186008 | 800 Al |  | 0.0367 | 0.0417 | 0.168 | 0.73 | 0.004 | 1.129 | 0.509 | 0.73 | 1055 | 0.5 | 609 | 0.75 | 580 | 1 | 551 | 75.2 | 20 | 90 | 250 | 50 | 150
3x1*70 Al + as25 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 70 | Al | 25 | trefoil | 1 | 0.28367 | 0.00041895 | 1 | 0.28367 | 0.00041895 | 9.1 | 30 | 0.092011 | 0.00016932 | 186000 | 70 Al |  | 0.443 | 0.443 | 0.141 | 0.28 | 0.004 | 2.7 | 0.429 | 0.28 | 230 | 0.5 | 189 | 0.75 | 180 | 1 | 171 | 6.6 | 20 | 90 | 250 | 50 | 150
3x1*95 Al + as25 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 95 | Al | 25 | trefoil | 1 | 0.3927 | 0.00080267 | 1 | 0.3927 | 0.00080267 | 10.8 | 31 | 0.12137 | 0.0004282 | 186001 | 95 Al |  | 0.32 | 0.32 | 0.134 | 0.31 | 0.004 | 2.506 | 0.397 | 0.31 | 270 | 0.5 | 226 | 0.75 | 215 | 1 | 204 | 8.9 | 20 | 90 | 250 | 50 | 150
3x1*120 Al + as25 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 120 | Al | 25 | trefoil | 1 | 0.49669 | 0.0012836 | 1 | 0.49669 | 0.0012836 | 12.1 | 33 | 0.13444 | 0.00075788 |  | 120 Al |  | 0.253 | 0.254 | 0.13 | 0.34 | 0.004 | 2.45 | 0.38 | 0.34 | 320 | 0.5 | 257 | 0.75 | 245 | 1 | 233 | 11.3 | 20 | 90 | 250 | 50 | 150
3x1*150 Al + as25 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 150 | Al | 25 | trefoil | 1 | 0.61002 | 0.0019351 | 1 | 0.61002 | 0.0019351 | 13.3 | 34 | 0.15302 | 0.001299 | 186002 | 150 Al |  | 0.206 | 0.207 | 0.127 | 0.36 | 0.004 | 2.41 | 0.37 | 0.36 | 365 | 0.5 | 289 | 0.75 | 275 | 1 | 261 | 14.1 | 20 | 90 | 250 | 50 | 150
3x1*185 Al + as25 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 185 | Al | 25 | trefoil | 1 | 0.76624 | 0.0030505 | 1 | 0.76624 | 0.0030505 | 14.9 | 35 | 0.18123 | 0.0024204 |  | 185 Al |  | 0.164 | 0.165 | 0.122 | 0.4 | 0.004 | 2.35 | 0.36 | 0.4 | 420 | 0.5 | 326 | 0.75 | 310 | 1 | 295 | 17.4 | 20 | 90 | 250 | 50 | 150
3x1*240 Al + as25 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 240 | Al | 25 | trefoil | 1 | 1.0053 | 0.0052417 | 1 | 1.0053 | 0.0052417 | 17.1 | 38 | 0.2025 | 0.0046176 | 186003 | 240 Al |  | 0.125 | 0.126 | 0.118 | 0.44 | 0.004 | 2.268 | 0.337 | 0.44 | 495 | 0.5 | 373 | 0.75 | 355 | 1 | 337 | 22.6 | 20 | 90 | 250 | 50 | 150
3x1*300 Al + as35 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 300 | Al | 35 | trefoil | 1 | 1.2566 | 0.0081709 | 1 | 1.2566 | 0.0081709 | 19.1 | 40 | 0.22801 | 0.0080354 |  | 300 Al |  | 0.1 | 0.102 | 0.114 | 0.48 | 0.004 | 1.7 | 0.32 | 0.48 | 565 | 0.5 | 420 | 0.75 | 400 | 1 | 380 | 28.2 | 20 | 90 | 250 | 50 | 150
3x1*400 Al + as50 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 400 | Al | 50 | trefoil | 1 | 1.6152 | 0.013442 | 1 | 1.6152 | 0.013442 | 21.7 | 42 | 0.26694 | 0.015237 | 186004 | 400 Al |  | 0.0778 | 0.08 | 0.111 | 0.53 | 0.004 | 1.182 | 0.31 | 0.53 | 660 | 0.5 | 473 | 0.75 | 450 | 1 | 428 | 37.6 | 20 | 90 | 250 | 50 | 150
3x1*500 Al + as50 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 500 | Al | 50 | trefoil | 1 | 2.0771 | 0.022073 | 1 | 2.0771 | 0.022073 | 24.6 | 45 | 0.29884 | 0.027266 |  | 500 Al |  | 0.0605 | 0.0635 | 0.107 | 0.59 | 0.004 | 1.16 | 0.3 | 0.59 | 765 | 0.5 | 536 | 0.75 | 510 | 1 | 485 | 47 | 20 | 90 | 250 | 50 | 150
3x1*630 Al + as50 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 630 | Al | 50 | trefoil | 1 | 2.6794 | 0.036305 | 1 | 2.6794 | 0.036305 | 27.9 | 48 | 0.33785 | 0.048546 | 186006 | 630 Al |  | 0.0469 | 0.0509 | 0.103 | 0.66 | 0.004 | 1.143 | 0.282 | 0.66 | 880 | 0.5 | 604 | 0.75 | 575 | 1 | 546 | 59.2 | 20 | 90 | 250 | 50 | 150
3x1*800 Al + as50 YMeKrvas 6/10 trefoil | YMeKrvas | 6 | 10 | 3x1 | 800 | Al | 50 | trefoil | 1 | 3.4241 | 0.05822 | 1 | 3.4241 | 0.05822 | 31.5 | 52 | 0.36696 | 0.079254 | 186008 | 800 Al |  | 0.0367 | 0.0417 | 0.101 | 0.73 | 0.004 | 1.131 | 0.271 | 0.73 | 1010 | 0.5 | 672 | 0.75 | 640 | 1 | 608 | 75.2 | 20 | 90 | 250 | 50 | 150
3x1*16 Cu + as16 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 16 | Cu | 16 | flat | 1 | 0.10927 | 6.2187e-05 | 1 | 0.10927 | 6.2187e-05 | 5 | 28 | 0.031888 | 8.6842e-06 |  | 16 Cu |  | 1.15 | 1.15 | 0.257 | 0.16 | 0.004 | 4.6 | 0.88 | 0.16 | 150 | 0.5 | 126 | 0.75 | 120 | 1 | 114 | 2.3 | 20 | 90 | 250 | 50 | 150
3x1*25 Cu + as16 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 25 | Cu | 16 | flat | 1 | 0.17285 | 0.00015559 | 1 | 0.17285 | 0.00015559 | 6 | 29 | 0.042806 | 2.9181e-05 |  | 25 Cu |  | 0.727 | 0.727 | 0.247 | 0.18 | 0.004 | 4.2 | 0.85 | 0.18 | 195 | 0.5 | 158 | 0.75 | 150 | 1 | 143 | 3.6 | 20 | 90 | 250 | 50 | 150
3x1*35 Cu + as16 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 35 | Cu | 16 | flat | 1 | 0.23982 | 0.00029947 | 1 | 0.23982 | 0.00029947 | 7.1 | 30 | 0.056011 | 7.3519e-05 | 186107 | 35 Cu |  | 0.524 | 0.524 | 0.232 | 0.19 | 0.004 | 4.036 | 0.816 | 0.19 | 235 | 0.5 | 184 | 0.75 | 175 | 1 | 166 | 5 | 20 | 90 | 250 | 50 | 150
3x1*50 Cu + as25 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 50 | Cu | 25 | flat | 1 | 0.32471 | 0.00054892 | 1 | 0.32471 | 0.00054892 | 8.2 | 31 | 0.069969 | 0.00016835 | 186108 | 50 Cu |  | 0.387 | 0.387 | 0.225 | 0.21 | 0.004 | 2.603 | 0.777 | 0.21 | 280 | 0.5 | 215 | 0.75 | 205 | 1 | 195 | 7.2 | 20 | 90 | 250 | 50 | 150
3x1*70 Cu + as25 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 70 | Cu | 25 | flat | 1 | 0.46889 | 0.0011441 | 1 | 0.46889 | 0.0011441 | 9.9 | 33 | 0.09 | 0.00045099 | 186109 | 70 Cu |  | 0.268 | 0.268 | 0.215 | 0.24 | 0.004 | 2.45 | 0.738 | 0.24 | 350 | 0.5 | 257 | 0.75 | 245 | 1 | 233 | 10 | 20 | 90 | 250 | 50 | 150
3x1*95 Cu + as25 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 95 | Cu | 25 | flat | 1 | 0.65111 | 0.0022041 | 1 | 0.65111 | 0.0022041 | 11.5 | 34 | 0.1144 | 0.0011021 | 186110 | 95 Cu |  | 0.193 | 0.194 | 0.207 | 0.26 | 0.004 | 2.36 | 0.704 | 0.26 | 425 | 0.5 | 305 | 0.75 | 290 | 1 | 276 | 13.6 | 20 | 90 | 250 | 50 | 150
3x1*120 Cu + as25 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 120 | Cu | 25 | flat | 1 | 0.82133 | 0.0035036 | 1 | 0.82133 | 0.0035036 | 13 | 36 | 0.1304 | 0.0019897 | 186111 | 120 Cu |  | 0.153 | 0.154 | 0.201 | 0.28 | 0.004 | 2.297 | 0.676 | 0.28 | 485 | 0.5 | 341 | 0.75 | 325 | 1 | 309 | 17.2 | 20 | 90 | 250 | 50 | 150
3x1*150 Cu + as25 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 150 | Cu | 25 | flat | 1 | 1.0134 | 0.0053262 | 1 | 1.0134 | 0.0053262 | 14.5 | 37 | 0.15358 | 0.003545 | 186112 | 150 Cu |  | 0.124 | 0.125 | 0.195 | 0.31 | 0.004 | 2.266 | 0.657 | 0.31 | 550 | 0.5 | 378 | 0.75 | 360 | 1 | 342 | 21.5 | 20 | 90 | 250 | 50 | 150
3x1*185 Cu + as25 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 185 | Cu | 25 | flat | 1 | 1.268 | 0.008319 | 1 | 1.268 | 0.008319 | 16.1 | 39 | 0.17042 | 0.0060862 | 186113 | 185 Cu |  | 0.0991 | 0.101 | 0.19 | 0.33 | 0.004 | 2.234 | 0.633 | 0.33 | 625 | 0.5 | 420 | 0.75 | 400 | 1 | 380 | 26.5 | 20 | 90 | 250 | 50 | 150
3x1*240 Cu + as25 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 240 | Cu | 25 | flat | 1 | 1.6666 | 0.014301 | 1 | 1.6666 | 0.014301 | 18.6 | 41 | 0.20581 | 0.012405 | 186114 | 240 Cu |  | 0.0754 | 0.0774 | 0.183 | 0.37 | 0.004 | 2.204 | 0.603 | 0.37 | 730 | 0.5 | 478 | 0.75 | 455 | 1 | 432 | 34.3 | 20 | 90 | 250 | 50 | 150
3x1*300 Cu + as50 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 300 | Cu | 50 | flat | 1 | 2.0909 | 0.022363 | 1 | 2.0909 | 0.022363 | 20.6 | 43 | 0.22951 | 0.021083 | 186115 | 300 Cu |  | 0.0601 | 0.0627 | 0.178 | 0.4 | 0.004 | 1.158 | 0.571 | 0.4 | 825 | 0.5 | 530 | 0.75 | 505 | 1 | 480 | 42.9 | 20 | 90 | 250 | 50 | 150
3x1*400 Cu + as50 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 400 | Cu | 50 | flat | 1 | 2.6737 | 0.036156 | 1 | 2.6737 | 0.036156 | 24 | 47 | 0.26075 | 0.037103 | 186116 | 400 Cu |  | 0.047 | 0.0504 | 0.174 | 0.45 | 0.004 | 1.143 | 0.556 | 0.45 | 880 | 0.5 | 541 | 0.75 | 515 | 1 | 489 | 57.2 | 20 | 90 | 250 | 50 | 150
3x1*500 Cu + as50 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 500 | Cu | 50 | flat | 1 | 3.4334 | 0.058524 | 1 | 3.4334 | 0.058524 | 27.2 | 50 | 0.29594 | 0.063807 | 186117 | 500 Cu |  | 0.0366 | 0.0411 | 0.168 | 0.5 | 0.004 | 1.133 | 0.532 | 0.5 | 985 | 0.5 | 588 | 0.75 | 560 | 1 | 532 | 71.5 | 20 | 90 | 250 | 50 | 150
3x1*630 Cu + as50 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 630 | Cu | 50 | flat | 1 | 4.4404 | 0.094898 | 1 | 4.4404 | 0.094898 | 31.1 | 54 | 0.33169 | 0.10505 | 186118 | 630 Cu |  | 0.0283 | 0.034 | 0.161 | 0.56 | 0.004 | 1.124 | 0.508 | 0.56 | 1095 | 0.5 | 646 | 0.75 | 615 | 1 | 584 | 90.1 | 20 | 90 | 250 | 50 | 150
3x1*16 Cu + as16 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 16 | Cu | 16 | trefoil | 1 | 0.10927 | 6.2187e-05 | 1 | 0.10927 | 6.2187e-05 | 5 | 28 | 0.031888 | 8.6842e-06 |  | 16 Cu |  | 1.15 | 1.15 | 0.168 | 0.16 | 0.004 | 4.6 | 0.55 | 0.16 | 125 | 0.5 | 110 | 0.75 | 105 | 1 | 100 | 2.3 | 20 | 90 | 250 | 50 | 150
3x1*25 Cu + as16 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 25 | Cu | 16 | trefoil | 1 | 0.17285 | 0.00015559 | 1 | 0.17285 | 0.00015559 | 6 | 29 | 0.042806 | 2.9181e-05 |  | 25 Cu |  | 0.727 | 0.727 | 0.159 | 0.18 | 0.004 | 4.2 | 0.52 | 0.18 | 160 | 0.5 | 142 | 0.75 | 135 | 1 | 128 | 3.6 | 20 | 90 | 250 | 50 | 150
3x1*35 Cu + as16 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 35 | Cu | 16 | trefoil | 1 | 0.23982 | 0.00029947 | 1 | 0.23982 | 0.00029947 | 7.1 | 30 | 0.056011 | 7.3519e-05 | 186107 | 35 Cu |  | 0.524 | 0.524 | 0.149 | 0.19 | 0.004 | 4.036 | 0.486 | 0.19 | 195 | 0.5 | 173 | 0.75 | 165 | 1 | 157 | 5 | 20 | 90 | 250 | 50 | 150
3x1*50 Cu + as25 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 50 | Cu | 25 | trefoil | 1 | 0.32471 | 0.00054892 | 1 | 0.32471 | 0.00054892 | 8.2 | 31 | 0.069969 | 0.00016835 | 186108 | 50 Cu |  | 0.387 | 0.387 | 0.143 | 0.21 | 0.004 | 2.603 | 0.46 | 0.21 | 235 | 0.5 | 200 | 0.75 | 190 | 1 | 181 | 7.2 | 20 | 90 | 250 | 50 | 150
3x1*70 Cu + as25 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 70 | Cu | 25 | trefoil | 1 | 0.46889 | 0.0011441 | 1 | 0.46889 | 0.0011441 | 9.9 | 33 | 0.09 | 0.00045099 | 186109 | 70 Cu |  | 0.268 | 0.268 | 0.134 | 0.24 | 0.004 | 2.45 | 0.428 | 0.24 | 295 | 0.5 | 247 | 0.75 | 235 | 1 | 223 | 10 | 20 | 90 | 250 | 50 | 150
3x1*95 Cu + as25 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 95 | Cu | 25 | trefoil | 1 | 0.65111 | 0.0022041 | 1 | 0.65111 | 0.0022041 | 11.5 | 34 | 0.1144 | 0.0011021 | 186110 | 95 Cu |  | 0.193 | 0.194 | 0.128 | 0.26 | 0.004 | 2.36 | 0.401 | 0.26 | 355 | 0.5 | 294 | 0.75 | 280 | 1 | 266 | 13.6 | 20 | 90 | 250 | 50 | 150
3x1*120 Cu + as25 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 120 | Cu | 25 | trefoil | 1 | 0.82133 | 0.0035036 | 1 | 0.82133 | 0.0035036 | 13 | 36 | 0.1304 | 0.0019897 | 186111 | 120 Cu |  | 0.153 | 0.154 | 0.123 | 0.28 | 0.004 | 2.298 | 0.381 | 0.28 | 410 | 0.5 | 331 | 0.75 | 315 | 1 | 299 | 17.2 | 20 | 90 | 250 | 50 | 150
3x1*150 Cu + as25 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 150 | Cu | 25 | trefoil | 1 | 1.0134 | 0.0053262 | 1 | 1.0134 | 0.0053262 | 14.5 | 37 | 0.15358 | 0.003545 | 186112 | 150 Cu |  | 0.124 | 0.125 | 0.118 | 0.31 | 0.004 | 2.266 | 0.368 | 0.31 | 465 | 0.5 | 368 | 0.75 | 350 | 1 | 333 | 21.5 | 20 | 90 | 250 | 50 | 150
3x1*185 Cu + as25 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 185 | Cu | 25 | trefoil | 1 | 1.268 | 0.008319 | 1 | 1.268 | 0.008319 | 16.1 | 39 | 0.17042 | 0.0060862 | 186113 | 185 Cu |  | 0.0991 | 0.101 | 0.114 | 0.33 | 0.004 | 2.235 | 0.352 | 0.33 | 535 | 0.5 | 415 | 0.75 | 395 | 1 | 375 | 26.5 | 20 | 90 | 250 | 50 | 150
3x1*240 Cu + as25 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 240 | Cu | 25 | trefoil | 1 | 1.6666 | 0.014301 | 1 | 1.6666 | 0.014301 | 18.6 | 41 | 0.20581 | 0.012405 | 186114 | 240 Cu |  | 0.0754 | 0.0774 | 0.109 | 0.37 | 0.004 | 2.205 | 0.333 | 0.37 | 630 | 0.5 | 478 | 0.75 | 455 | 1 | 432 | 34.3 | 20 | 90 | 250 | 50 | 150
3x1*300 Cu + as50 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 300 | Cu | 50 | trefoil | 1 | 2.0909 | 0.022363 | 1 | 2.0909 | 0.022363 | 20.6 | 43 | 0.22951 | 0.021083 | 186115 | 300 Cu |  | 0.0601 | 0.0627 | 0.106 | 0.4 | 0.004 | 1.159 | 0.318 | 0.4 | 720 | 0.5 | 536 | 0.75 | 510 | 1 | 485 | 42.9 | 20 | 90 | 250 | 50 | 150
3x1*400 Cu + as50 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 400 | Cu | 50 | trefoil | 1 | 2.6737 | 0.036156 | 1 | 2.6737 | 0.036156 | 24 | 47 | 0.26075 | 0.037103 | 186116 | 400 Cu |  | 0.047 | 0.0504 | 0.102 | 0.45 | 0.004 | 1.145 | 0.302 | 0.45 | 825 | 0.5 | 588 | 0.75 | 560 | 1 | 532 | 57.2 | 20 | 90 | 250 | 50 | 150
3x1*500 Cu + as50 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 500 | Cu | 50 | trefoil | 1 | 3.4334 | 0.058524 | 1 | 3.4334 | 0.058524 | 27.2 | 50 | 0.29594 | 0.063807 | 186117 | 500 Cu |  | 0.0366 | 0.0411 | 0.098 | 0.5 | 0.004 | 1.135 | 0.289 | 0.5 | 940 | 0.5 | 662 | 0.75 | 630 | 1 | 599 | 71.5 | 20 | 90 | 250 | 50 | 150
3x1*630 Cu + as50 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 630 | Cu | 50 | trefoil | 1 | 4.4404 | 0.094898 | 1 | 4.4404 | 0.094898 | 31.1 | 54 | 0.33169 | 0.10505 | 186118 | 630 Cu |  | 0.0283 | 0.034 | 0.095 | 0.56 | 0.004 | 1.127 | 0.277 | 0.56 | 1070 | 0.5 | 735 | 0.75 | 700 | 1 | 665 | 90.1 | 20 | 90 | 250 | 50 | 150
3x1*70 Al + as25 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 70 | Al | 25 | flat | 1 | 0.28367 | 0.00041895 | 1 | 0.28367 | 0.00041895 | 9.1 | 32 | 0.080869 | 0.0001487 |  | 70 Al |  | 0.443 | 0.443 | 0.228 | 0.22 | 0.004 | 2.63 | 0.75 | 0.22 | 270 | 0.5 | 205 | 0.75 | 195 | 1 | 185 | 6.6 | 20 | 90 | 250 | 50 | 150
3x1*95 Al + as25 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 95 | Al | 25 | flat | 1 | 0.3927 | 0.00080267 | 1 | 0.3927 | 0.00080267 | 10.8 | 34 | 0.1009 | 0.00035546 |  | 95 Al |  | 0.32 | 0.32 | 0.219 | 0.25 | 0.004 | 2.51 | 0.73 | 0.25 | 330 | 0.5 | 242 | 0.75 | 230 | 1 | 219 | 8.9 | 20 | 90 | 250 | 50 | 150
3x1*120 Al + as25 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 120 | Al | 25 | flat | 1 | 0.49669 | 0.0012836 | 1 | 0.49669 | 0.0012836 | 12.1 | 35 | 0.11952 | 0.00067303 | 186022 | 120 Al |  | 0.253 | 0.253 | 0.213 | 0.27 | 0.004 | 2.44 | 0.704 | 0.27 | 380 | 0.5 | 273 | 0.75 | 260 | 1 | 247 | 11.3 | 20 | 90 | 250 | 50 | 150
3x1*150 Al + as25 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 150 | Al | 25 | flat | 1 | 0.61002 | 0.0019351 | 1 | 0.61002 | 0.0019351 | 13.3 | 36 | 0.13649 | 0.0011574 | 186023 | 150 Al |  | 0.206 | 0.207 | 0.209 | 0.29 | 0.004 | 2.372 | 0.681 | 0.29 | 430 | 0.5 | 299 | 0.75 | 285 | 1 | 271 | 14.1 | 20 | 90 | 250 | 50 | 150
3x1*185 Al + as25 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 185 | Al | 25 | flat | 1 | 0.76624 | 0.0030505 | 1 | 0.76624 | 0.0030505 | 14.9 | 38 | 0.15375 | 0.0020493 |  | 185 Al |  | 0.164 | 0.165 | 0.203 | 0.31 | 0.004 | 2.31 | 0.66 | 0.31 | 495 | 0.5 | 336 | 0.75 | 320 | 1 | 304 | 17.4 | 20 | 90 | 250 | 50 | 150
3x1*240 Al + as25 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 240 | Al | 25 | flat | 1 | 1.0053 | 0.0052417 | 1 | 1.0053 | 0.0052417 | 17.1 | 40 | 0.18276 | 0.0041615 | 186024 | 240 Al |  | 0.125 | 0.126 | 0.196 | 0.35 | 0.004 | 2.268 | 0.627 | 0.35 | 580 | 0.5 | 383 | 0.75 | 365 | 1 | 347 | 22.6 | 20 | 90 | 250 | 50 | 150
3x1*300 Al + as35 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 300 | Al | 35 | flat | 1 | 1.2566 | 0.0081709 | 1 | 1.2566 | 0.0081709 | 19.1 | 42 | 0.20681 | 0.0072772 | 186025 | 300 Al |  | 0.1 | 0.102 | 0.191 | 0.38 | 0.004 | 1.664 | 0.6 | 0.38 | 660 | 0.5 | 431 | 0.75 | 410 | 1 | 390 | 28.2 | 20 | 90 | 250 | 50 | 150
3x1*400 Al + as50 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 400 | Al | 50 | flat | 1 | 1.6152 | 0.013442 | 1 | 1.6152 | 0.013442 | 21.7 | 45 | 0.23254 | 0.01324 | 186026 | 400 Al |  | 0.0778 | 0.0799 | 0.188 | 0.42 | 0.004 | 1.181 | 0.585 | 0.42 | 735 | 0.5 | 457 | 0.75 | 435 | 1 | 413 | 37.6 | 20 | 90 | 250 | 50 | 150
3x1*500 Al + as50 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 500 | Al | 50 | flat | 1 | 2.0771 | 0.022073 | 1 | 2.0771 | 0.022073 | 24.6 | 47 | 0.27395 | 0.024947 |  | 500 Al |  | 0.0605 | 0.0633 | 0.181 | 0.46 | 0.004 | 1.16 | 0.56 | 0.46 | 835 | 0.5 | 504 | 0.75 | 480 | 1 | 456 | 47 | 20 | 90 | 250 | 50 | 150
3x1*630 Al + as50 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 630 | Al | 50 | flat | 1 | 2.6794 | 0.036305 | 1 | 2.6794 | 0.036305 | 27.9 | 51 | 0.29927 | 0.042871 | 186027 | 630 Al |  | 0.0469 | 0.0506 | 0.175 | 0.51 | 0.004 | 1.146 | 0.537 | 0.51 | 940 | 0.5 | 557 | 0.75 | 530 | 1 | 504 | 59.2 | 20 | 90 | 250 | 50 | 150
3x1*800 Al + as50 YMeKrvas 8,7/15 flat | YMeKrvas | 8.7 | 15 | 3x1 | 800 | Al | 50 | flat | 1 | 3.4241 | 0.05822 | 1 | 3.4241 | 0.05822 | 31.5 | 55 | 0.32802 | 0.070611 | 186028 | 800 Al |  | 0.0367 | 0.0414 | 0.17 | 0.56 | 0.004 | 1.135 | 0.513 | 0.56 | 1055 | 0.5 | 609 | 0.75 | 580 | 1 | 551 | 75.2 | 20 | 90 | 250 | 50 | 150
3x1*70 Al + as25 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 70 | Al | 25 | trefoil | 1 | 0.28367 | 0.00041895 | 1 | 0.28367 | 0.00041895 | 9.1 | 32 | 0.080869 | 0.0001487 |  | 70 Al |  | 0.443 | 0.443 | 0.146 | 0.22 | 0.004 | 2.63 | 0.43 | 0.22 | 230 | 0.5 | 189 | 0.75 | 180 | 1 | 171 | 6.6 | 20 | 90 | 250 | 50 | 150
3x1*95 Al + as25 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 95 | Al | 25 | trefoil | 1 | 0.3927 | 0.00080267 | 1 | 0.3927 | 0.00080267 | 10.8 | 34 | 0.1009 | 0.00035546 |  | 95 Al |  | 0.32 | 0.32 | 0.139 | 0.25 | 0.004 | 2.51 | 0.415 | 0.25 | 270 | 0.5 | 226 | 0.75 | 215 | 1 | 204 | 8.9 | 20 | 90 | 250 | 50 | 150
3x1*120 Al + as25 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 120 | Al | 25 | trefoil | 1 | 0.49669 | 0.0012836 | 1 | 0.49669 | 0.0012836 | 12.1 | 35 | 0.11952 | 0.00067303 | 186022 | 120 Al |  | 0.253 | 0.253 | 0.134 | 0.27 | 0.004 | 2.44 | 0.401 | 0.27 | 320 | 0.5 | 257 | 0.75 | 245 | 1 | 233 | 11.3 | 20 | 90 | 250 | 50 | 150
3x1*150 Al + as25 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 150 | Al | 25 | trefoil | 1 | 0.61002 | 0.0019351 | 1 | 0.61002 | 0.0019351 | 13.3 | 36 | 0.13649 | 0.0011574 | 186023 | 150 Al |  | 0.206 | 0.207 | 0.131 | 0.29 | 0.004 | 2.372 | 0.385 | 0.29 | 365 | 0.5 | 289 | 0.75 | 275 | 1 | 261 | 14.1 | 20 | 90 | 250 | 50 | 150
3x1*185 Al + as25 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 185 | Al | 25 | trefoil | 1 | 0.76624 | 0.0030505 | 1 | 0.76624 | 0.0030505 | 14.9 | 38 | 0.15375 | 0.0020493 |  | 185 Al |  | 0.164 | 0.165 | 0.126 | 0.31 | 0.004 | 2.31 | 0.37 | 0.31 | 420 | 0.5 | 326 | 0.75 | 310 | 1 | 295 | 17.4 | 20 | 90 | 250 | 50 | 150
3x1*240 Al + as25 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 240 | Al | 25 | trefoil | 1 | 1.0053 | 0.0052417 | 1 | 1.0053 | 0.0052417 | 17.1 | 40 | 0.18276 | 0.0041615 | 186024 | 240 Al |  | 0.125 | 0.126 | 0.121 | 0.35 | 0.004 | 2.268 | 0.35 | 0.35 | 495 | 0.5 | 373 | 0.75 | 355 | 1 | 337 | 22.6 | 20 | 90 | 250 | 50 | 150
3x1*300 Al + as35 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 300 | Al | 35 | trefoil | 1 | 1.2566 | 0.0081709 | 1 | 1.2566 | 0.0081709 | 19.1 | 42 | 0.20681 | 0.0072772 | 186025 | 300 Al |  | 0.1 | 0.102 | 0.118 | 0.38 | 0.004 | 1.665 | 0.337 | 0.38 | 565 | 0.5 | 420 | 0.75 | 400 | 1 | 380 | 28.2 | 20 | 90 | 250 | 50 | 150
3x1*400 Al + as50 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 400 | Al | 50 | trefoil | 1 | 1.6152 | 0.013442 | 1 | 1.6152 | 0.013442 | 21.7 | 45 | 0.23254 | 0.01324 | 186026 | 400 Al |  | 0.0778 | 0.0799 | 0.114 | 0.42 | 0.004 | 1.182 | 0.322 | 0.42 | 660 | 0.5 | 473 | 0.75 | 450 | 1 | 428 | 37.6 | 20 | 90 | 250 | 50 | 150
3x1*500 Al + as50 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 500 | Al | 50 | trefoil | 1 | 2.0771 | 0.022073 | 1 | 2.0771 | 0.022073 | 24.6 | 47 | 0.27395 | 0.024947 |  | 500 Al |  | 0.0605 | 0.0633 | 0.11 | 0.46 | 0.004 | 1.16 | 0.31 | 0.46 | 765 | 0.5 | 536 | 0.75 | 510 | 1 | 485 | 47 | 20 | 90 | 250 | 50 | 150
3x1*630 Al + as50 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 630 | Al | 50 | trefoil | 1 | 2.6794 | 0.036305 | 1 | 2.6794 | 0.036305 | 27.9 | 51 | 0.29927 | 0.042871 | 186027 | 630 Al |  | 0.0469 | 0.0506 | 0.107 | 0.51 | 0.004 | 1.147 | 0.294 | 0.51 | 880 | 0.5 | 604 | 0.75 | 575 | 1 | 546 | 59.2 | 20 | 90 | 250 | 50 | 150
3x1*800 Al + as50 YMeKrvas 8,7/15 trefoil | YMeKrvas | 8.7 | 15 | 3x1 | 800 | Al | 50 | trefoil | 1 | 3.4241 | 0.05822 | 1 | 3.4241 | 0.05822 | 31.5 | 55 | 0.32802 | 0.070611 | 186028 | 800 Al |  | 0.0367 | 0.0414 | 0.104 | 0.56 | 0.004 | 1.137 | 0.282 | 0.56 | 1010 | 0.5 | 672 | 0.75 | 640 | 1 | 608 | 75.2 | 20 | 90 | 250 | 50 | 150
3x1*25 Cu + as16 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 25 | Cu | 16 | flat | 1 | 0.17285 | 0.00015559 | 1 | 0.17285 | 0.00015559 | 6 | 31 | 0.037461 | 2.5527e-05 | 186153 | 25 Cu |  | 0.727 | 0.727 | 0.248 | 0.15 | 0.004 | 4.257 | 0.847 | 0.15 | 195 | 0.5 | 158 | 0.75 | 150 | 1 | 143 | 3.6 | 20 | 90 | 250 | 50 | 150
3x1*35 Cu + as25 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 35 | Cu | 25 | flat | 1 | 0.23982 | 0.00029947 | 1 | 0.23982 | 0.00029947 | 7.1 | 32 | 0.049229 | 6.4585e-05 | 186126 | 35 Cu |  | 0.524 | 0.524 | 0.234 | 0.17 | 0.004 | 2.776 | 0.815 | 0.17 | 235 | 0.5 | 184 | 0.75 | 175 | 1 | 166 | 5 | 20 | 90 | 250 | 50 | 150
3x1*50 Cu + as25 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 50 | Cu | 25 | flat | 1 | 0.32471 | 0.00054892 | 1 | 0.32471 | 0.00054892 | 8.2 | 33 | 0.061745 | 0.00014848 | 186127 | 50 Cu |  | 0.387 | 0.387 | 0.226 | 0.18 | 0.004 | 2.6 | 0.781 | 0.18 | 280 | 0.5 | 215 | 0.75 | 205 | 1 | 195 | 7.2 | 20 | 90 | 250 | 50 | 150
3x1*70 Cu + as25 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 70 | Cu | 25 | flat | 1 | 0.46889 | 0.0011441 | 1 | 0.46889 | 0.0011441 | 9.9 | 35 | 0.080008 | 0.00040064 |  | 70 Cu |  | 0.268 | 0.268 | 0.216 | 0.2 | 0.004 | 2.45 | 0.75 | 0.2 | 350 | 0.5 | 257 | 0.75 | 245 | 1 | 233 | 10 | 20 | 90 | 250 | 50 | 150
3x1*95 Cu + as25 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 95 | Cu | 25 | flat | 1 | 0.65111 | 0.0022041 | 1 | 0.65111 | 0.0022041 | 11.5 | 37 | 0.096603 | 0.00092945 | 186128 | 95 Cu |  | 0.193 | 0.194 | 0.208 | 0.22 | 0.004 | 2.354 | 0.708 | 0.22 | 425 | 0.5 | 305 | 0.75 | 290 | 1 | 276 | 13.6 | 20 | 90 | 250 | 50 | 150
3x1*120 Cu + as50 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 120 | Cu | 50 | flat | 1 | 0.82133 | 0.0035036 | 1 | 0.82133 | 0.0035036 | 13 | 38 | 0.11704 | 0.0017841 | 186129 | 120 Cu |  | 0.153 | 0.154 | 0.202 | 0.24 | 0.004 | 1.275 | 0.662 | 0.24 | 485 | 0.5 | 341 | 0.75 | 325 | 1 | 309 | 17.2 | 20 | 90 | 250 | 50 | 150
3x1*150 Cu + as25 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 150 | Cu | 25 | flat | 1 | 1.0134 | 0.0053262 | 1 | 1.0134 | 0.0053262 | 14.5 | 40 | 0.13141 | 0.0030283 | 186130 | 150 Cu |  | 0.124 | 0.125 | 0.196 | 0.26 | 0.004 | 2.266 | 0.661 | 0.26 | 550 | 0.5 | 378 | 0.75 | 360 | 1 | 342 | 21.5 | 20 | 90 | 250 | 50 | 150
3x1*185 Cu + as25 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 185 | Cu | 25 | flat | 1 | 1.268 | 0.008319 | 1 | 1.268 | 0.008319 | 16.1 | 41 | 0.1542 | 0.0055004 | 186131 | 185 Cu |  | 0.0991 | 0.1 | 0.191 | 0.28 | 0.004 | 2.234 | 0.637 | 0.28 | 625 | 0.5 | 420 | 0.75 | 400 | 1 | 380 | 26.5 | 20 | 90 | 250 | 50 | 150
3x1*240 Cu + as25 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 240 | Cu | 25 | flat | 1 | 1.6666 | 0.014301 | 1 | 1.6666 | 0.014301 | 18.6 | 44 | 0.1787 | 0.01075 | 186132 | 240 Cu |  | 0.0754 | 0.0773 | 0.184 | 0.31 | 0.004 | 2.204 | 0.607 | 0.31 | 730 | 0.5 | 478 | 0.75 | 455 | 1 | 432 | 34.3 | 20 | 90 | 250 | 50 | 150
3x1*300 Cu + as35 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 300 | Cu | 35 | flat | 1 | 2.0909 | 0.022363 | 1 | 2.0909 | 0.022363 | 20.6 | 46 | 0.20055 | 0.018382 |  | 300 Cu |  | 0.0601 | 0.0625 | 0.179 | 0.34 | 0.004 | 1.57 | 0.59 | 0.34 | 825 | 0.5 | 530 | 0.75 | 505 | 1 | 480 | 42.9 | 20 | 90 | 250 | 50 | 150
3x1*400 Cu + as50 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 400 | Cu | 50 | flat | 1 | 2.6737 | 0.036156 | 1 | 2.6737 | 0.036156 | 24 | 49 | 0.2399 | 0.03408 | 186133 | 400 Cu |  | 0.047 | 0.0503 | 0.175 | 0.38 | 0.004 | 1.144 | 0.56 | 0.38 | 880 | 0.5 | 541 | 0.75 | 515 | 1 | 489 | 57.2 | 20 | 90 | 250 | 50 | 150
3x1*500 Cu + as35 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 500 | Cu | 35 | flat | 1 | 3.4334 | 0.058524 | 1 | 3.4334 | 0.058524 | 27.2 | 53 | 0.26338 | 0.056631 | 186134 | 500 Cu |  | 0.0366 | 0.0408 | 0.169 | 0.42 | 0.004 | 1.548 | 0.536 | 0.42 | 985 | 0.5 | 588 | 0.75 | 560 | 1 | 532 | 71.5 | 20 | 90 | 250 | 50 | 150
3x1*630 Cu + as50 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 630 | Cu | 50 | flat | 1 | 4.4404 | 0.094898 | 1 | 4.4404 | 0.094898 | 31.1 | 57 | 0.29769 | 0.09398 | 186135 | 630 Cu |  | 0.0283 | 0.0336 | 0.162 | 0.47 | 0.004 | 1.127 | 0.512 | 0.47 | 1095 | 0.5 | 646 | 0.75 | 615 | 1 | 584 | 90.1 | 20 | 90 | 250 | 50 | 150
3x1*25 Cu + as16 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 25 | Cu | 16 | trefoil | 1 | 0.17285 | 0.00015559 | 1 | 0.17285 | 0.00015559 | 6 | 31 | 0.037461 | 2.5527e-05 | 186153 | 25 Cu |  | 0.727 | 0.727 | 0.163 | 0.15 | 0.004 | 4.257 | 0.509 | 0.15 | 160 | 0.5 | 142 | 0.75 | 135 | 1 | 128 | 3.6 | 20 | 90 | 250 | 50 | 150
3x1*35 Cu + as25 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 35 | Cu | 25 | trefoil | 1 | 0.23982 | 0.00029947 | 1 | 0.23982 | 0.00029947 | 7.1 | 32 | 0.049229 | 6.4585e-05 | 186126 | 35 Cu |  | 0.524 | 0.524 | 0.153 | 0.17 | 0.004 | 2.776 | 0.503 | 0.17 | 195 | 0.5 | 173 | 0.75 | 165 | 1 | 157 | 5 | 20 | 90 | 250 | 50 | 150
3x1*50 Cu + as25 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 50 | Cu | 25 | trefoil | 1 | 0.32471 | 0.00054892 | 1 | 0.32471 | 0.00054892 | 8.2 | 33 | 0.061745 | 0.00014848 | 186127 | 50 Cu |  | 0.387 | 0.387 | 0.147 | 0.18 | 0.004 | 2.6 | 0.476 | 0.18 | 235 | 0.5 | 200 | 0.75 | 190 | 1 | 181 | 7.2 | 20 | 90 | 250 | 50 | 150
3x1*70 Cu + as25 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 70 | Cu | 25 | trefoil | 1 | 0.46889 | 0.0011441 | 1 | 0.46889 | 0.0011441 | 9.9 | 35 | 0.080008 | 0.00040064 |  | 70 Cu |  | 0.268 | 0.268 | 0.138 | 0.2 | 0.004 | 2.45 | 0.45 | 0.2 | 295 | 0.5 | 247 | 0.75 | 235 | 1 | 223 | 10 | 20 | 90 | 250 | 50 | 150
3x1*95 Cu + as25 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 95 | Cu | 25 | trefoil | 1 | 0.65111 | 0.0022041 | 1 | 0.65111 | 0.0022041 | 11.5 | 37 | 0.096603 | 0.00092945 | 186128 | 95 Cu |  | 0.193 | 0.194 | 0.131 | 0.22 | 0.004 | 2.354 | 0.416 | 0.22 | 355 | 0.5 | 294 | 0.75 | 280 | 1 | 266 | 13.6 | 20 | 90 | 250 | 50 | 150
3x1*120 Cu + as50 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 120 | Cu | 50 | trefoil | 1 | 0.82133 | 0.0035036 | 1 | 0.82133 | 0.0035036 | 13 | 38 | 0.11704 | 0.0017841 | 186129 | 120 Cu |  | 0.153 | 0.154 | 0.126 | 0.24 | 0.004 | 1.276 | 0.392 | 0.24 | 410 | 0.5 | 331 | 0.75 | 315 | 1 | 299 | 17.2 | 20 | 90 | 250 | 50 | 150
3x1*150 Cu + as25 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 150 | Cu | 25 | trefoil | 1 | 1.0134 | 0.0053262 | 1 | 1.0134 | 0.0053262 | 14.5 | 40 | 0.13141 | 0.0030283 | 186130 | 150 Cu |  | 0.124 | 0.125 | 0.122 | 0.26 | 0.004 | 2.266 | 0.384 | 0.26 | 465 | 0.5 | 368 | 0.75 | 350 | 1 | 333 | 21.5 | 20 | 90 | 250 | 50 | 150
3x1*185 Cu + as25 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 185 | Cu | 25 | trefoil | 1 | 1.268 | 0.008319 | 1 | 1.268 | 0.008319 | 16.1 | 41 | 0.1542 | 0.0055004 | 186131 | 185 Cu |  | 0.0991 | 0.1 | 0.118 | 0.28 | 0.004 | 2.234 | 0.365 | 0.28 | 535 | 0.5 | 415 | 0.75 | 395 | 1 | 375 | 26.5 | 20 | 90 | 250 | 50 | 150
3x1*240 Cu + as25 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 240 | Cu | 25 | trefoil | 1 | 1.6666 | 0.014301 | 1 | 1.6666 | 0.014301 | 18.6 | 44 | 0.1787 | 0.01075 | 186132 | 240 Cu |  | 0.0754 | 0.0773 | 0.112 | 0.31 | 0.004 | 2.205 | 0.345 | 0.31 | 630 | 0.5 | 478 | 0.75 | 455 | 1 | 432 | 34.3 | 20 | 90 | 250 | 50 | 150
3x1*300 Cu + as35 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 300 | Cu | 35 | trefoil | 1 | 2.0909 | 0.022363 | 1 | 2.0909 | 0.022363 | 20.6 | 46 | 0.20055 | 0.018382 |  | 300 Cu |  | 0.0601 | 0.0625 | 0.109 | 0.34 | 0.004 | 1.57 | 0.33 | 0.34 | 720 | 0.5 | 536 | 0.75 | 510 | 1 | 485 | 42.9 | 20 | 90 | 250 | 50 | 150
3x1*400 Cu + as50 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 400 | Cu | 50 | trefoil | 1 | 2.6737 | 0.036156 | 1 | 2.6737 | 0.036156 | 24 | 49 | 0.2399 | 0.03408 | 186133 | 400 Cu |  | 0.047 | 0.0503 | 0.105 | 0.38 | 0.004 | 1.145 | 0.31 | 0.38 | 825 | 0.5 | 588 | 0.75 | 560 | 1 | 532 | 57.2 | 20 | 90 | 250 | 50 | 150
3x1*500 Cu + as35 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 500 | Cu | 35 | trefoil | 1 | 3.4334 | 0.058524 | 1 | 3.4334 | 0.058524 | 27.2 | 53 | 0.26338 | 0.056631 | 186134 | 500 Cu |  | 0.0366 | 0.0408 | 0.101 | 0.42 | 0.004 | 1.55 | 0.298 | 0.42 | 940 | 0.5 | 662 | 0.75 | 630 | 1 | 599 | 71.5 | 20 | 90 | 250 | 50 | 150
3x1*630 Cu + as50 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 630 | Cu | 50 | trefoil | 1 | 4.4404 | 0.094898 | 1 | 4.4404 | 0.094898 | 31.1 | 57 | 0.29769 | 0.09398 | 186135 | 630 Cu |  | 0.0283 | 0.0336 | 0.097 | 0.47 | 0.004 | 1.129 | 0.286 | 0.47 | 1070 | 0.5 | 735 | 0.75 | 700 | 1 | 665 | 90.1 | 20 | 90 | 250 | 50 | 150
3x1*95 Al + as25 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 95 | Al | 25 | flat | 1 | 0.3927 | 0.00080267 | 1 | 0.3927 | 0.00080267 | 10.8 | 36 | 0.09 | 0.00031681 | 186031 | 95 Al |  | 0.32 | 0.32 | 0.22 | 0.22 | 0.004 | 2.523 | 0.731 | 0.22 | 330 | 0.5 | 242 | 0.75 | 230 | 1 | 219 | 8.9 | 20 | 90 | 250 | 50 | 150
3x1*120 Al + as35 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 120 | Al | 35 | flat | 1 | 0.49669 | 0.0012836 | 1 | 0.49669 | 0.0012836 | 12.1 | 37 | 0.10695 | 0.00060169 |  | 120 Al |  | 0.253 | 0.253 | 0.214 | 0.23 | 0.004 | 1.85 | 0.71 | 0.23 | 380 | 0.5 | 273 | 0.75 | 260 | 1 | 247 | 11.3 | 20 | 90 | 250 | 50 | 150
3x1*150 Al + as35 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 150 | Al | 35 | flat | 1 | 0.61002 | 0.0019351 | 1 | 0.61002 | 0.0019351 | 13.3 | 38 | 0.1225 | 0.0010377 | 186033 | 150 Al |  | 0.206 | 0.207 | 0.21 | 0.25 | 0.004 | 1.796 | 0.679 | 0.25 | 430 | 0.5 | 299 | 0.75 | 285 | 1 | 271 | 14.1 | 20 | 90 | 250 | 50 | 150
3x1*185 Al + as35 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 185 | Al | 35 | flat | 1 | 0.76624 | 0.0030505 | 1 | 0.76624 | 0.0030505 | 14.9 | 40 | 0.13876 | 0.0018475 |  | 185 Al |  | 0.164 | 0.165 | 0.204 | 0.27 | 0.004 | 1.74 | 0.66 | 0.27 | 495 | 0.5 | 336 | 0.75 | 320 | 1 | 304 | 17.4 | 20 | 90 | 250 | 50 | 150
3x1*240 Al + as35 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 240 | Al | 35 | flat | 1 | 1.0053 | 0.0052417 | 1 | 1.0053 | 0.0052417 | 17.1 | 42 | 0.16577 | 0.00377 | 186036 | 240 Al |  | 0.125 | 0.126 | 0.197 | 0.29 | 0.004 | 1.693 | 0.629 | 0.29 | 580 | 0.5 | 383 | 0.75 | 365 | 1 | 347 | 22.6 | 20 | 90 | 250 | 50 | 150
3x1*300 Al + as25 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 300 | Al | 25 | flat | 1 | 1.2566 | 0.0081709 | 1 | 1.2566 | 0.0081709 | 19.1 | 44 | 0.18843 | 0.0066219 | 186037 | 300 Al |  | 0.1 | 0.101 | 0.192 | 0.32 | 0.004 | 2.236 | 0.611 | 0.32 | 660 | 0.5 | 431 | 0.75 | 410 | 1 | 390 | 28.2 | 20 | 90 | 250 | 50 | 150
3x1*400 Al + as50 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 400 | Al | 50 | flat | 1 | 1.6152 | 0.013442 | 1 | 1.6152 | 0.013442 | 21.7 | 47 | 0.21317 | 0.01212 | 186038 | 400 Al |  | 0.0778 | 0.0798 | 0.189 | 0.35 | 0.004 | 1.182 | 0.589 | 0.35 | 735 | 0.5 | 457 | 0.75 | 435 | 1 | 413 | 37.6 | 20 | 90 | 250 | 50 | 150
3x1*500 Al + as50 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 500 | Al | 50 | flat | 1 | 2.0771 | 0.022073 | 1 | 2.0771 | 0.022073 | 24.6 | 50 | 0.24206 | 0.02199 |  | 500 Al |  | 0.0605 | 0.0632 | 0.183 | 0.39 | 0.004 | 1.16 | 0.57 | 0.39 | 835 | 0.5 | 504 | 0.75 | 480 | 1 | 456 | 47 | 20 | 90 | 250 | 50 | 150
3x1*630 Al + as50 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 630 | Al | 50 | flat | 1 | 2.6794 | 0.036305 | 1 | 2.6794 | 0.036305 | 27.9 | 53 | 0.27711 | 0.039627 | 186041 | 630 Al |  | 0.0469 | 0.0505 | 0.177 | 0.43 | 0.004 | 1.148 | 0.541 | 0.43 | 940 | 0.5 | 557 | 0.75 | 530 | 1 | 504 | 59.2 | 20 | 90 | 250 | 50 | 150
3x1*800 Al + as50 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 800 | Al | 50 | flat | 1 | 3.4241 | 0.05822 | 1 | 3.4241 | 0.05822 | 31.5 | 57 | 0.3054 | 0.065618 | 186060 | 800 Al |  | 0.0367 | 0.0412 | 0.171 | 0.47 | 0.004 | 1.136 | 0.517 | 0.47 | 1055 | 0.5 | 609 | 0.75 | 580 | 1 | 551 | 75.2 | 20 | 90 | 250 | 50 | 150
3x1*1000 Al + as50 YMeKrvas 12/20 flat | YMeKrvas | 12 | 20 | 3x1 | 1000 | Al | 50 | flat | 1 | 4.3183 | 0.090123 | 1 | 4.3183 | 0.090123 | 35.5 | 61 | 0.33869 | 0.10324 | 186043 | 1000 Al |  | 0.0291 | 0.0347 | 0.164 | 0.53 | 0.004 | 1.128 | 0.497 | 0.53 | 1165 | 0.5 | 662 | 0.75 | 630 | 1 | 599 | 94 | 20 | 90 | 250 | 50 | 150
3x1*95 Al + as25 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 95 | Al | 25 | trefoil | 1 | 0.3927 | 0.00080267 | 1 | 0.3927 | 0.00080267 | 10.8 | 36 | 0.09 | 0.00031681 | 186031 | 95 Al |  | 0.32 | 0.32 | 0.143 | 0.22 | 0.004 | 2.523 | 0.436 | 0.22 | 270 | 0.5 | 226 | 0.75 | 215 | 1 | 204 | 8.9 | 20 | 90 | 250 | 50 | 150
3x1*120 Al + as35 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 120 | Al | 35 | trefoil | 1 | 0.49669 | 0.0012836 | 1 | 0.49669 | 0.0012836 | 12.1 | 37 | 0.10695 | 0.00060169 |  | 120 Al |  | 0.253 | 0.253 | 0.138 | 0.23 | 0.004 | 1.85 | 0.42 | 0.23 | 320 | 0.5 | 257 | 0.75 | 245 | 1 | 233 | 11.3 | 20 | 90 | 250 | 50 | 150
3x1*150 Al + as35 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 150 | Al | 35 | trefoil | 1 | 0.61002 | 0.0019351 | 1 | 0.61002 | 0.0019351 | 13.3 | 38 | 0.1225 | 0.0010377 | 186033 | 150 Al |  | 0.206 | 0.207 | 0.134 | 0.25 | 0.004 | 1.797 | 0.4 | 0.25 | 365 | 0.5 | 289 | 0.75 | 275 | 1 | 261 | 14.1 | 20 | 90 | 250 | 50 | 150
3x1*185 Al + as35 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 185 | Al | 35 | trefoil | 1 | 0.76624 | 0.0030505 | 1 | 0.76624 | 0.0030505 | 14.9 | 40 | 0.13876 | 0.0018475 |  | 185 Al |  | 0.164 | 0.165 | 0.13 | 0.27 | 0.004 | 1.74 | 0.385 | 0.27 | 420 | 0.5 | 326 | 0.75 | 310 | 1 | 295 | 17.4 | 20 | 90 | 250 | 50 | 150
3x1*240 Al + as35 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 240 | Al | 35 | trefoil | 1 | 1.0053 | 0.0052417 | 1 | 1.0053 | 0.0052417 | 17.1 | 42 | 0.16577 | 0.00377 | 186036 | 240 Al |  | 0.125 | 0.126 | 0.124 | 0.29 | 0.004 | 1.693 | 0.365 | 0.29 | 495 | 0.5 | 373 | 0.75 | 355 | 1 | 337 | 22.6 | 20 | 90 | 250 | 50 | 150
3x1*300 Al + as25 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 300 | Al | 25 | trefoil | 1 | 1.2566 | 0.0081709 | 1 | 1.2566 | 0.0081709 | 19.1 | 44 | 0.18843 | 0.0066219 | 186037 | 300 Al |  | 0.1 | 0.101 | 0.121 | 0.32 | 0.004 | 2.236 | 0.349 | 0.32 | 565 | 0.5 | 420 | 0.75 | 400 | 1 | 380 | 28.2 | 20 | 90 | 250 | 50 | 150
3x1*400 Al + as50 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 400 | Al | 50 | trefoil | 1 | 1.6152 | 0.013442 | 1 | 1.6152 | 0.013442 | 21.7 | 47 | 0.21317 | 0.01212 | 186038 | 400 Al |  | 0.0778 | 0.0798 | 0.117 | 0.35 | 0.004 | 1.183 | 0.334 | 0.35 | 660 | 0.5 | 473 | 0.75 | 450 | 1 | 428 | 37.6 | 20 | 90 | 250 | 50 | 150
3x1*500 Al + as50 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 500 | Al | 50 | trefoil | 1 | 2.0771 | 0.022073 | 1 | 2.0771 | 0.022073 | 24.6 | 50 | 0.24206 | 0.02199 |  | 500 Al |  | 0.0605 | 0.0632 | 0.113 | 0.39 | 0.004 | 1.16 | 0.32 | 0.39 | 765 | 0.5 | 536 | 0.75 | 510 | 1 | 485 | 47 | 20 | 90 | 250 | 50 | 150
3x1*630 Al + as50 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 630 | Al | 50 | trefoil | 1 | 2.6794 | 0.036305 | 1 | 2.6794 | 0.036305 | 27.9 | 53 | 0.27711 | 0.039627 | 186041 | 630 Al |  | 0.0469 | 0.0505 | 0.109 | 0.43 | 0.004 | 1.15 | 0.306 | 0.43 | 880 | 0.5 | 604 | 0.75 | 575 | 1 | 546 | 59.2 | 20 | 90 | 250 | 50 | 150
3x1*800 Al + as50 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 800 | Al | 50 | trefoil | 1 | 3.4241 | 0.05822 | 1 | 3.4241 | 0.05822 | 31.5 | 57 | 0.3054 | 0.065618 | 186060 | 800 Al |  | 0.0367 | 0.0412 | 0.106 | 0.47 | 0.004 | 1.138 | 0.294 | 0.47 | 1010 | 0.5 | 672 | 0.75 | 640 | 1 | 608 | 75.2 | 20 | 90 | 250 | 50 | 150
3x1*1000 Al + as50 YMeKrvas 12/20 trefoil | YMeKrvas | 12 | 20 | 3x1 | 1000 | Al | 50 | trefoil | 1 | 4.3183 | 0.090123 | 1 | 4.3183 | 0.090123 | 35.5 | 61 | 0.33869 | 0.10324 | 186043 | 1000 Al |  | 0.0291 | 0.0347 | 0.099 | 0.53 | 0.004 | 1.13 | 0.282 | 0.53 | 1135 | 0.5 | 740 | 0.75 | 705 | 1 | 670 | 94 | 20 | 90 | 250 | 50 | 150
3x1*35 Cu + as16 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 35 | Cu | 16 | flat | 1 | 0.23982 | 0.00029947 | 1 | 0.23982 | 0.00029947 | 7.1 | 37 | 0.036822 | 4.8266e-05 |  | 35 Cu |  | 0.524 | 0.524 | 0.236 | 0.13 | 0.004 | 3.8 | 0.85 | 0.13 | 235 | 0.5 | 184 | 0.75 | 175 | 1 | 166 | 5 | 20 | 90 | 250 | 50 | 150
3x1*50 Cu + as16 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 50 | Cu | 16 | flat | 1 | 0.32471 | 0.00054892 | 1 | 0.32471 | 0.00054892 | 8.2 | 39 | 0.044208 | 0.00010617 | 186136 | 50 Cu |  | 0.387 | 0.387 | 0.229 | 0.14 | 0.004 | 3.642 | 0.803 | 0.14 | 280 | 0.5 | 215 | 0.75 | 205 | 1 | 195 | 7.2 | 20 | 90 | 250 | 50 | 150
3x1*70 Cu + as25 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 70 | Cu | 25 | flat | 1 | 0.46889 | 0.0011441 | 1 | 0.46889 | 0.0011441 | 9.9 | 40 | 0.061256 | 0.00030633 | 186137 | 70 Cu |  | 0.268 | 0.268 | 0.219 | 0.16 | 0.004 | 2.449 | 0.753 | 0.16 | 350 | 0.5 | 257 | 0.75 | 245 | 1 | 233 | 10 | 20 | 90 | 250 | 50 | 150
3x1*95 Cu + as50 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 95 | Cu | 50 | flat | 1 | 0.65111 | 0.0022041 | 1 | 0.65111 | 0.0022041 | 11.5 | 42 | 0.074972 | 0.00072021 | 186138 | 95 Cu |  | 0.193 | 0.194 | 0.211 | 0.17 | 0.004 | 1.326 | 0.697 | 0.17 | 425 | 0.5 | 305 | 0.75 | 290 | 1 | 276 | 13.6 | 20 | 90 | 250 | 50 | 150
3x1*120 Cu + as25 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 120 | Cu | 25 | flat | 1 | 0.82133 | 0.0035036 | 1 | 0.82133 | 0.0035036 | 13 | 43 | 0.091401 | 0.0013907 | 186139 | 120 Cu |  | 0.153 | 0.154 | 0.205 | 0.18 | 0.004 | 2.303 | 0.692 | 0.18 | 485 | 0.5 | 341 | 0.75 | 325 | 1 | 309 | 17.2 | 20 | 90 | 250 | 50 | 150
3x1*150 Cu + as25 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 150 | Cu | 25 | flat | 1 | 1.0134 | 0.0053262 | 1 | 1.0134 | 0.0053262 | 14.5 | 45 | 0.10383 | 0.002388 | 186140 | 150 Cu |  | 0.124 | 0.125 | 0.199 | 0.2 | 0.004 | 2.266 | 0.672 | 0.2 | 550 | 0.5 | 378 | 0.75 | 360 | 1 | 342 | 21.5 | 20 | 90 | 250 | 50 | 150
3x1*185 Cu + as25 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 185 | Cu | 25 | flat | 1 | 1.268 | 0.008319 | 1 | 1.268 | 0.008319 | 16.1 | 46 | 0.1225 | 0.0043596 | 186141 | 185 Cu |  | 0.0991 | 0.1 | 0.194 | 0.21 | 0.004 | 2.234 | 0.649 | 0.21 | 625 | 0.5 | 420 | 0.75 | 400 | 1 | 380 | 26.5 | 20 | 90 | 250 | 50 | 150
3x1*240 Cu + as50 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 240 | Cu | 50 | flat | 1 | 1.6666 | 0.014301 | 1 | 1.6666 | 0.014301 | 18.6 | 49 | 0.14409 | 0.0086456 | 186142 | 240 Cu |  | 0.0754 | 0.0771 | 0.187 | 0.23 | 0.004 | 1.179 | 0.603 | 0.23 | 730 | 0.5 | 478 | 0.75 | 455 | 1 | 432 | 34.3 | 20 | 90 | 250 | 50 | 150
3x1*300 Cu + as50 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 300 | Cu | 50 | flat | 1 | 2.0909 | 0.022363 | 1 | 2.0909 | 0.022363 | 20.6 | 51 | 0.16315 | 0.014912 | 186143 | 300 Cu |  | 0.0601 | 0.0623 | 0.182 | 0.25 | 0.004 | 1.162 | 0.585 | 0.25 | 825 | 0.5 | 530 | 0.75 | 505 | 1 | 480 | 42.9 | 20 | 90 | 250 | 50 | 150
3x1*400 Cu + as50 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 400 | Cu | 50 | flat | 1 | 2.6737 | 0.036156 | 1 | 2.6737 | 0.036156 | 24 | 55 | 0.19041 | 0.026944 | 186144 | 400 Cu |  | 0.047 | 0.05 | 0.178 | 0.28 | 0.004 | 1.107 | 0.572 | 0.28 | 880 | 0.5 | 541 | 0.75 | 515 | 1 | 489 | 57.2 | 20 | 90 | 250 | 50 | 150
3x1*500 Cu + as50 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 500 | Cu | 50 | flat | 1 | 3.4334 | 0.058524 | 1 | 3.4334 | 0.058524 | 27.2 | 58 | 0.21993 | 0.047114 |  | 500 Cu |  | 0.0366 | 0.0405 | 0.172 | 0.3 | 0.004 | 1.09 | 0.55 | 0.3 | 985 | 0.5 | 588 | 0.75 | 560 | 1 | 532 | 71.5 | 20 | 90 | 250 | 50 | 150
3x1*630 Cu + as50 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 630 | Cu | 50 | flat | 1 | 4.4404 | 0.094898 | 1 | 4.4404 | 0.094898 | 31.1 | 62 | 0.25162 | 0.07909 | 186145 | 630 Cu |  | 0.0283 | 0.0332 | 0.165 | 0.34 | 0.004 | 1.08 | 0.52 | 0.34 | 1095 | 0.5 | 646 | 0.75 | 615 | 1 | 584 | 90.1 | 20 | 90 | 250 | 50 | 150
3x1*35 Cu + as16 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 35 | Cu | 16 | trefoil | 1 | 0.23982 | 0.00029947 | 1 | 0.23982 | 0.00029947 | 7.1 | 37 | 0.036822 | 4.8266e-05 |  | 35 Cu |  | 0.524 | 0.524 | 0.162 | 0.13 | 0.004 | 3.8 | 0.55 | 0.13 | 195 | 0.5 | 173 | 0.75 | 165 | 1 | 157 | 5 | 20 | 90 | 250 | 50 | 150
3x1*50 Cu + as16 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 50 | Cu | 16 | trefoil | 1 | 0.32471 | 0.00054892 | 1 | 0.32471 | 0.00054892 | 8.2 | 39 | 0.044208 | 0.00010617 | 186136 | 50 Cu |  | 0.387 | 0.387 | 0.156 | 0.14 | 0.004 | 3.642 | 0.517 | 0.14 | 235 | 0.5 | 200 | 0.75 | 190 | 1 | 181 | 7.2 | 20 | 90 | 250 | 50 | 150
3x1*70 Cu + as25 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 70 | Cu | 25 | trefoil | 1 | 0.46889 | 0.0011441 | 1 | 0.46889 | 0.0011441 | 9.9 | 40 | 0.061256 | 0.00030633 | 186137 | 70 Cu |  | 0.268 | 0.268 | 0.146 | 0.16 | 0.004 | 2.45 | 0.475 | 0.16 | 295 | 0.5 | 247 | 0.75 | 235 | 1 | 223 | 10 | 20 | 90 | 250 | 50 | 150
3x1*95 Cu + as50 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 95 | Cu | 50 | trefoil | 1 | 0.65111 | 0.0022041 | 1 | 0.65111 | 0.0022041 | 11.5 | 42 | 0.074972 | 0.00072021 | 186138 | 95 Cu |  | 0.193 | 0.194 | 0.14 | 0.17 | 0.004 | 1.326 | 0.445 | 0.17 | 355 | 0.5 | 294 | 0.75 | 280 | 1 | 266 | 13.6 | 20 | 90 | 250 | 50 | 150
3x1*120 Cu + as25 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 120 | Cu | 25 | trefoil | 1 | 0.82133 | 0.0035036 | 1 | 0.82133 | 0.0035036 | 13 | 43 | 0.091401 | 0.0013907 | 186139 | 120 Cu |  | 0.153 | 0.154 | 0.134 | 0.18 | 0.004 | 2.303 | 0.428 | 0.18 | 410 | 0.5 | 331 | 0.75 | 315 | 1 | 299 | 17.2 | 20 | 90 | 250 | 50 | 150
3x1*150 Cu + as25 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 150 | Cu | 25 | trefoil | 1 | 1.0134 | 0.0053262 | 1 | 1.0134 | 0.0053262 | 14.5 | 45 | 0.10383 | 0.002388 | 186140 | 150 Cu |  | 0.124 | 0.125 | 0.129 | 0.2 | 0.004 | 2.266 | 0.412 | 0.2 | 465 | 0.5 | 368 | 0.75 | 350 | 1 | 333 | 21.5 | 20 | 90 | 250 | 50 | 150
3x1*185 Cu + as25 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 185 | Cu | 25 | trefoil | 1 | 1.268 | 0.008319 | 1 | 1.268 | 0.008319 | 16.1 | 46 | 0.1225 | 0.0043596 | 186141 | 185 Cu |  | 0.0991 | 0.1 | 0.125 | 0.21 | 0.004 | 2.235 | 0.396 | 0.21 | 535 | 0.5 | 415 | 0.75 | 395 | 1 | 375 | 26.5 | 20 | 90 | 250 | 50 | 150
3x1*240 Cu + as50 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 240 | Cu | 50 | trefoil | 1 | 1.6666 | 0.014301 | 1 | 1.6666 | 0.014301 | 18.6 | 49 | 0.14409 | 0.0086456 | 186142 | 240 Cu |  | 0.0754 | 0.0771 | 0.12 | 0.23 | 0.004 | 1.179 | 0.365 | 0.23 | 630 | 0.5 | 478 | 0.75 | 455 | 1 | 432 | 34.3 | 20 | 90 | 250 | 50 | 150
3x1*300 Cu + as50 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 300 | Cu | 50 | trefoil | 1 | 2.0909 | 0.022363 | 1 | 2.0909 | 0.022363 | 20.6 | 51 | 0.16315 | 0.014912 | 186143 | 300 Cu |  | 0.0601 | 0.0623 | 0.116 | 0.25 | 0.004 | 1.162 | 0.357 | 0.25 | 720 | 0.5 | 536 | 0.75 | 510 | 1 | 485 | 42.9 | 20 | 90 | 250 | 50 | 150
3x1*400 Cu + as50 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 400 | Cu | 50 | trefoil | 1 | 2.6737 | 0.036156 | 1 | 2.6737 | 0.036156 | 24 | 55 | 0.19041 | 0.026944 | 186144 | 400 Cu |  | 0.047 | 0.05 | 0.112 | 0.28 | 0.004 | 1.108 | 0.338 | 0.28 | 825 | 0.5 | 588 | 0.75 | 560 | 1 | 532 | 57.2 | 20 | 90 | 250 | 50 | 150
3x1*500 Cu + as50 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 500 | Cu | 50 | trefoil | 1 | 3.4334 | 0.058524 | 1 | 3.4334 | 0.058524 | 27.2 | 58 | 0.21993 | 0.047114 |  | 500 Cu |  | 0.0366 | 0.0405 | 0.108 | 0.3 | 0.004 | 1.09 | 0.325 | 0.3 | 940 | 0.5 | 662 | 0.75 | 630 | 1 | 599 | 71.5 | 20 | 90 | 250 | 50 | 150
3x1*630 Cu + as50 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 630 | Cu | 50 | trefoil | 1 | 4.4404 | 0.094898 | 1 | 4.4404 | 0.094898 | 31.1 | 62 | 0.25162 | 0.07909 | 186145 | 630 Cu |  | 0.0283 | 0.0332 | 0.103 | 0.34 | 0.004 | 1.08 | 0.309 | 0.34 | 1070 | 0.5 | 735 | 0.75 | 700 | 1 | 665 | 90.1 | 20 | 90 | 250 | 50 | 150
3x1*120 Al + as25 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 120 | Al | 25 | flat | 1 | 0.49669 | 0.0012836 | 1 | 0.49669 | 0.0012836 | 12.1 | 42 | 0.082999 | 0.00046617 |  | 120 Al |  | 0.253 | 0.253 | 0.217 | 0.18 | 0.004 | 2.4 | 0.72 | 0.18 | 380 | 0.5 | 273 | 0.75 | 260 | 1 | 247 | 11.3 | 20 | 90 | 250 | 50 | 150
3x1*150 Al + as25 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 150 | Al | 25 | flat | 1 | 0.61002 | 0.0019351 | 1 | 0.61002 | 0.0019351 | 13.3 | 44 | 0.091369 | 0.00077227 | 186050 | 150 Al |  | 0.206 | 0.207 | 0.212 | 0.19 | 0.004 | 2.372 | 0.697 | 0.19 | 430 | 0.5 | 299 | 0.75 | 285 | 1 | 271 | 14.1 | 20 | 90 | 250 | 50 | 150
3x1*185 Al + as25 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 185 | Al | 25 | flat | 1 | 0.76624 | 0.0030505 | 1 | 0.76624 | 0.0030505 | 14.9 | 45 | 0.10963 | 0.0014567 |  | 185 Al |  | 0.164 | 0.165 | 0.207 | 0.2 | 0.004 | 2.3 | 0.675 | 0.2 | 495 | 0.5 | 336 | 0.75 | 320 | 1 | 304 | 17.4 | 20 | 90 | 250 | 50 | 150
3x1*240 Al + as25 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 240 | Al | 25 | flat | 1 | 1.0053 | 0.0052417 | 1 | 1.0053 | 0.0052417 | 17.1 | 47 | 0.13237 | 0.0030033 | 186051 | 240 Al |  | 0.125 | 0.126 | 0.2 | 0.22 | 0.004 | 2.268 | 0.643 | 0.22 | 580 | 0.5 | 383 | 0.75 | 365 | 1 | 347 | 22.6 | 20 | 90 | 250 | 50 | 150
3x1*300 Al + as50 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 300 | Al | 50 | flat | 1 | 1.2566 | 0.0081709 | 1 | 1.2566 | 0.0081709 | 19.1 | 49 | 0.15194 | 0.0053253 | 186052 | 300 Al |  | 0.1 | 0.101 | 0.195 | 0.24 | 0.004 | 1.186 | 0.608 | 0.24 | 660 | 0.5 | 431 | 0.75 | 410 | 1 | 390 | 28.2 | 20 | 90 | 250 | 50 | 150
3x1*400 Al + as50 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 400 | Al | 50 | flat | 1 | 1.6152 | 0.013442 | 1 | 1.6152 | 0.013442 | 21.7 | 52 | 0.17415 | 0.0098725 | 186054 | 400 Al |  | 0.0778 | 0.0796 | 0.192 | 0.26 | 0.004 | 1.185 | 0.601 | 0.26 | 735 | 0.5 | 457 | 0.75 | 435 | 1 | 413 | 37.6 | 20 | 90 | 250 | 50 | 150
3x1*500 Al + as50 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 500 | Al | 50 | flat | 1 | 2.0771 | 0.022073 | 1 | 2.0771 | 0.022073 | 24.6 | 55 | 0.20005 | 0.018116 |  | 500 Al |  | 0.0605 | 0.0629 | 0.186 | 0.28 | 0.004 | 1.17 | 0.575 | 0.28 | 835 | 0.5 | 504 | 0.75 | 480 | 1 | 456 | 47 | 20 | 90 | 250 | 50 | 150
3x1*630 Al + as50 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 630 | Al | 50 | flat | 1 | 2.6794 | 0.036305 | 1 | 2.6794 | 0.036305 | 27.9 | 59 | 0.22362 | 0.031842 | 186056 | 630 Al |  | 0.0469 | 0.0501 | 0.179 | 0.31 | 0.004 | 1.149 | 0.549 | 0.31 | 940 | 0.5 | 557 | 0.75 | 530 | 1 | 504 | 59.2 | 20 | 90 | 250 | 50 | 150
3x1*800 Al + as50 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 800 | Al | 50 | flat | 1 | 3.4241 | 0.05822 | 1 | 3.4241 | 0.05822 | 31.5 | 63 | 0.25 | 0.053463 | 186057 | 800 Al |  | 0.0367 | 0.0408 | 0.174 | 0.34 | 0.004 | 1.161 | 0.529 | 0.34 | 1055 | 0.5 | 609 | 0.75 | 580 | 1 | 551 | 75.2 | 20 | 90 | 250 | 50 | 150
3x1*1000 Al + as50 YMeKrvas 18/30 flat | YMeKrvas | 18 | 30 | 3x1 | 1000 | Al | 50 | flat | 1 | 4.3183 | 0.090123 | 1 | 4.3183 | 0.090123 | 35.5 | 67 | 0.28074 | 0.08512 | 186058 | 1000 Al |  | 0.0291 | 0.0342 | 0.166 | 0.38 | 0.004 | 1.154 | 0.505 | 0.38 | 1165 | 0.5 | 662 | 0.75 | 630 | 1 | 599 | 94 | 20 | 90 | 250 | 50 | 150
3x1*120 Al + as25 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 120 | Al | 25 | trefoil | 1 | 0.49669 | 0.0012836 | 1 | 0.49669 | 0.0012836 | 12.1 | 42 | 0.082999 | 0.00046617 |  | 120 Al |  | 0.253 | 0.253 | 0.146 | 0.18 | 0.004 | 2.4 | 0.45 | 0.18 | 320 | 0.5 | 257 | 0.75 | 245 | 1 | 233 | 11.3 | 20 | 90 | 250 | 50 | 150
3x1*150 Al + as25 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 150 | Al | 25 | trefoil | 1 | 0.61002 | 0.0019351 | 1 | 0.61002 | 0.0019351 | 13.3 | 44 | 0.091369 | 0.00077227 | 186050 | 150 Al |  | 0.206 | 0.207 | 0.142 | 0.19 | 0.004 | 2.372 | 0.433 | 0.19 | 365 | 0.5 | 289 | 0.75 | 275 | 1 | 261 | 14.1 | 20 | 90 | 250 | 50 | 150
3x1*185 Al + as25 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 185 | Al | 25 | trefoil | 1 | 0.76624 | 0.0030505 | 1 | 0.76624 | 0.0030505 | 14.9 | 45 | 0.10963 | 0.0014567 |  | 185 Al |  | 0.164 | 0.165 | 0.137 | 0.2 | 0.004 | 2.3 | 0.42 | 0.2 | 420 | 0.5 | 326 | 0.75 | 310 | 1 | 295 | 17.4 | 20 | 90 | 250 | 50 | 150
3x1*240 Al + as25 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 240 | Al | 25 | trefoil | 1 | 1.0053 | 0.0052417 | 1 | 1.0053 | 0.0052417 | 17.1 | 47 | 0.13237 | 0.0030033 | 186051 | 240 Al |  | 0.125 | 0.126 | 0.132 | 0.22 | 0.004 | 2.268 | 0.393 | 0.22 | 495 | 0.5 | 373 | 0.75 | 355 | 1 | 337 | 22.6 | 20 | 90 | 250 | 50 | 150
3x1*300 Al + as50 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 300 | Al | 50 | trefoil | 1 | 1.2566 | 0.0081709 | 1 | 1.2566 | 0.0081709 | 19.1 | 49 | 0.15194 | 0.0053253 | 186052 | 300 Al |  | 0.1 | 0.101 | 0.128 | 0.24 | 0.004 | 1.187 | 0.374 | 0.24 | 565 | 0.5 | 420 | 0.75 | 400 | 1 | 380 | 28.2 | 20 | 90 | 250 | 50 | 150
3x1*400 Al + as50 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 400 | Al | 50 | trefoil | 1 | 1.6152 | 0.013442 | 1 | 1.6152 | 0.013442 | 21.7 | 52 | 0.17415 | 0.0098725 | 186054 | 400 Al |  | 0.0778 | 0.0796 | 0.124 | 0.26 | 0.004 | 1.186 | 0.362 | 0.26 | 660 | 0.5 | 473 | 0.75 | 450 | 1 | 428 | 37.6 | 20 | 90 | 250 | 50 | 150
3x1*500 Al + as50 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 500 | Al | 50 | trefoil | 1 | 2.0771 | 0.022073 | 1 | 2.0771 | 0.022073 | 24.6 | 55 | 0.20005 | 0.018116 |  | 500 Al |  | 0.0605 | 0.0629 | 0.12 | 0.28 | 0.004 | 1.17 | 0.35 | 0.28 | 765 | 0.5 | 536 | 0.75 | 510 | 1 | 485 | 47 | 20 | 90 | 250 | 50 | 150
3x1*630 Al + as50 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 630 | Al | 50 | trefoil | 1 | 2.6794 | 0.036305 | 1 | 2.6794 | 0.036305 | 27.9 | 59 | 0.22362 | 0.031842 | 186056 | 630 Al |  | 0.0469 | 0.0501 | 0.116 | 0.31 | 0.004 | 1.15 | 0.33 | 0.31 | 880 | 0.5 | 604 | 0.75 | 575 | 1 | 546 | 59.2 | 20 | 90 | 250 | 50 | 150
3x1*800 Al + as50 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 800 | Al | 50 | trefoil | 1 | 3.4241 | 0.05822 | 1 | 3.4241 | 0.05822 | 31.5 | 63 | 0.25 | 0.053463 | 186057 | 800 Al |  | 0.0367 | 0.0408 | 0.112 | 0.34 | 0.004 | 1.163 | 0.318 | 0.34 | 1010 | 0.5 | 672 | 0.75 | 640 | 1 | 608 | 75.2 | 20 | 90 | 250 | 50 | 150
3x1*1000 Al + as50 YMeKrvas 18/30 trefoil | YMeKrvas | 18 | 30 | 3x1 | 1000 | Al | 50 | trefoil | 1 | 4.3183 | 0.090123 | 1 | 4.3183 | 0.090123 | 35.5 | 67 | 0.28074 | 0.08512 | 186058 | 1000 Al |  | 0.0291 | 0.0342 | 0.105 | 0.38 | 0.004 | 1.155 | 0.306 | 0.38 | 1135 | 0.5 | 740 | 0.75 | 705 | 1 | 670 | 94 | 20 | 90 | 250 | 50 | 150
3x1*240 Al + as50 YMeKrvas 36/50 flat | YMeKrvas | 36 | 50 | 3x1 | 240 | Al | 50 | flat | 1 | 1.0053 | 0.0052417 | 1 | 1.0053 | 0.0052417 | 17.1 | 54 | 0.10028 | 0.0022699 |  | 240 Al |  | 0.125 | 0.126 | 0.16 | 0.17 | 0.004 | 1.2 | 0.69 | 0.17 | 580 | 0.5 | 383 | 0.75 | 365 | 1 | 347 | 22.6 | 20 | 90 | 250 | 50 | 150
3x1*300 Al + as50 YMeKrvas 36/50 flat | YMeKrvas | 36 | 50 | 3x1 | 300 | Al | 50 | flat | 1 | 1.2566 | 0.0081709 | 1 | 1.2566 | 0.0081709 | 19.1 | 56 | 0.11633 | 0.0040666 |  | 300 Al |  | 0.1 | 0.101 | 0.159 | 0.19 | 0.004 | 1.19 | 0.66 | 0.19 | 660 | 0.5 | 431 | 0.75 | 410 | 1 | 390 | 28.2 | 20 | 90 | 250 | 50 | 150
3x1*400 Al + as50 YMeKrvas 36/50 flat | YMeKrvas | 36 | 50 | 3x1 | 400 | Al | 50 | flat | 1 | 1.6152 | 0.013442 | 1 | 1.6152 | 0.013442 | 21.7 | 59 | 0.13527 | 0.0076468 |  | 400 Al |  | 0.0778 | 0.0794 | 0.195 | 0.2 | 0.004 | 1.18 | 0.63 | 0.2 | 735 | 0.5 | 457 | 0.75 | 435 | 1 | 413 | 37.6 | 20 | 90 | 250 | 50 | 150
3x1*500 Al + as50 YMeKrvas 36/50 flat | YMeKrvas | 36 | 50 | 3x1 | 500 | Al | 50 | flat | 1 | 2.0771 | 0.022073 | 1 | 2.0771 | 0.022073 | 24.6 | 62 | 0.15743 | 0.01421 |  | 500 Al |  | 0.0605 | 0.0627 | 0.189 | 0.22 | 0.004 | 1.17 | 0.6 | 0.22 | 835 | 0.5 | 504 | 0.75 | 480 | 1 | 456 | 47 | 20 | 90 | 250 | 50 | 150
3x1*630 Al + as70 YMeKrvas 36/50 flat | YMeKrvas | 36 | 50 | 3x1 | 630 | Al | 70 | flat | 1 | 2.6794 | 0.036305 | 1 | 2.6794 | 0.036305 | 27.9 | 66 | 0.1787 | 0.025355 | 186379 | 630 Al |  | 0.0469 | 0.0498 | 0.183 | 0.24 | 0.004 | 1.009 | 0.559 | 0.24 | 940 | 0.5 | 557 | 0.75 | 530 | 1 | 504 | 59.2 | 20 | 90 | 250 | 50 | 150
3x1*1200 Al + as70 YMeKrvas 36/50 flat | YMeKrvas | 36 | 50 | 3x1 | 1200 | Al | 70 | flat | 1 | 5.0876 | 0.12169 | 1 | 5.0876 | 0.12169 | 39 | 78 | 0.25 | 0.094022 | 186378 | 1200 Al |  | 0.0247 | 0.03 | 0.166 | 0.36 | 0.004 | 0.982 | 0.503 | 0.36 | 1300 | 0.5 | 693 | 0.75 | 660 | 1 | 627 | 112.8 | 20 | 90 | 250 | 50 | 150
3x1*240 Al + as50 YMeKrvas 36/50 trefoil | YMeKrvas | 36 | 50 | 3x1 | 240 | Al | 50 | trefoil | 1 | 1.0053 | 0.0052417 | 1 | 1.0053 | 0.0052417 | 17.1 | 54 | 0.10028 | 0.0022699 |  | 240 Al |  | 0.125 | 0.126 | 0.124 | 0.17 | 0.004 | 1.2 | 0.43 | 0.17 | 495 | 0.5 | 373 | 0.75 | 355 | 1 | 337 | 22.6 | 20 | 90 | 250 | 50 | 150
3x1*300 Al + as50 YMeKrvas 36/50 trefoil | YMeKrvas | 36 | 50 | 3x1 | 300 | Al | 50 | trefoil | 1 | 1.2566 | 0.0081709 | 1 | 1.2566 | 0.0081709 | 19.1 | 56 | 0.11633 | 0.0040666 |  | 300 Al |  | 0.1 | 0.101 | 0.122 | 0.19 | 0.004 | 1.19 | 0.41 | 0.19 | 565 | 0.5 | 420 | 0.75 | 400 | 1 | 380 | 28.2 | 20 | 90 | 250 | 50 | 150
3x1*400 Al + as50 YMeKrvas 36/50 trefoil | YMeKrvas | 36 | 50 | 3x1 | 400 | Al | 50 | trefoil | 1 | 1.6152 | 0.013442 | 1 | 1.6152 | 0.013442 | 21.7 | 59 | 0.13527 | 0.0076468 |  | 400 Al |  | 0.0778 | 0.0794 | 0.132 | 0.2 | 0.004 | 1.18 | 0.39 | 0.2 | 660 | 0.5 | 473 | 0.75 | 450 | 1 | 428 | 37.6 | 20 | 90 | 250 | 50 | 150
3x1*500 Al + as50 YMeKrvas 36/50 trefoil | YMeKrvas | 36 | 50 | 3x1 | 500 | Al | 50 | trefoil | 1 | 2.0771 | 0.022073 | 1 | 2.0771 | 0.022073 | 24.6 | 62 | 0.15743 | 0.01421 |  | 500 Al |  | 0.0605 | 0.0627 | 0.127 | 0.22 | 0.004 | 1.17 | 0.37 | 0.22 | 765 | 0.5 | 536 | 0.75 | 510 | 1 | 485 | 47 | 20 | 90 | 250 | 50 | 150
3x1*630 Al + as70 YMeKrvas 36/50 trefoil | YMeKrvas | 36 | 50 | 3x1 | 630 | Al | 70 | trefoil | 1 | 2.6794 | 0.036305 | 1 | 2.6794 | 0.036305 | 27.9 | 66 | 0.1787 | 0.025355 | 186379 | 630 Al |  | 0.0469 | 0.0498 | 0.123 | 0.24 | 0.004 | 1.01 | 0.349 | 0.24 | 880 | 0.5 | 604 | 0.75 | 575 | 1 | 546 | 59.2 | 20 | 90 | 250 | 50 | 150
3x1*1200 Al + as70 YMeKrvas 36/50 trefoil | YMeKrvas | 36 | 50 | 3x1 | 1200 | Al | 70 | trefoil | 1 | 5.0876 | 0.12169 | 1 | 5.0876 | 0.12169 | 39 | 78 | 0.25 | 0.094022 | 186378 | 1200 Al |  | 0.0247 | 0.03 | 0.108 | 0.36 | 0.004 | 0.983 | 0.318 | 0.36 | 1265 | 0.5 | 851 | 0.75 | 810 | 1 | 770 | 112.8 | 20 | 90 | 250 | 50 | 150
3*16 Cu + as16 VG-YMvKrvas 6/10 | VG-YMvKrvas | 6 | 10 | 3 | 16 | Cu | 16 |  | 1 | 0.10927 | 6.2187e-05 | 1 | 0.10927 | 6.2187e-05 | 5 | 13.8 | 0.13127 | 3.6004e-05 |  | 16 Cu |  | 1.15 | 1.15 | 0.135 | 0.19 | 0.004 | 5.5 | 0.43 | 0.19 | 115 | 0.5 | 110 | 0.75 | 105 | 1 | 100 | 2.3 | 20 | 90 | 250 | 50 | 150
3*25 Cu + as25 VG-YMvKrvas 6/10 | VG-YMvKrvas | 6 | 10 | 3 | 25 | Cu | 25 |  | 1 | 0.17285 | 0.00015559 | 1 | 0.17285 | 0.00015559 | 6 | 14.8 | 0.16435 | 0.00011301 |  | 25 Cu |  | 0.727 | 0.727 | 0.127 | 0.21 | 0.004 | 4.5 | 0.4 | 0.21 | 145 | 0.5 | 142 | 0.75 | 135 | 1 | 128 | 3.6 | 20 | 90 | 250 | 50 | 150
3*35 Cu + as25 VG-YMvKrvas 6/10 | VG-YMvKrvas | 6 | 10 | 3 | 35 | Cu | 25 |  | 1 | 0.23982 | 0.00029947 | 1 | 0.23982 | 0.00029947 | 7.1 | 15.9 | 0.1994 | 0.0002644 |  | 35 Cu |  | 0.524 | 0.524 | 0.121 | 0.23 | 0.004 | 3.7 | 0.38 | 0.23 | 175 | 0.5 | 168 | 0.75 | 160 | 1 | 152 | 5 | 20 | 90 | 250 | 50 | 150
3*50 Cu + as25 VG-YMvKrvas 6/10 | VG-YMvKrvas | 6 | 10 | 3 | 50 | Cu | 25 |  | 1 | 0.32471 | 0.00054892 | 1 | 0.32471 | 0.00054892 | 8.2 | 17 | 0.23266 | 0.00056629 |  | 50 Cu |  | 0.387 | 0.387 | 0.115 | 0.25 | 0.004 | 3.5 | 0.36 | 0.25 | 210 | 0.5 | 194 | 0.75 | 185 | 1 | 176 | 7.2 | 20 | 90 | 250 | 50 | 150
3*70 Cu + as50 VG-YMvKrvas 6/10 | VG-YMvKrvas | 6 | 10 | 3 | 70 | Cu | 50 |  | 1 | 0.46889 | 0.0011441 | 1 | 0.46889 | 0.0011441 | 9.9 | 18.7 | 0.28028 | 0.0014235 |  | 70 Cu |  | 0.268 | 0.269 | 0.109 | 0.29 | 0.004 | 3.4 | 0.34 | 0.29 | 260 | 0.5 | 236 | 0.75 | 225 | 1 | 214 | 10 | 20 | 90 | 250 | 50 | 150
3*95 Cu + as50 VG-YMvKrvas 6/10 | VG-YMvKrvas | 6 | 10 | 3 | 95 | Cu | 50 |  | 1 | 0.65111 | 0.0022041 | 1 | 0.65111 | 0.0022041 | 11.5 | 20.3 | 0.32093 | 0.0031372 |  | 95 Cu |  | 0.193 | 0.194 | 0.104 | 0.32 | 0.004 | 3.3 | 0.33 | 0.32 | 315 | 0.5 | 284 | 0.75 | 270 | 1 | 257 | 13.6 | 20 | 90 | 250 | 50 | 150
3*120 Cu + as50 VG-YMvKrvas 6/10 | VG-YMvKrvas | 6 | 10 | 3 | 120 | Cu | 50 |  | 1 | 0.82133 | 0.0035036 | 1 | 0.82133 | 0.0035036 | 13 | 21.8 | 0.35561 | 0.0055136 |  | 120 Cu |  | 0.153 | 0.154 | 0.1 | 0.35 | 0.004 | 3.2 | 0.31 | 0.35 | 360 | 0.5 | 315 | 0.75 | 300 | 1 | 285 | 17.2 | 20 | 90 | 250 | 50 | 150
3*150 Cu + as50 VG-YMvKrvas 6/10 | VG-YMvKrvas | 6 | 10 | 3 | 150 | Cu | 50 |  | 1 | 1.0134 | 0.0053262 | 1 | 1.0134 | 0.0053262 | 14.5 | 23.3 | 0.38728 | 0.0090898 |  | 150 Cu |  | 0.124 | 0.126 | 0.097 | 0.38 | 0.004 | 3.1 | 0.295 | 0.38 | 410 | 0.5 | 352 | 0.75 | 335 | 1 | 318 | 21.5 | 20 | 90 | 250 | 50 | 150
3*185 Cu + as50 VG-YMvKrvas 6/10 | VG-YMvKrvas | 6 | 10 | 3 | 185 | Cu | 50 |  | 1 | 1.268 | 0.008319 | 1 | 1.268 | 0.008319 | 16.1 | 24.9 | 0.41807 | 0.015199 |  | 185 Cu |  | 0.0991 | 0.101 | 0.094 | 0.41 | 0.004 | 3 | 0.285 | 0.41 | 460 | 0.5 | 399 | 0.75 | 380 | 1 | 361 | 26.5 | 20 | 90 | 250 | 50 | 150
3*240 Cu + as50 VG-YMvKrvas 6/10 | VG-YMvKrvas | 6 | 10 | 3 | 240 | Cu | 50 |  | 1 | 1.6666 | 0.014301 | 1 | 1.6666 | 0.014301 | 18.6 | 27.4 | 0.46081 | 0.028301 |  | 240 Cu |  | 0.0754 | 0.0786 | 0.091 | 0.46 | 0.004 | 2.9 | 0.27 | 0.46 | 540 | 0.5 | 457 | 0.75 | 435 | 1 | 413 | 34.3 | 20 | 90 | 250 | 50 | 150
3*16 Cu + as16 VG-YMvKrvas 8,7/15 | VG-YMvKrvas | 8.7 | 15 | 3 | 16 | Cu | 16 |  | 1 | 0.10927 | 6.2187e-05 | 1 | 0.10927 | 6.2187e-05 | 5 | 16.1 | 0.096447 | 2.6387e-05 |  | 16 Cu |  | 1.15 | 1.15 | 0.143 | 0.16 | 0.004 | 6.4 | 0.45 | 0.16 | 115 | 0.5 | 110 | 0.75 | 105 | 1 | 100 | 2.3 | 20 | 90 | 250 | 50 | 150
3*25 Cu + as25 VG-YMvKrvas 8,7/15 | VG-YMvKrvas | 8.7 | 15 | 3 | 25 | Cu | 25 |  | 1 | 0.17285 | 0.00015559 | 1 | 0.17285 | 0.00015559 | 6 | 17.1 | 0.12311 | 8.4407e-05 | 172601 | 25 Cu |  | 0.727 | 0.727 | 0.135 | 0.17 | 0.004 | 5.141 | 0.426 | 0.17 | 145 | 0.5 | 142 | 0.75 | 135 | 1 | 128 | 3.6 | 20 | 90 | 250 | 50 | 150
3*35 Cu + as25 VG-YMvKrvas 8,7/15 | VG-YMvKrvas | 8.7 | 15 | 3 | 35 | Cu | 25 |  | 1 | 0.23982 | 0.00029947 | 1 | 0.23982 | 0.00029947 | 7.1 | 18.2 | 0.15219 | 0.00020112 | 172602 | 35 Cu |  | 0.524 | 0.524 | 0.128 | 0.19 | 0.004 | 4.209 | 0.402 | 0.19 | 175 | 0.5 | 168 | 0.75 | 160 | 1 | 152 | 5 | 20 | 90 | 250 | 50 | 150
3*50 Cu + as25 VG-YMvKrvas 8,7/15 | VG-YMvKrvas | 8.7 | 15 | 3 | 50 | Cu | 25 |  | 1 | 0.32471 | 0.00054892 | 1 | 0.32471 | 0.00054892 | 8.2 | 19.3 | 0.18051 | 0.00043775 |  | 50 Cu |  | 0.387 | 0.387 | 0.122 | 0.2 | 0.004 | 3.4 | 0.38 | 0.2 | 210 | 0.5 | 194 | 0.75 | 185 | 1 | 176 | 7.2 | 20 | 90 | 250 | 50 | 150
3*70 Cu + as50 VG-YMvKrvas 8,7/15 | VG-YMvKrvas | 8.7 | 15 | 3 | 70 | Cu | 50 |  | 1 | 0.46889 | 0.0011441 | 1 | 0.46889 | 0.0011441 | 9.9 | 21 | 0.22224 | 0.0011242 | 172604 | 70 Cu |  | 0.268 | 0.269 | 0.115 | 0.23 | 0.004 | 2.942 | 0.355 | 0.23 | 260 | 0.5 | 236 | 0.75 | 225 | 1 | 214 | 10 | 20 | 90 | 250 | 50 | 150
3*95 Cu + as50 VG-YMvKrvas 8,7/15 | VG-YMvKrvas | 8.7 | 15 | 3 | 95 | Cu | 50 |  | 1 | 0.65111 | 0.0022041 | 1 | 0.65111 | 0.0022041 | 11.5 | 22.6 | 0.25893 | 0.0025201 | 172605 | 95 Cu |  | 0.193 | 0.194 | 0.11 | 0.25 | 0.004 | 2.762 | 0.338 | 0.25 | 315 | 0.5 | 284 | 0.75 | 270 | 1 | 257 | 13.6 | 20 | 90 | 250 | 50 | 150
3*120 Cu + as50 VG-YMvKrvas 8,7/15 | VG-YMvKrvas | 8.7 | 15 | 3 | 120 | Cu | 50 |  | 1 | 0.82133 | 0.0035036 | 1 | 0.82133 | 0.0035036 | 13 | 24.1 | 0.29097 | 0.0044909 | 172606 | 120 Cu |  | 0.153 | 0.154 | 0.106 | 0.28 | 0.004 | 2.667 | 0.317 | 0.28 | 360 | 0.5 | 315 | 0.75 | 300 | 1 | 285 | 17.2 | 20 | 90 | 250 | 50 | 150
3*150 Cu + as50 VG-YMvKrvas 8,7/15 | VG-YMvKrvas | 8.7 | 15 | 3 | 150 | Cu | 50 |  | 1 | 1.0134 | 0.0053262 | 1 | 1.0134 | 0.0053262 | 14.5 | 25.6 | 0.32082 | 0.0074944 | 172607 | 150 Cu |  | 0.124 | 0.126 | 0.103 | 0.3 | 0.004 | 2.6 | 0.305 | 0.3 | 410 | 0.5 | 352 | 0.75 | 335 | 1 | 318 | 21.5 | 20 | 90 | 250 | 50 | 150
3*185 Cu + as50 VG-YMvKrvas 8,7/15 | VG-YMvKrvas | 8.7 | 15 | 3 | 185 | Cu | 50 |  | 1 | 1.268 | 0.008319 | 1 | 1.268 | 0.008319 | 16.1 | 27.2 | 0.35036 | 0.012676 | 172608 | 185 Cu |  | 0.0991 | 0.101 | 0.099 | 0.32 | 0.004 | 2.489 | 0.294 | 0.32 | 460 | 0.5 | 399 | 0.75 | 380 | 1 | 361 | 26.5 | 20 | 90 | 250 | 50 | 150
3*240 Cu + as50 VG-YMvKrvas 8,7/15 | VG-YMvKrvas | 8.7 | 15 | 3 | 240 | Cu | 50 |  | 1 | 1.6666 | 0.014301 | 1 | 1.6666 | 0.014301 | 18.6 | 29.6 | 0.39486 | 0.024134 | 172609 | 240 Cu |  | 0.0754 | 0.0783 | 0.095 | 0.36 | 0.004 | 2.4 | 0.28 | 0.36 | 540 | 0.5 | 457 | 0.75 | 435 | 1 | 413 | 34.3 | 20 | 90 | 250 | 50 | 150
3*25 Cu + as25 VG-YMvKrvas 12/20 | VG-YMvKrvas | 12 | 20 | 3 | 25 | Cu | 25 |  | 1 | 0.17285 | 0.00015559 | 1 | 0.17285 | 0.00015559 | 6 | 19.3 | 0.096647 | 6.6136e-05 |  | 25 Cu |  | 0.727 | 0.727 | 0.142 | 0.15 | 0.004 | 5.7 | 0.45 | 0.15 | 145 | 0.5 | 142 | 0.75 | 135 | 1 | 128 | 3.6 | 20 | 90 | 250 | 50 | 150
3*35 Cu + as25 VG-YMvKrvas 12/20 | VG-YMvKrvas | 12 | 20 | 3 | 35 | Cu | 25 |  | 1 | 0.23982 | 0.00029947 | 1 | 0.23982 | 0.00029947 | 7.1 | 20.4 | 0.12113 | 0.00015973 |  | 35 Cu |  | 0.524 | 0.524 | 0.135 | 0.16 | 0.004 | 4.7 | 0.43 | 0.16 | 175 | 0.5 | 168 | 0.75 | 160 | 1 | 152 | 5 | 20 | 90 | 250 | 50 | 150
3*50 Cu + as25 VG-YMvKrvas 12/20 | VG-YMvKrvas | 12 | 20 | 3 | 50 | Cu | 25 |  | 1 | 0.32471 | 0.00054892 | 1 | 0.32471 | 0.00054892 | 8.2 | 21.5 | 0.14546 | 0.00035188 | 172612 | 50 Cu |  | 0.387 | 0.387 | 0.128 | 0.18 | 0.004 | 3.826 | 0.401 | 0.18 | 210 | 0.5 | 194 | 0.75 | 185 | 1 | 176 | 7.2 | 20 | 90 | 250 | 50 | 150
3*70 Cu + as50 VG-YMvKrvas 12/20 | VG-YMvKrvas | 12 | 20 | 3 | 70 | Cu | 50 |  | 1 | 0.46889 | 0.0011441 | 1 | 0.46889 | 0.0011441 | 9.9 | 23.2 | 0.18209 | 0.00091846 |  | 70 Cu |  | 0.268 | 0.269 | 0.12 | 0.2 | 0.004 | 2.6 | 0.37 | 0.2 | 260 | 0.5 | 236 | 0.75 | 225 | 1 | 214 | 10 | 20 | 90 | 250 | 50 | 150
3*95 Cu + as50 VG-YMvKrvas 12/20 | VG-YMvKrvas | 12 | 20 | 3 | 95 | Cu | 50 |  | 1 | 0.65111 | 0.0022041 | 1 | 0.65111 | 0.0022041 | 11.5 | 24.8 | 0.21503 | 0.0020863 | 172614 | 95 Cu |  | 0.193 | 0.194 | 0.114 | 0.22 | 0.004 | 2.4 | 0.35 | 0.22 | 315 | 0.5 | 284 | 0.75 | 270 | 1 | 257 | 13.6 | 20 | 90 | 250 | 50 | 150
3*120 Cu + as50 VG-YMvKrvas 12/20 | VG-YMvKrvas | 12 | 20 | 3 | 120 | Cu | 50 |  | 1 | 0.82133 | 0.0035036 | 1 | 0.82133 | 0.0035036 | 13 | 26.3 | 0.24433 | 0.0037585 | 172615 | 120 Cu |  | 0.153 | 0.154 | 0.11 | 0.24 | 0.004 | 2.246 | 0.333 | 0.24 | 360 | 0.5 | 315 | 0.75 | 300 | 1 | 285 | 17.2 | 20 | 90 | 250 | 50 | 150
3*150 Cu + as50 VG-YMvKrvas 12/20 | VG-YMvKrvas | 12 | 20 | 3 | 150 | Cu | 50 |  | 1 | 1.0134 | 0.0053262 | 1 | 1.0134 | 0.0053262 | 14.5 | 27.8 | 0.27205 | 0.0063331 |  | 150 Cu |  | 0.124 | 0.125 | 0.106 | 0.25 | 0.004 | 2.1 | 0.315 | 0.25 | 410 | 0.5 | 352 | 0.75 | 335 | 1 | 318 | 21.5 | 20 | 90 | 250 | 50 | 150
3*185 Cu + as50 VG-YMvKrvas 12/20 | VG-YMvKrvas | 12 | 20 | 3 | 185 | Cu | 50 |  | 1 | 1.268 | 0.008319 | 1 | 1.268 | 0.008319 | 16.1 | 29.4 | 0.29989 | 0.010811 |  | 185 Cu |  | 0.0991 | 0.101 | 0.103 | 0.27 | 0.004 | 2 | 0.305 | 0.27 | 460 | 0.5 | 399 | 0.75 | 380 | 1 | 361 | 26.5 | 20 | 90 | 250 | 50 | 150
3*240 Cu + as50 VG-YMvKrvas 12/20 | VG-YMvKrvas | 12 | 20 | 3 | 240 | Cu | 50 |  | 1 | 1.6666 | 0.014301 | 1 | 1.6666 | 0.014301 | 18.6 | 32 | 0.33785 | 0.020564 | 172618 | 240 Cu |  | 0.0754 | 0.078 | 0.1 | 0.31 | 0.004 | 1.9 | 0.294 | 0.31 | 540 | 0.5 | 457 | 0.75 | 435 | 1 | 413 | 34.3 | 20 | 90 | 250 | 50 | 150
3*35 Cu + as25 VG-YMvKrvas 18/30 | VG-YMvKrvas | 18 | 30 | 3 | 35 | Cu | 25 |  | 1 | 0.23982 | 0.00029947 | 1 | 0.23982 | 0.00029947 | 7.1 | 25.7 | 0.076322 | 0.00010032 |  | 35 Cu |  | 0.524 | 0.524 | 0.148 | 0.13 | 0.004 | 5.7 | 0.46 | 0.13 | 175 | 0.5 | 168 | 0.75 | 160 | 1 | 152 | 5 | 20 | 90 | 250 | 50 | 150
3*50 Cu + as25 VG-YMvKrvas 18/30 | VG-YMvKrvas | 18 | 30 | 3 | 50 | Cu | 25 |  | 1 | 0.32471 | 0.00054892 | 1 | 0.32471 | 0.00054892 | 8.2 | 26.8 | 0.093618 | 0.00022563 |  | 50 Cu |  | 0.387 | 0.387 | 0.141 | 0.14 | 0.004 | 4.3 | 0.42 | 0.14 | 210 | 0.5 | 194 | 0.75 | 185 | 1 | 176 | 7.2 | 20 | 90 | 250 | 50 | 150
3*70 Cu + as50 VG-YMvKrvas 18/30 | VG-YMvKrvas | 18 | 30 | 3 | 70 | Cu | 50 |  | 1 | 0.46889 | 0.0011441 | 1 | 0.46889 | 0.0011441 | 9.9 | 28.5 | 0.12066 | 0.00060597 |  | 70 Cu |  | 0.268 | 0.268 | 0.132 | 0.15 | 0.004 | 2.3 | 0.38 | 0.15 | 260 | 0.5 | 236 | 0.75 | 225 | 1 | 214 | 10 | 20 | 90 | 250 | 50 | 150
3*95 Cu + as50 VG-YMvKrvas 18/30 | VG-YMvKrvas | 18 | 30 | 3 | 95 | Cu | 50 |  | 1 | 0.65111 | 0.0022041 | 1 | 0.65111 | 0.0022041 | 11.5 | 30.1 | 0.14597 | 0.0014094 |  | 95 Cu |  | 0.193 | 0.194 | 0.126 | 0.17 | 0.004 | 2 | 0.36 | 0.17 | 315 | 0.5 | 284 | 0.75 | 270 | 1 | 257 | 13.6 | 20 | 90 | 250 | 50 | 150
3*120 Cu + as50 VG-YMvKrvas 18/30 | VG-YMvKrvas | 18 | 30 | 3 | 120 | Cu | 50 |  | 1 | 0.82133 | 0.0035036 | 1 | 0.82133 | 0.0035036 | 13 | 31.6 | 0.16924 | 0.0025896 |  | 120 Cu |  | 0.153 | 0.154 | 0.122 | 0.18 | 0.004 | 1.8 | 0.34 | 0.18 | 360 | 0.5 | 315 | 0.75 | 300 | 1 | 285 | 17.2 | 20 | 90 | 250 | 50 | 150
3*150 Cu + as50 VG-YMvKrvas 18/30 | VG-YMvKrvas | 18 | 30 | 3 | 150 | Cu | 50 |  | 1 | 1.0134 | 0.0053262 | 1 | 1.0134 | 0.0053262 | 14.5 | 33.1 | 0.1919 | 0.0044418 |  | 150 Cu |  | 0.124 | 0.125 | 0.117 | 0.19 | 0.004 | 1.6 | 0.32 | 0.19 | 410 | 0.5 | 352 | 0.75 | 335 | 1 | 318 | 21.5 | 20 | 90 | 250 | 50 | 150
3*95 Al + as50 YMeKrvas 6/10 | YMeKrvas | 6 | 10 | 3 | 95 | Al | 50 |  | 1 | 0.3927 | 0.00080267 | 1 | 0.3927 | 0.00080267 | 10.8 | 19.2 | 0.31641 | 0.0011317 | 186012 | 95 Al |  | 0.32 | 0.321 | 0.113 | 0.304 | 0.004 | 1.737 | 0.094 | 0.304 | 250 | 0.5 | 226 | 0.75 | 215 | 1 | 204 | 8.9 | 20 | 90 | 250 | 50 | 150
3*150 Al + as50 YMeKrvas 6/10 | YMeKrvas | 6 | 10 | 3 | 150 | Al | 50 |  | 1 | 0.61002 | 0.0019351 | 1 | 0.61002 | 0.0019351 | 13.3 | 21.7 | 0.37565 | 0.0032396 | 186016 | 150 Al |  | 0.206 | 0.207 | 0.099 | 0.356 | 0.004 | 1.591 | 0.102 | 0.356 | 330 | 0.5 | 294 | 0.75 | 280 | 1 | 266 | 14.1 | 20 | 90 | 250 | 50 | 150
3*240 Al + as50 YMeKrvas 6/10 | YMeKrvas | 6 | 10 | 3 | 240 | Al | 50 |  | 1 | 1.0053 | 0.0052417 | 1 | 1.0053 | 0.0052417 | 17.1 | 25.5 | 0.44969 | 0.010436 | 186020 | 240 Al |  | 0.125 | 0.127 | 0.083 | 0.436 | 0.004 | 1.488 | 0.114 | 0.436 | 455 | 0.5 | 378 | 0.75 | 360 | 1 | 342 | 22.6 | 20 | 90 | 250 | 50 | 150
3*95 Al + as50 YMeKrvas 12/20 | YMeKrvas | 12 | 20 | 3 | 95 | Al | 50 |  | 1 | 0.3927 | 0.00080267 | 1 | 0.3927 | 0.00080267 | 10.8 | 22.7 | 0.22636 | 0.00080454 | 186068 | 95 Al |  | 0.32 | 0.321 | 0.113 | 0.21 | 0.004 | 1.736 | 0.127 | 0.21 | 250 | 0.5 | 226 | 0.75 | 215 | 1 | 204 | 8.9 | 20 | 90 | 250 | 50 | 150
3*150 Al + as70 YMeKrvas 12/20 | YMeKrvas | 12 | 20 | 3 | 150 | Al | 70 |  | 1 | 0.61002 | 0.0019351 | 1 | 0.61002 | 0.0019351 | 13.3 | 25.3 | 0.27635 | 0.0023667 | 186046 | 150 Al |  | 0.206 | 0.207 | 0.099 | 0.244 | 0.004 | 1.212 | 0.133 | 0.244 | 330 | 0.5 | 294 | 0.75 | 280 | 1 | 266 | 14.1 | 20 | 90 | 250 | 50 | 150
3*240 Al + as50 YMeKrvas 12/20 | YMeKrvas | 12 | 20 | 3 | 240 | Al | 50 |  | 1 | 1.0053 | 0.0052417 | 1 | 1.0053 | 0.0052417 | 17.1 | 29.7 | 0.3315 | 0.0076291 | 186067 | 240 Al |  | 0.125 | 0.127 | 0.083 | 0.293 | 0.004 | 1.488 | 0.14 | 0.293 | 455 | 0.5 | 378 | 0.75 | 360 | 1 | 342 | 22.6 | 20 | 90 | 250 | 50 | 150

## Cable (3)
Name | mantel | Uo | Unom | #geleiders | geleiderdoorsnede | geleidermateriaal | aardschermdoorsnede | formatie | ks | xs² | ys | kp | xp² | yp' | dc | s | (dc/s)² | yp | Info | Shortname | Price | Rdc | R | X | C | Tan_delta | R0 | X0 | C0 | Inom0 | G1 | Inom1 | G2 | Inom2 | G3 | Inom3 | Ik1s | TR | TInom | TIk1s | Frequency | VoP
|  | kV | kV |  | mm² |  | mm² | [7 empty] | mm | mm |  |  |  |  | EUR/m | Ohm/km | Ohm/km | Ohm/km | µF/km |  | Ohm/km | Ohm/km | µF/km | A | Km/W | A | Km/W | A | Km/W | A | kA | °C | °C | °C | Hz | m/µs
3x1*50 Al + as16 NA2XS(F)2Y 12/20 flat | NA2XS(F)2Y | 12 | 20 | 3x1 | 50 | Al | 16 | flat | 1 | 0.19604 | 0.00020014 | 1 | 0.19604 | 0.00020014 | 8.3 | 29 | 0.081914 | 7.2015e-05 |  | 50 Al |  | 0.641 | 0.641 | 0.23 | 0.17 | 0.004 |  |  | 0.17 | 219 | 0.5 | 215 | 0.75 | 205 | 1 | 195 | 4.7 | 20 | 90 | 250 | 50 | 150
3x1*70 Al + as16 NA2XS(F)2Y 12/20 flat | NA2XS(F)2Y | 12 | 20 | 3x1 | 70 | Al | 16 | flat | 1 | 0.28367 | 0.00041895 | 1 | 0.28367 | 0.00041895 | 9.8 | 30 | 0.10671 | 0.00019657 |  | 70 Al |  | 0.443 | 0.443 | 0.22 | 0.19 | 0.004 |  |  | 0.19 | 273 | 0.5 | 261 | 0.75 | 249 | 1 | 237 | 6.6 | 20 | 90 | 250 | 50 | 150
3x1*95 Al + as16 NA2XS(F)2Y 12/20 flat | NA2XS(F)2Y | 12 | 20 | 3x1 | 95 | Al | 16 | flat | 1 | 0.3927 | 0.00080267 | 1 | 0.3927 | 0.00080267 | 11.3 | 32 | 0.1247 | 0.00044003 |  | 95 Al |  | 0.32 | 0.32 | 0.21 | 0.21 | 0.004 |  |  | 0.21 | 332 | 0.5 | 311 | 0.75 | 296 | 1 | 282 | 9 | 20 | 90 | 250 | 50 | 150
3x1*120 Al + as16 NA2XS(F)2Y 12/20 flat | NA2XS(F)2Y | 12 | 20 | 3x1 | 120 | Al | 16 | flat | 1 | 0.49669 | 0.0012836 | 1 | 0.49669 | 0.0012836 | 12.8 | 33 | 0.15045 | 0.00084907 |  | 120 Al |  | 0.253 | 0.254 | 0.2 | 0.23 | 0.004 |  |  | 0.23 | 384 | 0.5 | 352 | 0.75 | 335 | 1 | 319 | 11.3 | 20 | 90 | 250 | 50 | 150
3x1*150 Al + as16 NA2XS(F)2Y 12/20 flat | NA2XS(F)2Y | 12 | 20 | 3x1 | 150 | Al | 16 | flat | 1 | 0.61002 | 0.0019351 | 1 | 0.61002 | 0.0019351 | 14.2 | 35 | 0.1646 | 0.0013986 |  | 150 Al |  | 0.206 | 0.207 | 0.19 | 0.25 | 0.004 |  |  | 0.25 | 432 | 0.5 | 389 | 0.75 | 370 | 1 | 352 | 14.2 | 20 | 90 | 250 | 50 | 150
3x1*150 Al + as25 NA2XS(F)2Y 12/20 flat | NA2XS(F)2Y | 12 | 20 | 3x1 | 150 | Al | 25 | flat | 1 | 0.61002 | 0.0019351 | 1 | 0.61002 | 0.0019351 | 14.2 | 35 | 0.1646 | 0.0013986 |  | 150 Al |  | 0.206 | 0.207 | 0.19 | 0.25 | 0.004 |  |  | 0.25 | 432 | 0.5 | 389 | 0.75 | 370 | 1 | 352 | 14.2 | 20 | 90 | 250 | 50 | 150
3x1*185 Al + as25 NA2XS(F)2Y 12/20 flat | NA2XS(F)2Y | 12 | 20 | 3x1 | 185 | Al | 25 | flat | 1 | 0.76624 | 0.0030505 | 1 | 0.76624 | 0.0030505 | 15.8 | 36 | 0.19262 | 0.0025746 |  | 185 Al |  | 0.164 | 0.165 | 0.19 | 0.27 | 0.004 |  |  | 0.27 | 494 | 0.5 | 437 | 0.75 | 416 | 1 | 396 | 17.5 | 20 | 90 | 250 | 50 | 150
3x1*240 Al + as25 NA2XS(F)2Y 12/20 flat | NA2XS(F)2Y | 12 | 20 | 3x1 | 240 | Al | 25 | flat | 1 | 1.0053 | 0.0052417 | 1 | 1.0053 | 0.0052417 | 18.1 | 39 | 0.21539 | 0.0049161 |  | 240 Al |  | 0.125 | 0.126 | 0.18 | 0.3 | 0.004 |  |  | 0.3 | 581 | 0.5 | 502 | 0.75 | 478 | 1 | 455 | 22.7 | 20 | 90 | 250 | 50 | 150
3x1*300 Al + as25 NA2XS(F)2Y 12/20 flat | NA2XS(F)2Y | 12 | 20 | 3x1 | 300 | Al | 25 | flat | 1 | 1.2566 | 0.0081709 | 1 | 1.2566 | 0.0081709 | 20.2 | 41 | 0.24274 | 0.0085637 |  | 300 Al |  | 0.1 | 0.102 | 0.17 | 0.32 | 0.004 |  |  | 0.32 | 663 | 0.5 | 563 | 0.75 | 536 | 1 | 510 | 28.4 | 20 | 90 | 250 | 50 | 150
3x1*400 Al + as35 NA2XS(F)2Y 12/20 flat | NA2XS(F)2Y | 12 | 20 | 3x1 | 400 | Al | 35 | flat | 1 | 1.6152 | 0.013442 | 1 | 1.6152 | 0.013442 | 23.3 | 44 | 0.28042 | 0.016022 |  | 400 Al |  | 0.0778 | 0.08 | 0.16 | 0.36 | 0.004 |  |  | 0.36 | 753 | 0.5 | 622 | 0.75 | 592 | 1 | 564 | 37.8 | 20 | 90 | 250 | 50 | 150
3x1*500 Al + as35 NA2XS(F)2Y 12/20 flat | NA2XS(F)2Y | 12 | 20 | 3x1 | 500 | Al | 35 | flat | 1 | 2.0771 | 0.022073 | 1 | 2.0771 | 0.022073 | 26.5 | 47 | 0.3179 | 0.029046 |  | 500 Al |  | 0.0605 | 0.064 | 0.15 | 0.4 | 0.004 |  |  | 0.4 | 866 | 0.5 | 699 | 0.75 | 666 | 1 | 634 | 47.3 | 20 | 90 | 250 | 50 | 150
3x1*630 Al + as35 NA2XS(F)2Y 12/20 flat | NA2XS(F)2Y | 12 | 20 | 3x1 | 630 | Al | 35 | flat | 1 | 2.6794 | 0.036305 | 1 | 2.6794 | 0.036305 | 29.9 | 51 | 0.34372 | 0.049411 |  | 630 Al |  | 0.0469 | 0.051 | 0.15 | 0.44 | 0.004 |  |  | 0.44 | 900 | 0.5 | 736 | 0.75 | 701 | 1 | 668 | 59.6 | 20 | 90 | 250 | 50 | 150
3x1*800 Al + as35 NA2XS(F)2Y 12/20 flat | NA2XS(F)2Y | 12 | 20 | 3x1 | 800 | Al | 35 | flat | 1 | 3.4241 | 0.05822 | 1 | 3.4241 | 0.05822 | 34.2 | 55 | 0.38666 | 0.083647 |  | 800 Al |  | 0.0367 | 0.042 | 0.14 | 0.49 | 0.004 |  |  | 0.49 | 1008 | 0.5 | 806 | 0.75 | 768 | 1 | 731 | 75.6 | 20 | 90 | 250 | 50 | 150
3x1*1000 Al + as35 NA2XS(F)2Y 12/20 flat | NA2XS(F)2Y | 12 | 20 | 3x1 | 1000 | Al | 35 | flat | 1 | 4.3183 | 0.090123 | 1 | 4.3183 | 0.090123 | 38.1 | 60 | 0.40323 | 0.12364 |  | 1000 Al |  | 0.0291 | 0.035 | 0.14 | 0.54 | 0.004 |  |  | 0.54 | 1107 | 0.5 | 849 | 0.75 | 809 | 1 | 770 | 94.6 | 20 | 90 | 250 | 50 | 150
3x1*50 Al + as16 NA2XS(F)2Y 12/20 trefoil | NA2XS(F)2Y | 12 | 20 | 3x1 | 50 | Al | 16 | trefoil | 1 | 0.19604 | 0.00020014 | 1 | 0.19604 | 0.00020014 | 8.3 | 29 | 0.081914 | 7.2015e-05 |  | 50 Al |  | 0.641 | 0.641 | 0.14 | 0.17 | 0.004 |  |  | 0.17 | 185 | 0.5 | 190 | 0.75 | 181 | 1 | 172 | 4.7 | 20 | 90 | 250 | 50 | 150
3x1*70 Al + as16 NA2XS(F)2Y 12/20 trefoil | NA2XS(F)2Y | 12 | 20 | 3x1 | 70 | Al | 16 | trefoil | 1 | 0.28367 | 0.00041895 | 1 | 0.28367 | 0.00041895 | 9.8 | 30 | 0.10671 | 0.00019657 |  | 70 Al |  | 0.443 | 0.443 | 0.13 | 0.19 | 0.004 |  |  | 0.19 | 231 | 0.5 | 232 | 0.75 | 221 | 1 | 210 | 6.6 | 20 | 90 | 250 | 50 | 150
3x1*95 Al + as16 NA2XS(F)2Y 12/20 trefoil | NA2XS(F)2Y | 12 | 20 | 3x1 | 95 | Al | 16 | trefoil | 1 | 0.3927 | 0.00080267 | 1 | 0.3927 | 0.00080267 | 11.3 | 32 | 0.1247 | 0.00044003 |  | 95 Al |  | 0.32 | 0.32 | 0.13 | 0.21 | 0.004 |  |  | 0.21 | 280 | 0.5 | 277 | 0.75 | 264 | 1 | 251 | 9 | 20 | 90 | 250 | 50 | 150
3x1*120 Al + as16 NA2XS(F)2Y 12/20 trefoil | NA2XS(F)2Y | 12 | 20 | 3x1 | 120 | Al | 16 | trefoil | 1 | 0.49669 | 0.0012836 | 1 | 0.49669 | 0.0012836 | 12.8 | 33 | 0.15045 | 0.00084907 |  | 120 Al |  | 0.253 | 0.254 | 0.12 | 0.23 | 0.004 |  |  | 0.23 | 323 | 0.5 | 314 | 0.75 | 299 | 1 | 285 | 11.3 | 20 | 90 | 250 | 50 | 150
3x1*150 Al + as16 NA2XS(F)2Y 12/20 trefoil | NA2XS(F)2Y | 12 | 20 | 3x1 | 150 | Al | 16 | trefoil | 1 | 0.61002 | 0.0019351 | 1 | 0.61002 | 0.0019351 | 14.2 | 35 | 0.1646 | 0.0013986 |  | 150 Al |  | 0.206 | 0.207 | 0.12 | 0.25 | 0.004 |  |  | 0.25 | 366 | 0.5 | 352 | 0.75 | 335 | 1 | 319 | 14.2 | 20 | 90 | 250 | 50 | 150
3x1*150 Al + as25 NA2XS(F)2Y 12/20 trefoil | NA2XS(F)2Y | 12 | 20 | 3x1 | 150 | Al | 25 | trefoil | 1 | 0.61002 | 0.0019351 | 1 | 0.61002 | 0.0019351 | 14.2 | 35 | 0.1646 | 0.0013986 |  | 150 Al |  | 0.206 | 0.207 | 0.12 | 0.25 | 0.004 |  |  | 0.25 | 366 | 0.5 | 352 | 0.75 | 335 | 1 | 319 | 14.2 | 20 | 90 | 250 | 50 | 150
3x1*185 Al + as25 NA2XS(F)2Y 12/20 trefoil | NA2XS(F)2Y | 12 | 20 | 3x1 | 185 | Al | 25 | trefoil | 1 | 0.76624 | 0.0030505 | 1 | 0.76624 | 0.0030505 | 15.8 | 36 | 0.19262 | 0.0025746 |  | 185 Al |  | 0.164 | 0.165 | 0.11 | 0.27 | 0.004 |  |  | 0.27 | 420 | 0.5 | 398 | 0.75 | 379 | 1 | 361 | 17.5 | 20 | 90 | 250 | 50 | 150
3x1*240 Al + as25 NA2XS(F)2Y 12/20 trefoil | NA2XS(F)2Y | 12 | 20 | 3x1 | 240 | Al | 25 | trefoil | 1 | 1.0053 | 0.0052417 | 1 | 1.0053 | 0.0052417 | 18.1 | 39 | 0.21539 | 0.0049161 |  | 240 Al |  | 0.125 | 0.126 | 0.11 | 0.3 | 0.004 |  |  | 0.3 | 496 | 0.5 | 460 | 0.75 | 438 | 1 | 417 | 22.7 | 20 | 90 | 250 | 50 | 150
3x1*300 Al + as25 NA2XS(F)2Y 12/20 trefoil | NA2XS(F)2Y | 12 | 20 | 3x1 | 300 | Al | 25 | trefoil | 1 | 1.2566 | 0.0081709 | 1 | 1.2566 | 0.0081709 | 20.2 | 41 | 0.24274 | 0.0085637 |  | 300 Al |  | 0.1 | 0.102 | 0.1 | 0.32 | 0.004 |  |  | 0.32 | 569 | 0.5 | 520 | 0.75 | 495 | 1 | 471 | 28.4 | 20 | 90 | 250 | 50 | 150
3x1*400 Al + as35 NA2XS(F)2Y 12/20 trefoil | NA2XS(F)2Y | 12 | 20 | 3x1 | 400 | Al | 35 | trefoil | 1 | 1.6152 | 0.013442 | 1 | 1.6152 | 0.013442 | 23.3 | 44 | 0.28042 | 0.016022 |  | 400 Al |  | 0.0778 | 0.08 | 0.1 | 0.36 | 0.004 |  |  | 0.36 | 660 | 0.5 | 590 | 0.75 | 562 | 1 | 535 | 37.8 | 20 | 90 | 250 | 50 | 150
3x1*500 Al + as35 NA2XS(F)2Y 12/20 trefoil | NA2XS(F)2Y | 12 | 20 | 3x1 | 500 | Al | 35 | trefoil | 1 | 2.0771 | 0.022073 | 1 | 2.0771 | 0.022073 | 26.5 | 47 | 0.3179 | 0.029046 |  | 500 Al |  | 0.0605 | 0.064 | 0.09 | 0.4 | 0.004 |  |  | 0.4 | 766 | 0.5 | 671 | 0.75 | 639 | 1 | 609 | 47.3 | 20 | 90 | 250 | 50 | 150
3x1*630 Al + as35 NA2XS(F)2Y 12/20 trefoil | NA2XS(F)2Y | 12 | 20 | 3x1 | 630 | Al | 35 | trefoil | 1 | 2.6794 | 0.036305 | 1 | 2.6794 | 0.036305 | 29.9 | 51 | 0.34372 | 0.049411 |  | 630 Al |  | 0.0469 | 0.051 | 0.09 | 0.44 | 0.004 |  |  | 0.44 | 861 | 0.5 | 761 | 0.75 | 725 | 1 | 690 | 59.6 | 20 | 90 | 250 | 50 | 150
3x1*800 Al + as35 NA2XS(F)2Y 12/20 trefoil | NA2XS(F)2Y | 12 | 20 | 3x1 | 800 | Al | 35 | trefoil | 1 | 3.4241 | 0.05822 | 1 | 3.4241 | 0.05822 | 34.2 | 55 | 0.38666 | 0.083647 |  | 800 Al |  | 0.0367 | 0.042 | 0.09 | 0.49 | 0.004 |  |  | 0.49 | 976 | 0.5 | 842 | 0.75 | 802 | 1 | 764 | 75.6 | 20 | 90 | 250 | 50 | 150
3x1*1000 Al + as35 NA2XS(F)2Y 12/20 trefoil | NA2XS(F)2Y | 12 | 20 | 3x1 | 1000 | Al | 35 | trefoil | 1 | 4.3183 | 0.090123 | 1 | 4.3183 | 0.090123 | 38.1 | 60 | 0.40323 | 0.12364 |  | 1000 Al |  | 0.0291 | 0.035 | 0.08 | 0.54 | 0.004 |  |  | 0.54 | 1095 | 0.5 | 923 | 0.75 | 879 | 1 | 837 | 94.6 | 20 | 90 | 250 | 50 | 150

## Trafo
Name | Shortname | Unom1 | Unom2 | Snom | Uk | Pk | Pnul | Inul | R0 | Z0 | Side Z0 | Ik2s | s1 | s2 | Clock | Tapside | Tapsize | Tapmin | Tapnom | Tapmax | Controllable | Ki | Tau | Preference
|  | kV | kV | MVA | % | kW | kW | A | Ohm | Ohm |  | kA |  |  |  |  | kV | [5 empty] | s
10250/400 V 50 kVA | 50 kVA | 10.25 | 0.4 | 0.05 | 4 | 0.9 | 0.12 | 0 | 0.0576 | 0.1143 | 0 | 1.8 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 15 | 0.1 | 0
10250/400 V 100 kVA | 100 kVA | 10.25 | 0.4 | 0.1 | 4 | 1.4 | 0.19 | 0 | 0.0224 | 0.06 | 0 | 3.6 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 14 | 0.15 | 0
10250/400 V 160 kVA | 160 kVA | 10.25 | 0.4 | 0.16 | 4 | 2.1 | 0.26 | 0 | 0.0131 | 0.0378 | 0 | 5.7 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 12 | 0.2 | 0
10250/400 V 200 kVA | 200 kVA | 10.25 | 0.4 | 0.2 | 4 | 2.5 | 0.31 | 0 | 0.01 | 0.0304 | 0 | 7.2 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 12 | 0.21 | 0
10250/400 V 250 kVA | 250 kVA | 10.25 | 0.4 | 0.25 | 4 | 2.8 | 0.37 | 0 | 0.0072 | 0.0246 | 0 | 9 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 12 | 0.22 | 0
10250/400 V 315 kVA | 315 kVA | 10.25 | 0.4 | 0.315 | 4 | 3.3 | 0.43 | 0 | 0.0053 | 0.0196 | 0 | 11.4 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 12 | 0.23 | 0
10250/400 V 400 kVA | 400 kVA | 10.25 | 0.4 | 0.4 | 4 | 4 | 0.52 | 0 | 0.004 | 0.0155 | 0 | 14.4 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 12 | 0.25 | 0
10250/400 V 500 kVA | 500 kVA | 10.25 | 0.4 | 0.5 | 4 | 4.6 | 0.62 | 0 | 0.003 | 0.012 | 0 | 18.5 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 12 | 0.25 | 0
10250/400 V 630 kVA | 630 kVA | 10.25 | 0.4 | 0.63 | 4 | 5.4 | 0.75 | 0 | 0.0022 | 0.0099 | 0 | 22.7 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 11 | 0.3 | 0
10250/400 V 800 kVA | 800 kVA | 10.25 | 0.4 | 0.8 | 6 | 7.6 | 0.85 | 0 | 0.0019 | 0.0118 | 0 | 19 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 10.5 | 0.33 | 0
10250/400 V 1000 kVA | 1000 kVA | 10.25 | 0.4 | 1 | 6 | 9.9 | 0.97 | 0 | 0.0016 | 0.0095 | 0 | 24.1 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 10 | 0.35 | 0
10250/400 V 1250 kVA | 1250 kVA | 10.25 | 0.4 | 1.25 | 6 | 12 | 1.15 | 0 | 0.0013 | 0.008 | 0 | 29.5 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 10 | 0.35 | 0
10250/400 V 1600 kVA | 1600 kVA | 10.25 | 0.4 | 1.6 | 6 | 14.6 | 1.4 | 0 | 0.0009 | 0.0059 | 0 | 38.5 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 10 | 0.4 | 0
10500/420 V 50 kVA | 50 kVA | 10.5 | 0.42 | 0.05 | 4 | 0.7 | 0.12 | 0 | 0.0494 | 0.1322 | 0 | 1.7 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 15 | 0.1 | 0
10500/420 V 100 kVA | 100 kVA | 10.5 | 0.42 | 0.1 | 4 | 1.1 | 0.19 | 0 | 0.0194 | 0.0678 | 0 | 3.4 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 14 | 0.15 | 0
10500/420 V 160 kVA | 160 kVA | 10.5 | 0.42 | 0.16 | 4 | 1.6 | 0.26 | 0 | 0.011 | 0.0427 | 0 | 5.5 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 12 | 0.2 | 0
10500/420 V 250 kVA | 250 kVA | 10.5 | 0.42 | 0.25 | 4 | 2.2 | 0.37 | 0 | 0.0062 | 0.0275 | 0 | 8.6 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 12 | 0.22 | 0
10500/420 V 400 kVA | 400 kVA | 10.5 | 0.42 | 0.4 | 4 | 3.1 | 0.52 | 0 | 0.0034 | 0.0173 | 0 | 13.7 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 12 | 0.25 | 0
10500/420 V 500 kVA | 500 kVA | 10.5 | 0.42 | 0.5 | 4 | 3.5 | 0.63 | 0 | 0.0025 | 0.0135 | 0 | 17.5 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 12 | 0.25 | 0
10500/420 V 630 kVA | 630 kVA | 10.5 | 0.42 | 0.63 | 4 | 4.2 | 0.75 | 0 | 0.0019 | 0.011 | 0 | 21.6 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 11 | 0.3 | 0
10500/420 V 800 kVA | 800 kVA | 10.5 | 0.42 | 0.8 | 6 | 5.8 | 0.85 | 0 | 0.0015 | 0.013 | 0 | 18 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 10.5 | 0.33 | 0
10500/420 V 1000 kVA | 1000 kVA | 10.5 | 0.42 | 1 | 6 | 7.5 | 0.97 | 0 | 0.0013 | 0.0105 | 0 | 22.9 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 10 | 0.35 | 0
10500/420 V 1250 kVA | 1250 kVA | 10.5 | 0.42 | 1.25 | 6 | 9 | 1.15 | 0 | 0.0011 | 0.009 | 0 | 28.5 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 10 | 0.35 | 0
10500/420 V 1600 kVA | 1600 kVA | 10.5 | 0.42 | 1.6 | 6 | 11 | 1.4 | 0 | 0.0008 | 0.0066 | 0 | 36.7 | D | yn | 5 | 1 | 0.25 | -2 | 0 | 2 |  | 10 | 0.4 | 0
100 kVA (N2009) | 100 kVA | 10.75 | 0.42 | 0.1 | 4 | 1.35 | 0.19 | 0 | 0.0309 | 0.0706 | 0 | 3.4 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 14 | 0.15 | 0
160 kVA (N2009) | 160 kVA | 10.75 | 0.42 | 0.16 | 4 | 1.905 | 0.26 | 0 | 0.0162 | 0.0441 | 0 | 5.5 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 12 | 0.2 | 0
250 kVA (N2009) | 250 kVA | 10.75 | 0.42 | 0.25 | 4 | 2.64 | 0.365 | 0 | 0.0069 | 0.0282 | 0 | 8.6 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 12 | 0.22 | 0
400 kVA (N2009) | 400 kVA | 10.75 | 0.42 | 0.4 | 4 | 3.75 | 0.52 | 0 | 0.0037 | 0.0176 | 0 | 13.7 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 12 | 0.25 | 0
630 kVA (N2009) | 630 kVA | 10.75 | 0.42 | 0.63 | 4 | 5.2 | 0.745 | 0 | 0.0022 | 0.0112 | 0 | 21.7 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 11 | 0.3 | 0
1000 kVA (N2009) | 1000 kVA | 10.75 | 0.42 | 1 | 6 | 8.8 | 0.97 | 0 | 0.0013 | 0.0106 | 0 | 22.9 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 10 | 0.35 | 0
1600 kVA (N2009) | 1600 kVA | 10.75 | 0.42 | 1.6 | 6 | 12.9 | 1.4 | 0 | 0.0008 | 0.0066 | 0 | 36.7 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 10 | 0.4 | 0
2000 kVA (N2009) | 2000 kVA | 10.75 | 0.42 | 2 | 6 | 16 | 1.75 | 0 | 0.0006 | 0.0053 | 0 | 45.8 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 9.5 | 0.4 | 0
2500 kVA (N2009) | 2500 kVA | 10.75 | 0.42 | 2.5 | 6 | 20 | 2.15 | 0 | 0.0005 | 0.0042 | 0 | 57.3 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 9 | 0.45 | 0
50 kVA (N2015) | 50 kVA | 10.75 | 0.42 | 0.05 | 4 | 1.1 | 0.09 | 0 | 0.0776 | 0.1411 | 0 | 1.7 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 15 | 0.1 | 0
100 kVA (N2015) | 100 kVA | 10.75 | 0.42 | 0.1 | 4 | 1.75 | 0.145 | 0 | 0.0309 | 0.0706 | 0 | 3.4 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 14 | 0.15 | 0
160 kVA (N2015) | 160 kVA | 10.75 | 0.42 | 0.16 | 4 | 2.35 | 0.21 | 0 | 0.0162 | 0.0441 | 0 | 5.5 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 12 | 0.2 | 0
250 kVA (N2015) | 250 kVA | 10.75 | 0.42 | 0.25 | 4 | 3.25 | 0.3 | 0 | 0.0092 | 0.0282 | 0 | 8.6 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 12 | 0.22 | 0
315 kVA (N2015) | 315 kVA | 10.75 | 0.42 | 0.315 | 4 | 3.9 | 0.36 | 0 | 0.0069 | 0.0224 | 0 | 10.8 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 12 | 0.23 | 0
400 kVA (N2015) | 400 kVA | 10.75 | 0.42 | 0.4 | 4 | 4.6 | 0.43 | 0 | 0.0051 | 0.0176 | 0 | 13.7 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 12 | 0.25 | 0
500 kVA (N2015) | 500 kVA | 10.75 | 0.42 | 0.5 | 4 | 5.5 | 0.51 | 0 | 0.0039 | 0.0141 | 0 | 17.2 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 12 | 0.25 | 0
630 kVA (N2015) | 630 kVA | 10.75 | 0.42 | 0.63 | 4 | 6.5 | 0.6 | 0 | 0.0029 | 0.0112 | 0 | 21.7 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 11 | 0.3 | 0
800 kVA (N2015) | 800 kVA | 10.75 | 0.42 | 0.8 | 4 | 8.4 | 0.65 | 0 | 0.0023 | 0.0088 | 0 | 27.5 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 10.5 | 0.33 | 0
1000 kVA (N2015) | 1000 kVA | 10.75 | 0.42 | 1 | 6 | 10.5 | 0.77 | 0 | 0.0019 | 0.0106 | 0 | 22.9 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 10 | 0.35 | 0
1250 kVA (N2015) | 1250 kVA | 10.75 | 0.42 | 1.25 | 6 | 11 | 0.95 | 0 | 0.0012 | 0.0085 | 0 | 28.6 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 10 | 0.35 | 0
1600 kVA (N2015) | 1600 kVA | 10.75 | 0.42 | 1.6 | 6 | 14 | 1.2 | 0 | 0.001 | 0.0066 | 0 | 36.7 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 10 | 0.4 | 0
2000 kVA (N2015) | 2000 kVA | 10.75 | 0.42 | 2 | 6 | 18 | 1.45 | 0 | 0.0008 | 0.0053 | 0 | 45.8 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 9.5 | 0.4 | 0
2500 kVA (N2015) | 2500 kVA | 10.75 | 0.42 | 2.5 | 6 | 22 | 1.75 | 0 | 0.0006 | 0.0042 | 0 | 57.3 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 9 | 0.45 | 0
3150 kVA (N2015) | 3150 kVA | 10.75 | 0.42 | 3.15 | 6 | 27.5 | 2.2 | 0 | 0.0005 | 0.0034 | 0 | 72.2 | D | yn | 5 | 1 | 0.25 | 5 | 3 | 1 |  | 8.5 | 0.5 | 0
rODB 250 kVA | 250 kVA | 10.75 | 0.42 | 0.25 | 4 | 2.64 | 0.365 | 6.873 | 0.0062 | 0.0275 | 0 | 8.6 | D | yn | 5 | 1 | 0.26875 | 9 | 5 | 1 | TRUE | 12 | 0.22 | 0
rODB 400 kVA | 400 kVA | 10.75 | 0.42 | 0.4 | 4 | 3.75 | 0.515 | 10.997 | 0.0034 | 0.0173 | 0 | 13.7 | D | yn | 5 | 1 | 0.26875 | 9 | 5 | 1 | TRUE | 12 | 0.25 | 0
rODB 630 kVA | 630 kVA | 10.75 | 0.42 | 0.63 | 4 | 5.2 | 0.745 | 17.321 | 0.0019 | 0.011 | 0 | 21.6 | D | yn | 5 | 1 | 0.26875 | 9 | 5 | 1 | TRUE | 11 | 0.3 | 0
rODB 1000 kVA | 1000 kVA | 10.75 | 0.42 | 1 | 6 | 8.8 | 0.97 | 27.493 | 0.0013 | 0.0105 | 0 | 22.9 | D | yn | 5 | 1 | 0.26875 | 9 | 5 | 1 | TRUE | 10 | 0.35 | 0
DOTULr 630 kVA | 630 kVA | 10.75 | 0.42 | 0.63 | 4 | 6 | 0.66 |  | 0.004 | 0.011 | 0 | 21.7 | D | yn | 5 | 1 | 0.161 | 9 | 5 | 1 | TRUE | 11 | 0.3 | 0
DOTULr 400 kVA | 400 kVA | 10.75 | 0.42 | 0.4 | 4 | 3.9 | 0.43 |  | 0.006 | 0.0175 | 0 | 13.7 | D | yn | 5 | 1 | 0.161 | 9 | 5 | 1 | TRUE | 12 | 0.25 | 0

## Specialtrafo
Name | Sort | New sort | Shortname | Unom1 | Unom2 | Snom | Ukmin | Uknom | Ukmax | Pkmin | Pknom | Pkmax | Pnul | Inul | R0 | Z0 | Ik2s | Tapside | Tapsize | Tapmin | Tapnom | Tapmax
| Vision 8&9, Gaia 7&8 | Vision 9, Gaia 8 |  | kV | kV | MVA | % | % | % | kW | kW | kW | kW | A | Ohm | Ohm | kA |  | kV
40/26 kV 40 MVA Yd11 | SpaarYd11 |  | 40 MVA | 26.25 | 21 | 40 | 8.6 | 8.6 | 8.6 | 86.5 | 86.5 | 86.5 | 13.6 | 0 | 0 | 0.741 | 30 | 1 | 0.25 | -5 | 0 | 5
20/10 kV 15 MVA Yn0 | SpaarY0 | SpaarYa0 | 15 MVA | 20.15 | 10.4 | 15 | 3.45 | 4.79 | 6.32 | 63.14 | 73.36 | 84.07 | 7 | 2.35 | 0 | 1.3 | 0 | 1 | 0.185 | -10 | 0 | 10
RLD 50/380 | RELO |  | RELO 33 k | 0.38 | 0.38 | 0.033 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.001 | -57 | 0 | 57
RLD 100/380 | RELO |  | RELO 66 k | 0.38 | 0.38 | 0.066 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.001 | -57 | 0 | 57
RLD 200/380 | RELO |  | RELO 132 k | 0.38 | 0.38 | 0.132 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.001 | -57 | 0 | 57
LVRSys 70 kVA 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 70 kVA | 0.4 | 0.4 | 0.07 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6 | 2 | 0.006 | -4 | 0 | 4
LVRSys 22 kVA 6% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 22 kVA 6% | 0.4 | 0.4 | 0.022 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0.006 | -4 | 0 | 4
LVRSys 22 kVA 7% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 22 kVA 7% | 0.4 | 0.4 | 0.022 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0.007 | -4 | 0 | 4
LVRSys 22 kVA 8% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 22 kVA 8% | 0.4 | 0.4 | 0.022 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0.008 | -4 | 0 | 4
LVRSys 22 kVA 10% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 22 kVA 10% | 0.4 | 0.4 | 0.022 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0.01 | -4 | 0 | 4
LVRSys 22 kVA 16% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 22 kVA 16% | 0.4 | 0.4 | 0.022 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0.016 | -4 | 0 | 4
LVRSys 22 kVA 24% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 22 kVA 24% | 0.4 | 0.4 | 0.022 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2 | 0.024 | -4 | 0 | 4
LVRSys 44 kVA 6% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 44 kVA 6% | 0.4 | 0.4 | 0.044 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 0.006 | -4 | 0 | 4
LVRSys 44 kVA 7% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 44 kVA 7% | 0.4 | 0.4 | 0.044 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 0.007 | -4 | 0 | 4
LVRSys 44 kVA 8% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 44 kVA 8% | 0.4 | 0.4 | 0.044 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 0.008 | -4 | 0 | 4
LVRSys 44 kVA 10% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 44 kVA 10% | 0.4 | 0.4 | 0.044 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 0.01 | -4 | 0 | 4
LVRSys 44 kVA 16% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 44 kVA 16% | 0.4 | 0.4 | 0.044 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 0.016 | -4 | 0 | 4
LVRSys 44 kVA 24% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 44 kVA 24% | 0.4 | 0.4 | 0.044 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 0.024 | -4 | 0 | 4
LVRSys 70 kVA 6% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 70 kVA 6% | 0.4 | 0.4 | 0.07 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6 | 2 | 0.006 | -4 | 0 | 4
LVRSys 70 kVA 7% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 70 kVA 7% | 0.4 | 0.4 | 0.07 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6 | 2 | 0.007 | -4 | 0 | 4
LVRSys 70 kVA 8% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 70 kVA 8% | 0.4 | 0.4 | 0.07 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6 | 2 | 0.008 | -4 | 0 | 4
LVRSys 70 kVA 10% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 70 kVA 10% | 0.4 | 0.4 | 0.07 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6 | 2 | 0.01 | -4 | 0 | 4
LVRSys 70 kVA 16% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 70 kVA 16% | 0.4 | 0.4 | 0.07 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6 | 2 | 0.016 | -4 | 0 | 4
LVRSys 70 kVA 24% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 70 kVA 24% | 0.4 | 0.4 | 0.07 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.6 | 2 | 0.024 | -4 | 0 | 4
LVRSys 87 kVA 6% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 87 kVA 6% | 0.4 | 0.4 | 0.087 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 2 | 0.006 | -4 | 0 | 4
LVRSys 87 kVA 7% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 87 kVA 7% | 0.4 | 0.4 | 0.087 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 2 | 0.007 | -4 | 0 | 4
LVRSys 87 kVA 8% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 87 kVA 8% | 0.4 | 0.4 | 0.087 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 2 | 0.008 | -4 | 0 | 4
LVRSys 87 kVA 10% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 87 kVA 10% | 0.4 | 0.4 | 0.087 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 2 | 0.01 | -4 | 0 | 4
LVRSys 87 kVA 16% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 87 kVA 16% | 0.4 | 0.4 | 0.087 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 2 | 0.016 | -4 | 0 | 4
LVRSys 87 kVA 24% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 87 kVA 24% | 0.4 | 0.4 | 0.087 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 2 | 0.024 | -4 | 0 | 4
LVRSys 110 kVA 6% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 110 kVA 6% | 0.4 | 0.4 | 0.11 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 2 | 0.006 | -4 | 0 | 4
LVRSys 110 kVA 7% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 110 kVA 7% | 0.4 | 0.4 | 0.11 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 2 | 0.007 | -4 | 0 | 4
LVRSys 110 kVA 8% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 110 kVA 8% | 0.4 | 0.4 | 0.11 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 2 | 0.008 | -4 | 0 | 4
LVRSys 110 kVA 10% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 110 kVA 10% | 0.4 | 0.4 | 0.11 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 2 | 0.01 | -4 | 0 | 4
LVRSys 110 kVA 16% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 110 kVA 16% | 0.4 | 0.4 | 0.11 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 2 | 0.016 | -4 | 0 | 4
LVRSys 110 kVA 24% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 110 kVA 24% | 0.4 | 0.4 | 0.11 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 2 | 0.024 | -4 | 0 | 4
LVRSys 144 kVA 6% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 144 kVA 6% | 0.4 | 0.4 | 0.144 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 2 | 0.006 | -4 | 0 | 4
LVRSys 144 kVA 7% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 144 kVA 7% | 0.4 | 0.4 | 0.144 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 2 | 0.007 | -4 | 0 | 4
LVRSys 144 kVA 8% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 144 kVA 8% | 0.4 | 0.4 | 0.144 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 2 | 0.008 | -4 | 0 | 4
LVRSys 144 kVA 10% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 144 kVA 10% | 0.4 | 0.4 | 0.144 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 2 | 0.01 | -4 | 0 | 4
LVRSys 175 kVA 6% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 175 kVA 6% | 0.4 | 0.4 | 0.175 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 0.006 | -4 | 0 | 4
LVRSys 175 kVA 7% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 175 kVA 7% | 0.4 | 0.4 | 0.175 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 0.007 | -4 | 0 | 4
LVRSys 175 kVA 8% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 175 kVA 8% | 0.4 | 0.4 | 0.175 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 0.008 | -4 | 0 | 4
LVRSys 175 kVA 10% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 175 kVA 10% | 0.4 | 0.4 | 0.175 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 2 | 0.01 | -4 | 0 | 4
LVRSys 250 kVA 6% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 250 kVA 6% | 0.4 | 0.4 | 0.25 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 2 | 0.006 | -4 | 0 | 4
LVRSys 250 kVA 7% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 250 kVA 7% | 0.4 | 0.4 | 0.25 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 2 | 0.007 | -4 | 0 | 4
LVRSys 250 kVA 8% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 250 kVA 8% | 0.4 | 0.4 | 0.25 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 2 | 0.008 | -4 | 0 | 4
LVRSys 250 kVA 10% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 250 kVA 10% | 0.4 | 0.4 | 0.25 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 2 | 0.01 | -4 | 0 | 4
LVRSys 400 kVA 6% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 400 kVA 6% | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 2 | 0.006 | -4 | 0 | 4
LVRSys 400 kVA 8% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 400 kVA 8% | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 2 | 0.008 | -4 | 0 | 4
LVRSys 400 kVA 10% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 400 kVA 10% | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 2 | 0.01 | -4 | 0 | 4
LVRSys 630 kVA 6% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 630 kVA 6% | 0.4 | 0.4 | 0.63 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 2 | 0.006 | -4 | 0 | 4
LVRSys 630 kVA 8% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 630 kVA 8% | 0.4 | 0.4 | 0.63 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 2 | 0.008 | -4 | 0 | 4
LVRSys 630 kVA 10% 400 V | SpaarYN0asym | SpaarYNa0asym | LVRSys 630 kVA 10% | 0.4 | 0.4 | 0.63 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 2 | 0.01 | -4 | 0 | 4
Name | Sort |  | Shortname | Unom1 | Unom2 | Snom | Ukmin | Uknom | Ukmax | Pkmin | Pknom | Pkmax | Pnul | Inul | R0 | Z0 | R0URomin | R0URonom | R0URomax | Z0URomin | Z0URonom | Z0URomax | R0URkmin | R0URknom | R0URkmax | Z0URkmin | Z0URknom | Z0URkmax | R0RUkmin | R0RUknom | R0RUkmax | Z0RUkmin | Z0RUknom | Z0RUkmax | Ik2s | Tapside | Tapsize | Tapmin | Tapnom | Tapmax
|  |  |  | kV | kV | MVA | % | % | % | kW | kW | kW | kW | A | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | kA |  | kV
3NR2-50-0 | AXA |  | AXA 35 kVA | 0.4 | 0.4 | 0.035 | 3.41 | 0.01 | 3.55 | 0.675 | 0.0025 | 0.325 | 0 | 0 | 0 | 0.5 | 0.497 | 0.505 | 0.502 | 0.898 | 0.912 | 0.902 | 0.353 | 0 | 0.055 | 0.627 | 0 | 0.069 | 0.194 | 0 | 0.065 | 0.2 | 0 | 0.085 | 0 | 1 | 0.002 | -42 | 0 | 20
3NR2-100-0 | AXA |  | AXA 70 kVA | 0.4 | 0.4 | 0.07 | 3.41 | 0.01 | 3.55 | 1.35 | 0.005 | 0.65 | 0 | 0 | 0 | 0.5 | 0.497 | 0.505 | 0.502 | 0.898 | 0.912 | 0.902 | 0.353 | 0 | 0.055 | 0.627 | 0 | 0.069 | 0.194 | 0 | 0.065 | 0.2 | 0 | 0.085 | 0 | 1 | 0.002 | -42 | 0 | 20

## Coil
Name | Shortname | Unom | Inom | R | X | R0 | X0 | R2 | X2 | Ik2s
|  | kV | A | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | kA
Voorbeeld 300 A | 300 A | 10 | 300 | 0 | 0.3 | 0 | 0.3 | 0 | 0.3 | 13

## 3wt
Name | Unom1 | Unom2 | Unom3 | Snom1 | Snom2 | Snom3 | Uk12 | Uk13 | Uk23 | Pk12 | Pk13 | Pk23 | Sat12 | Sat13 | Sat23 | Pnul | Inul | R012 | Z012 | R013 | Z013 | R023 | Z023 | Ik2s1 | Ik2s2 | Ik2s3 | s1 | s2 | s3 | Clock12 | Clock13 | Tapside_u | Tapsize_u | Tapmin_u | Tapnom_u | Tapmax_u | Tapside_I | Tapsize_I | Tapmin_I | Tapnom_I | Tapmax_I
| kV | kV | kV | MVA | MVA | MVA | % | % | % | kW | kW | kW | MVA | MVA | MVA | kW | A | Ohm | Ohm | Ohm | Ohm | Ohm | Ohm | kA | kA | kA | [6 empty] | kV |  |  |  |  | kV

## Rail
Name | Unom | Inom | Ik_dynamic | Ik_thermic | T_thermic
| kV | A | kA | kA | s

## Sg
Name | Unom | Snom | Cosnom | Qmin | Qmax | Rg | Xd"sat | Excitation | Rotor | IkP | Ufmax | Xdsat | Xl | Xd | Xq | X0 | Xd' | Xq' | Xd'' | Xq'' | Open circuit time constant | Td' | Tq' | Td'' | Tq'' | Inertia as J | H | J | KD | nnom | Tdc unknown | Tdc | Ikd
| kV | MVA |  | Mvar | Mvar | pu | pu |  |  | kA | pu | pu | pu | pu | pu | pu | pu | pu | pu | pu |  | s | s | s | s |  | s | kgm² | pu | revs/min |  | A | kA
1 kVA en 400 V | 0.4 | 0.001 | 0.85 | -0.0005 | 0.0006 | 0.03 | 0.2 | 0 | 0 | 0.0022 | 1.3 | 1.6
2 kVA en 400 V | 0.4 | 0.002 | 0.85 | -0.001 | 0.0011 | 0.03 | 0.2 | 0 | 0 | 0.0043 | 1.3 | 1.6
5 kVA en 400 V | 0.4 | 0.005 | 0.85 | -0.0025 | 0.0027 | 0.03 | 0.2 | 0 | 0 | 0.0108 | 1.3 | 1.6
10 kVA en 400 V | 0.4 | 0.01 | 0.8 | -0.0038 | 0.0063 | 0.03 | 0.172 | 0 | 0 | 0.0217 | 1.3 | 1.67 | 0.05 | 1.67 | 1 | 0.001 | 0.172 | 0.25 | 0.086 | 0.161 | FALSE | 0.074 | 0.008 | 0.007 | 0.07 | TRUE |  | 0.21 | 0 | 1500 | TRUE |  | 0
20 kVA en 400 V | 0.4 | 0.02 | 0.8 | -0.008 | 0.0125 | 0.03 | 0.154 | 0 | 0 | 0.0433 | 1.3 | 1.93 | 0.05 | 1.93 | 1.16 | 0.001 | 0.154 | 0.2 | 0.077 | 0.162 | FALSE | 0.074 | 0.008 | 0.007 | 0.007 | TRUE |  | 0.3 | 0 | 1500 | TRUE |  | 0
50 kVA en 400 V | 0.4 | 0.05 | 0.8 | -0.02 | 0.0313 | 0.03 | 0.07 | 0 | 0 | 0.1083 | 1.3 | 2.64 | 0.05 | 2.64 | 1.58 | 0.0084 | 0.141 | 0.2 | 0.07 | 0.101 | FALSE | 0.05 | 0.0055 | 0.005 | 0.005 | TRUE |  | 1 | 0 | 1500 | TRUE |  | 0
100 kVA en 400 V | 0.4 | 0.1 | 0.8 | -0.0384 | 0.0625 | 0.03 | 0.077 | 0 | 0 | 0.2165 | 1.3 | 2.87 | 0.05 | 2.87 | 1.72 | 0.0039 | 0.129 | 0.2 | 0.077 | 0.161 | FALSE | 0.1 | 0.015 | 0.01 | 0.01 | TRUE |  | 3 | 0 | 1500 | TRUE |  | 0
200 kVA en 400 V | 0.4 | 0.2 | 0.8 | -0.077 | 0.125 | 0.03 | 0.115 | 0 | 0 | 0.433 | 1.3 | 3.39 | 0.05 | 3.39 | 1.73 | 0.006 | 0.144 | 0.3 | 0.115 | 0.151 | FALSE | 0.1 | 0.015 | 0.01 | 0.01 | TRUE |  | 7.5 | 0 | 1500 | TRUE |  | 0
500 kVA en 400 V | 0.4 | 0.5 | 0.8 | -0.19 | 0.3125 | 0.03 | 0.147 | 0 | 0 | 1.0825 | 1.3 | 3.07 | 0.05 | 3.07 | 1.84 | 0.007 | 0.159 | 1 | 0.111 | 0.147 | FALSE | 0.1 | 0.015 | 0.01 | 0.01 | TRUE |  | 21 | 0 | 1500 | TRUE |  | 0
1500 kVA en 400 V | 0.4 | 1.5 | 0.8 | -0.58 | 0.94 | 0.01 | 0.148 | 0 | 0 | 6.5 | 1.3 | 3.78 | 0.05 | 2.1 | 2.27 | 0.0033 | 0.174 | 1 | 0.148 | 0.154 | FALSE | 0.18 | 0.02 | 0.018 | 0.018 | TRUE |  | 62 | 0 | 1500 | TRUE |  | 0
Leroy Somer 3 MVA 400 V | 0.4 | 2.964 | 0.8 | -0.96 | 2.28 | 0.00836 | 0.143 | 0 | 0 | 13 | 1.3 | 2.857 | 0.084 | 3.03 | 1.82 | 0.025 | 0.311 | 0.311 | 0.168 | 0.21 | FALSE | 0.328 | 0.03 | 0.025 | 0.023 | TRUE |  | 180 | 0 | 1500 | TRUE |  | 0
Siemens 2400 kVA 400 V | 0.4 | 2.4 | 0.8 | -0.9299 | 1.44 | 0.0087 | 0.112 | 0 | 0 | 10.39 | 1.4 | 1.547 | 0.05 | 2.294 | 1.153 | 0.04 | 0.247 | 1.095 | 0.112 | 0.116 | FALSE | 0.532 | 0.029 | 0.027 | 0.027 | TRUE |  | 166 | 0 | 1500 | TRUE |  | 0
Siemens 4400 kVA 400 V | 0.4 | 4.4 | 0.8 | -1.7048 | 2.64 | 0.00432 | 0.253 | 0 | 0 | 19.05 | 1.4 | 2.179 | 0.05 | 2.404 | 2.183 | 0.129 | 0.35 | 0.35 | 0.253 | 0.29 | FALSE | 0.359 | 0.015 | 0.013 | 0.013 | TRUE |  | 230 | 0 | 1500 | TRUE |  | 0
Siemens 6,5 MVA 6,6 kV | 6.6 | 6.5 | 0.9 | -2.2 | 5.4 | 0.00419 | 0.154 | 0 | 0 | 1.7 | 1.3 | 2 | 0.07 | 2.264 | 1.4 | 0.1 | 0.316 | 1.33 | 0.154 | 0.166 | FALSE | 0.798 | 0.025 | 0.023 | 0.023 | TRUE |  | 496 | 0 | 1200 | TRUE |  | 0
Siemens 13 MVA 6,6 kV | 6.6 | 13 | 0.9 | -4.33 | 10.8 | 0.00422 | 0.152 | 0 | 0 | 3.4 | 1.3 | 2 | 0.072 | 1.749 | 0.858 | 0.1 | 0.24 | 0.815 | 0.152 | 0.193 | FALSE | 0.8928 | 0.052 | 0.0459 | 0.05 | TRUE |  | 950 | 0 | 1500 | TRUE |  | 0
Leroy Somer 2,9 MVA 10,5 kV | 10.5 | 2.9 | 0.8 | -1.2 | 2.16 | 0.00909 | 0.112 | 0 | 0 | 0.478 | 1.3 | 2.174 | 0.066 | 2.36 | 1.42 | 0.092 | 0.244 | 0.244 | 0.132 | 0.165 | FALSE | 0.256 | 0.08 | 0.025 | 0.022 | TRUE |  | 301 | 0 | 1500 | TRUE |  | 0
Leroy Somer 3,6 MVA 10,5 kV | 10.5 | 3.6 | 0.8 | -1.368 | 2.628 | 0.00834 | 0.146 | 0 | 0 | 0.594 | 1.3 | 2.273 | 0.069 | 2.45 | 1.47 | 0.096 | 0.254 | 0.254 | 0.137 | 0.172 | FALSE | 0.272 | 0.08 | 0.028 | 0.025 | TRUE |  | 363 | 0 | 1500 | TRUE |  | 0
AvK 7 MVA 10,5 kV | 10.5 | 7.05 | 0.8 | -4 | 5.46 | 0.004 | 0.171 | 0 | 0 | 1.163 | 1.3 | 1.76 | 0.1 | 1.95 | 0.98 | 0.1 | 0.281 | 0.281 | 0.188 | 0.257 | FALSE | 0.58 | 0.7 | 0.035 | 0.07 | TRUE |  | 1458 | 0 | 1500 | TRUE |  | 0
AvK 8 MVA 10,5 kV | 10.5 | 8 | 0.8 | -4.48 | 6.16 | 0.004 | 0.141 | 0 | 0 | 2199 | 1.3 | 1.7 | 0.1 | 1.89 | 0.95 | 0.1 | 0.234 | 0.234 | 0.155 | 0.211 | FALSE | 0.54 | 0.7 | 0.035 | 0.07 | TRUE |  | 1782 | 0 | 1500 | TRUE |  | 0
Siemens 29,8 MVA 10 kV | 10 | 29.8 | 0.8 | -10.9 | 24.1 | 0.0029 | 0.258 | 0 | 0 | 5.2 | 1.3 | 2.14 | 0.19 | 2.47 | 1.2 | 0.117 | 0.321 | 0.4815 | 0.258 | 0.2 | FALSE | 1.017 | 0.3051 | 0.025 | 0.025 | TRUE |  | 2220 | 0 | 1500 | TRUE |  | 0
Siemens 47,25 MVA 10 kV | 10.5 | 47.25 | 0.8 | -19.9 | 37.6 | 0.00255 | 0.188 | 0 | 0 | 8.2 | 1.3 | 2.03 | 0.149 | 2.21 | 2.1 | 0.102 | 0.271 | 0.474 | 0.188 | 0.206 | FALSE | 0.721 | 0.2163 | 0.031 | 0.031 | TRUE |  | 2726 | 0 | 3000 | TRUE |  | 0
Siemens 62,5 MVA 11 kV | 11 | 62.5 | 0.8 | -20.8 | 52 | 0.0017 | 0.166 | 0 | 0 | 9.8 | 1.3 | 2 | 0.132 | 1.97 | 1.87 | 0.1 | 0.235 | 0.425 | 0.166 | 0.183 | FALSE | 0.878 | 0.449 | 0.031 | 0.074 | TRUE |  | 4103 | 0 | 3000 | TRUE |  | 0
1 MVA en 10 kV | 10.5 | 1 | 0.8 | -0.4 | 0.75 | 0.0085 | 0.12 | 0 | 0 | 0.165 | 1.3 | 1.6
2 MVA en 10 kV | 10.5 | 2 | 0.8 | -0.8 | 1.5 | 0.0085 | 0.13 | 0 | 0 | 0.33 | 1.3 | 1.6
3 MVA en 10 kV | 10.5 | 3 | 0.8 | -1.2 | 2.25 | 0.0085 | 0.14 | 0 | 0 | 0.495 | 1.3 | 1.6
4 MVA en 10 kV | 10.5 | 4 | 0.8 | -1.6 | 3 | 0.0085 | 0.15 | 0 | 0 | 0.66 | 1.3 | 1.6

## Sm
Name | Unom | Snom | Cosnom | Rg | Xd" | Ia/Inom | R/Xa | Rotor | IkP | Xl | Xd | Xq | X0 | Xd' | Xq' | Xq'' | Open circuit time constant | Td' | Tq' | Td'' | Tq'' | H | KD | Tdc unknown | Tdc
| kV | MVA |  | pu | pu |  |  |  | kA | pu | pu | pu | pu | pu | pu | pu |  | s | s | s | s | s | pu |  | A
1 kVA en 400 V | 0.4 | 0.001 | 0.85 | 0.03 | 0.2 | 5 | 0.42
2 kVA en 400 V | 0.4 | 0.002 | 0.85 | 0.03 | 0.2 | 5 | 0.42
5 kVA en 400 V | 0.4 | 0.005 | 0.85 | 0.03 | 0.2 | 5 | 0.42
10 kVA en 400 V | 0.4 | 0.01 | 0.85 | 0.03 | 0.2 | 5 | 0.42
20 kVA en 400 V | 0.4 | 0.02 | 0.85 | 0.03 | 0.2 | 5 | 0.42
50 kVA en 400 V | 0.4 | 0.05 | 0.85 | 0.03 | 0.2 | 5 | 0.42
100 kVA en 400 V | 0.4 | 0.1 | 0.85 | 0.03 | 0.2 | 5 | 0.42
200 kVA en 400 V | 0.4 | 0.2 | 0.85 | 0.03 | 0.2 | 5 | 0.42
500 kVA en 400 V | 0.4 | 0.5 | 0.85 | 0.03 | 0.2 | 5 | 0.42

## Asg
Name | Unom | Pnom | Ia/Inom | Poles | Revs | Kipp torque | R/X | Cosnom | P2 | Cos2 | P3 | Cos3 | P4 | Cos4 | P5 | Cos5 | Locked rotor torque | Kipp revs | Efficiency | Inertia | k2 | k1 | k0 | Double cage | Own parameters | TmechCharEnable | TelCharEnable | Rs | Xsl | Xm | Rr | Xrl | Rr2 | Xr2l
| kV | MW |  |  | /min | % |  |  | pu |  | pu |  | pu |  | pu |  | % | /min | % | kgm² | % | % | % |  |  |  |  | pu | pu | pu | pu | pu | pu | pu
1 kW en 400 V | 0.4 | 0.001 | 5 | 2 | 3165 | 250 | 0.42 | 0.85 | 1.25 | 0.86 | 0.75 | 0.81 | 0.5 | 0.72 | 0.25 | 0.5
2 kW en 400 V | 0.4 | 0.002 | 6 | 2 | 3150 | 300 | 0.42 | 0.85 | 1.25 | 0.86 | 0.75 | 0.81 | 0.5 | 0.72 | 0.25 | 0.5
5 kW en 400 V | 0.4 | 0.005 | 6 | 2 | 3110 | 300 | 0.42 | 0.85 | 1.25 | 0.86 | 0.75 | 0.81 | 0.5 | 0.72 | 0.25 | 0.5
10 kW en 400 V | 0.4 | 0.01 | 7 | 2 | 3090 | 300 | 0.42 | 0.85 | 1.25 | 0.86 | 0.75 | 0.81 | 0.5 | 0.72 | 0.25 | 0.5
20 kW en 400 V | 0.4 | 0.02 | 7 | 2 | 3070 | 300 | 0.42 | 0.85 | 1.25 | 0.86 | 0.75 | 0.81 | 0.5 | 0.72 | 0.25 | 0.5
50 kW en 400 V | 0.4 | 0.05 | 7 | 2 | 3035 | 300 | 0.42 | 0.85 | 1.25 | 0.86 | 0.75 | 0.81 | 0.5 | 0.72 | 0.25 | 0.5
100 kW en 400 V | 0.4 | 0.1 | 8 | 2 | 3020 | 300 | 0.42 | 0.85 | 1.25 | 0.86 | 0.75 | 0.81 | 0.5 | 0.72 | 0.25 | 0.5
200 kW en 400 V | 0.4 | 0.2 | 8 | 2 | 3020 | 300 | 0.42 | 0.85 | 1.25 | 0.86 | 0.75 | 0.81 | 0.5 | 0.72 | 0.25 | 0.5
500 kW en 400 V | 0.4 | 0.5 | 8 | 2 | 3020 | 300 | 0.42 | 0.85 | 1.25 | 0.86 | 0.75 | 0.81 | 0.5 | 0.72 | 0.25 | 0.5

## Asm
Name | Unom | Pnom | Ia/Inom | Poles | Revs | Kipp | R/X | Cosnom | Effnom | P2 | Cos2 | Eff2 | P3 | Cos3 | Eff3 | P4 | Cos4 | Eff4 | P5 | Cos5 | Eff5 | OnePhase | Locked rotor torque | Kipp revs | Inertia | k2 | k1 | k0 | Double cage | Own parameters | TmechCharEnable | TelCharEnable | Rs | Xsl | Xm | Rr | Xrl | Rr2 | Xr2l
| kV | MW |  |  | /min | % |  |  | % | pu |  | % | pu |  | % | pu |  | % | pu |  | % |  | % | /min | kgm² | % | % | % |  |  |  |  | pu | pu | pu | pu | pu | pu | pu
1 kW en 400 V | 0.4 | 0.001 | 5 | 2 | 2835 | 250 | 0.42 | 0.85 | 95 | 1.25 | 0.86 | 95 | 0.75 | 0.81 | 95 | 0.5 | 0.75 | 94 | 0.25 | 0.54 | 90 | FALSE
2 kW en 400 V | 0.4 | 0.002 | 6 | 2 | 2850 | 300 | 0.42 | 0.85 | 95 | 1.25 | 0.86 | 95 | 0.75 | 0.81 | 95 | 0.5 | 0.75 | 94 | 0.25 | 0.54 | 90 | FALSE
5 kW en 400 V | 0.4 | 0.005 | 6 | 2 | 2890 | 300 | 0.42 | 0.85 | 95 | 1.25 | 0.86 | 95 | 0.75 | 0.81 | 95 | 0.5 | 0.75 | 94 | 0.25 | 0.54 | 90 | FALSE
10 kW en 400 V | 0.4 | 0.01 | 7 | 2 | 2910 | 300 | 0.42 | 0.85 | 95 | 1.25 | 0.86 | 95 | 0.75 | 0.81 | 95 | 0.5 | 0.75 | 94 | 0.25 | 0.54 | 90 | FALSE
20 kW en 400 V | 0.4 | 0.02 | 7 | 2 | 2930 | 300 | 0.42 | 0.85 | 95 | 1.25 | 0.86 | 95 | 0.75 | 0.81 | 95 | 0.5 | 0.75 | 94 | 0.25 | 0.54 | 90 | FALSE
50 kW en 400 V | 0.4 | 0.05 | 7 | 2 | 2965 | 300 | 0.42 | 0.85 | 95 | 1.25 | 0.86 | 95 | 0.75 | 0.81 | 95 | 0.5 | 0.75 | 94 | 0.25 | 0.54 | 90 | FALSE
100 kW en 400 V | 0.4 | 0.1 | 8 | 2 | 2980 | 300 | 0.42 | 0.85 | 95 | 1.25 | 0.86 | 95 | 0.75 | 0.81 | 95 | 0.5 | 0.75 | 94 | 0.25 | 0.54 | 90 | FALSE
200 kW en 400 V | 0.4 | 0.2 | 8 | 2 | 2980 | 300 | 0.42 | 0.85 | 95 | 1.25 | 0.86 | 95 | 0.75 | 0.81 | 95 | 0.5 | 0.75 | 94 | 0.25 | 0.54 | 90 | FALSE
500 kW en 400 V | 0.4 | 0.5 | 8 | 2 | 2980 | 300 | 0.42 | 0.85 | 95 | 1.25 | 0.86 | 95 | 0.75 | 0.81 | 95 | 0.5 | 0.75 | 94 | 0.25 | 0.54 | 90 | FALSE
1 kW en 230 V | 0.23 | 0.001 | 5 | 2 | 2835 | 250 | 0.42 | 0.85 | 95 | 1.25 | 0.86 | 95 | 0.75 | 0.81 | 95 | 0.5 | 0.75 | 94 | 0.25 | 0.54 | 90 | TRUE
2 kW en 230 V | 0.23 | 0.002 | 6 | 2 | 2850 | 300 | 0.42 | 0.85 | 95 | 1.25 | 0.86 | 95 | 0.75 | 0.81 | 95 | 0.5 | 0.75 | 94 | 0.25 | 0.54 | 90 | TRUE
5 kW en 230 V | 0.23 | 0.005 | 6 | 2 | 2890 | 300 | 0.42 | 0.85 | 95 | 1.25 | 0.86 | 95 | 0.75 | 0.81 | 95 | 0.5 | 0.75 | 94 | 0.25 | 0.54 | 90 | TRUE
10 kW en 230 V | 0.23 | 0.01 | 7 | 2 | 2910 | 300 | 0.42 | 0.85 | 95 | 1.25 | 0.86 | 95 | 0.75 | 0.81 | 95 | 0.5 | 0.75 | 94 | 0.25 | 0.54 | 90 | TRUE
WEG 75 kW 400V 2p | 0.4 | 0.075 | 7 | 2 | 2975 | 280 | 0.60711 | 0.88 | 94.3 | 0.75 | 0.86 | 94.3 | 0.5 | 0.79 | 93.4 | 0.25 | 0.57 | 90 | 0.1 | 0.33 | 79 | FALSE | 200 | 2850 | 3.4 | 0.0111 | -0.1 | 5 | TRUE | TRUE | FALSE | FALSE | 0.04019 | 0.087219 | 3.6641 | 0.00919 | 0.085 | 0.095 | 0.009
WEG 200 kW 400 V 2p | 0.4 | 0.2 | 6.5 | 2 | 2965 | 240 | 0.388 | 0.92 | 94.5 | 0.75 | 0.92 | 94.7 | 0.5 | 0.9 | 94.2 | 0.25 | 0.76 | 92 | 0.1 | 0.51 | 84 | FALSE | 90 | 2850 | 6.4 | 0.0111 | -0.46 | 8.255 | TRUE | TRUE | FALSE | FALSE | 0.040337 | 0.12656 | 1 | 0.006 | 0.04625 | 0.060375 | 0.0125
WEG 200 kW 400 V 4p | 0.4 | 0.2 | 6 | 4 | 1483 | 250 | 0.437 | 0.87 | 95 | 0.75 | 0.84 | 95 | 0.5 | 0.77 | 94.4 | 0.25 | 0.55 | 92 | 0.1 | 0.3 | 85 | FALSE | 140 | 1425 | 13.1 | 0.0111 | -0.46 | 8.255 | TRUE | TRUE | FALSE | FALSE | 0.03403 | 0.12656 | 4.2519 | 0.01 | 0.0875 | 0.11 | 0.003
WEG 200 kW 400 V 8p | 0.4 | 0.2 | 5.3 | 8 | 741 | 210 | 0.383 | 0.83 | 94.2 | 0.75 | 0.77 | 94.4 | 0.5 | 0.66 | 94.3 | 0.25 | 0.42 | 92 | 0.1 | 0.2 | 85.5 | FALSE | 110 | 712.5 | 35.96 | 0.0111 | -0.46 | 8.255 | TRUE | TRUE | FALSE | FALSE | 0.03864 | 0.15156 | 1.0059 | 0.00788 | 0.0835 | 0.09038 | 0.01
WEG 400 kW 400 V 2p | 0.4 | 0.4 | 6 | 2 | 2971 | 240 | 0.388 | 0.92 | 95.4 | 0.75 | 0.91 | 95.6 | 0.5 | 0.89 | 95.4 | 0.25 | 0.74 | 93 | 0.1 | 0.48 | 88 | FALSE | 90 | 2850 | 12.4 | 0.0111 | -0.46 | 8.255 | TRUE | TRUE | FALSE | FALSE | 0.03375 | 0.1375 | 1.6269 | 0.00569 | 0.05225 | 0.07038 | 0.003
WEG 400 kW 400 V 4p | 0.4 | 0.4 | 5.5 | 4 | 1484 | 250 | 0.437 | 0.89 | 95.4 | 0.75 | 0.87 | 95.6 | 0.5 | 0.82 | 95.1 | 0.25 | 0.59 | 93.2 | 0.1 | 0.32 | 86.8 | FALSE | 120 | 1425 | 23.9 | 0.0111 | -0.46 | 8.255 | TRUE | TRUE | FALSE | FALSE | 0.03179 | 0.14219 | 3.1641 | 0.011 | 0.071688 | 0.08038 | 0.003
WEG 400 kW 400 V 8p | 0.4 | 0.4 | 5.5 | 8 | 742 | 220 | 0.383 | 0.82 | 95 | 0.75 | 0.77 | 95.2 | 0.5 | 0.68 | 95.1 | 0.25 | 0.44 | 93.1 | 0.1 | 0.21 | 86.5 | FALSE | 80 | 712.5 | 110 | 0.0111 | -0.46 | 8.255 | TRUE | TRUE | FALSE | FALSE | 0.0326 | 0.15938 | 1 | 0.009756 | 0.05655 | 0.1 | 0.007
WEG 630 kW 400 V 2p | 0.4 | 0.63 | 5.9 | 2 | 2970 | 230 | 0.388 | 0.92 | 95.7 | 0.75 | 0.91 | 95.8 | 0.5 | 0.87 | 95.6 | 0.25 | 0.68 | 93.1 | 0.1 | 0.41 | 87.5 | FALSE | 100 | 2850 | 19 | 0.0111 | -0.46 | 8.255 | TRUE | TRUE | FALSE | FALSE | 0.03067 | 0.12906 | 1.3769 | 0.007 | 0.06105 | 0.1 | 0.001
WEG 630 kW 400 V 4p | 0.4 | 0.63 | 5.5 | 4 | 1484 | 230 | 0.437 | 0.88 | 95.9 | 0.75 | 0.86 | 95.9 | 0.5 | 0.82 | 95.8 | 0.25 | 0.64 | 94 | 0.1 | 0.38 | 90 | FALSE | 90 | 1425 | 39 | 0.0111 | -0.46 | 8.255 | TRUE | TRUE | FALSE | FALSE | 0.02698 | 0.14431 | 1.2519 | 0.00725 | 0.059625 | 0.07038 | 0.01
WEG 630 kW 400 V 8p | 0.4 | 0.63 | 5.5 | 8 | 744 | 210 | 0.383 | 0.82 | 95 | 0.75 | 0.8 | 95.5 | 0.5 | 0.75 | 95.4 | 0.25 | 0.54 | 94.5 | 0.1 | 0.29 | 89.2 | FALSE | 80 | 712.5 | 262 | 0.0111 | -0.46 | 8.255 | TRUE | TRUE | FALSE | FALSE | 0.03472 | 0.16309 | 1 | 0.0071869 | 0.0655 | 0.085 | 0.008
WEG 900 kW 400 V 2p | 0.4 | 0.9 | 6.2 | 2 | 2977 | 240 | 0.388 | 0.92 | 96.2 | 0.75 | 0.91 | 96.4 | 0.5 | 0.89 | 96.1 | 0.25 | 0.72 | 94.2 | 0.1 | 0.45 | 89.5 | FALSE | 70 | 2850 | 35.8 | 0.0111 | -0.46 | 8.255 | TRUE | TRUE | FALSE | FALSE | 0.02812 | 0.13906 | 1.1269 | 0.007506 | 0.045 | 0.09 | 0.001
WEG 900 kW 400 V 4p | 0.4 | 0.9 | 6.7 | 4 | 1490 | 240 | 0.437 | 0.89 | 96.2 | 0.75 | 0.875 | 96.2 | 0.5 | 0.8 | 96.1 | 0.25 | 0.6 | 94.2 | 0.1 | 0.3 | 88.5 | FALSE | 90 | 1425 | 75.1 | 0.0111 | -0.46 | 8.255 | TRUE | TRUE | FALSE | FALSE | 0.02807 | 0.13925 | 1.5 | 0.00944 | 0.059513 | 0.09 | 0.012
WEG 450 kW 10 kV 2p | 10 | 0.45 | 6.1 | 2 | 2982 | 250 | 0.382 | 0.92 | 94.1 | 0.75 | 0.92 | 94.2 | 0.5 | 0.9 | 93.7 | 0.25 | 0.75 | 92 | 0.1 | 0.5 | 85 | FALSE | 50 | 2850 | 54 | 0.0111 | -0.46 | 8.455 | TRUE | TRUE | FALSE | FALSE | 0.04905 | 0.12813 | 2.6269 | 0.00506 | 0.04 | 0.06038 | 0.0525
WEG 450 kW 10 kV 4p | 10 | 0.45 | 5.4 | 4 | 1487 | 230 | 0.35612 | 0.9 | 95.1 | 0.75 | 0.89 | 95.2 | 0.5 | 0.85 | 94.8 | 0.25 | 0.65 | 93 | 0.1 | 0.37 | 86 | FALSE | 90 | 1425 | 88.3 | 0.0111 | -0.46 | 8.455 | TRUE | TRUE | FALSE | FALSE | 0.036617 | 0.15 | 4.877 | 0.0081875 | 0.065 | 0.060375 | 0.0125
WEG 450 kW 10 kV 6p | 10 | 0.45 | 5.5 | 6 | 991 | 210 | 0.349 | 0.85 | 94.2 | 0.75 | 0.82 | 94.1 | 0.5 | 0.77 | 93.1 | 0.25 | 0.55 | 90 | 0.1 | 0.3 | 80 | FALSE | 80 | 950 | 137.3 | 0.0111 | -0.46 | 8.455 | TRUE | TRUE | FALSE | FALSE | 0.042028 | 0.15469 | 1 | 0.00725 | 0.0525 | 0.060375 | 0.0125
WEG 630 kW 10 kV 2p | 10 | 0.63 | 6.1 | 2 | 2982 | 250 | 0.354 | 0.92 | 94.7 | 0.75 | 0.92 | 94.7 | 0.5 | 0.9 | 94.3 | 0.25 | 0.75 | 92.5 | 0.1 | 0.49 | 85 | FALSE | 50 | 2850 | 62.1 | 0.0111 | -0.46 | 8.455 | TRUE | TRUE | FALSE | FALSE | 0.043501 | 0.1375 | 1.7129 | 0.005375 | 0.02875 | 0.052875 | 0.0125
WEG 630 kW 10 kV 4p | 10 | 0.63 | 5.4 | 4 | 1487 | 230 | 0.334 | 0.9 | 95.4 | 0.75 | 0.89 | 95.5 | 0.5 | 0.85 | 95.1 | 0.25 | 0.65 | 93 | 0.1 | 0.37 | 87 | FALSE | 90 | 1425 | 98.5 | 0.0111 | -0.46 | 8.455 | TRUE | TRUE | FALSE | FALSE | 0.03389 | 0.15 | 2.5957 | 0.00756 | 0.0625 | 0.06038 | 0.0125
WEG 800 kW 10 kV 2p | 10 | 0.8 | 6.1 | 2 | 2982 | 230 | 0.334 | 0.92 | 95.1 | 0.75 | 0.92 | 95.2 | 0.5 | 0.9 | 94.7 | 0.25 | 0.75 | 92.5 | 0.1 | 0.49 | 85 | FALSE | 50 | 2850 | 69.4 | 0.0111 | -0.46 | 8.455 | TRUE | TRUE | FALSE | FALSE | 0.039799 | 0.13125 | 1.0957 | 0.005375 | 0.0475 | 0.055375 | 0.04375
WEG 1 MW 10 kV 2p | 10 | 1 | 6.1 | 2 | 2982 | 250 | 0.299 | 0.92 | 95.5 | 0.75 | 0.92 | 95.6 | 0.5 | 0.9 | 95.1 | 0.25 | 0.75 | 92.5 | 0.1 | 0.49 | 85 | FALSE | 50 | 2850 | 74.6 | 0.0111 | -0.46 | 8.455 | TRUE | TRUE | FALSE | FALSE | 0.036097 | 0.13437 | 1.752 | 0.0050625 | 0.04 | 0.060375 | 0.0375
WEG 800 kW 10 kV 4p | 10 | 0.8 | 5.4 | 4 | 1487 | 230 | 0.334 | 0.9 | 95.6 | 0.75 | 0.89 | 95.7 | 0.5 | 0.85 | 95.3 | 0.25 | 0.64 | 93 | 0.1 | 0.37 | 86 | FALSE | 90 | 1425 | 106 | 0.0111 | -0.46 | 8.455 | TRUE | TRUE | FALSE | FALSE | 0.032078 | 0.15156 | 4.127 | 0.00725 | 0.065 | 0.060375 | 0.0125
WEG 1 MW 10 kV 4p | 10 | 1 | 5.4 | 4 | 1487 | 230 | 0.308 | 0.9 | 95.8 | 0.75 | 0.89 | 95.9 | 0.5 | 0.85 | 95.5 | 0.25 | 0.64 | 93 | 0.1 | 0.37 | 87 | FALSE | 90 | 1425 | 114 | 0.0111 | -0.46 | 8.455 | TRUE | TRUE | FALSE | FALSE | 0.03026 | 0.15156 | 2.3066 | 0.00694 | 0.06125 | 0.06038 | 0.0125
WEG 1,25 MW 10 kV 4p | 10 | 1.25 | 5.4 | 4 | 1487 | 230 | 0.311 | 0.9 | 96 | 0.75 | 0.89 | 96.1 | 0.5 | 0.85 | 95.7 | 0.25 | 0.65 | 93 | 0.1 | 0.38 | 87 | FALSE | 90 | 1425 | 122.5 | 0.0111 | -0.46 | 8.455 | TRUE | TRUE | FALSE | FALSE | 0.03026 | 0.15156 | 2.3066 | 0.00694 | 0.06125 | 0.06038 | 0.0125
WEG 1,6 MW 10 kV 4p | 10 | 1.6 | 5.6 | 4 | 1490 | 240 | 0.28 | 0.9 | 96.3 | 0.75 | 0.89 | 96.3 | 0.5 | 0.85 | 95.9 | 0.25 | 0.64 | 94 | 0.1 | 0.36 | 88 | FALSE | 80 | 1425 | 145 | 0.0111 | -0.46 | 8.455 | TRUE | TRUE | FALSE | FALSE | 0.027483 | 0.15 | 4.002 | 0.0050625 | 0.05375 | 0.060375 | 0.0125
WEG 3,15 MW 10 kV 4p | 10 | 3.15 | 5.5 | 4 | 1490 | 240 | 0.255 | 0.9 | 96.7 | 0.75 | 0.88 | 96.8 | 0.5 | 0.82 | 96.8 | 0.25 | 0.6 | 95 | 0.1 | 0.32 | 90 | FALSE | 80 | 1425 | 275 | 0.0111 | -0.46 | 8.455 | TRUE | TRUE | FALSE | FALSE | 0.02386 | 0.15469 | 4.0019 | 0.00537 | 0.055 | 0.06038 | 0.0125
WEG 6,3 MW 10 kV 4p | 10 | 6.3 | 5.7 | 4 | 1494 | 230 | 0.239 | 0.9 | 97.2 | 0.75 | 0.9 | 97.2 | 0.5 | 0.88 | 96.9 | 0.25 | 0.71 | 95.5 | 0.1 | 0.43 | 91 | FALSE | 70 | 1425 | 1010 | 0.0111 | -0.46 | 8.455 | TRUE | TRUE | FALSE | FALSE | 0.02169 | 0.14844 | 3 | 0.0065 | 0.0475 | 0.06038 | 0.0125

## Zigzag
Name | R0 | X0
| Ohm | Ohm
Nulpuntstrafo 7 Ohm | 0 | 7
Nulpuntstrafo 20 Ohm | 0 | 20

## Wind
Name | Unom | Pnom | Ik/Inom | R/X | WindCutIn | WindNom | WindCuttingOut | WindCuttedOut | Snom
| kV | MW |  |  | m/s | m/s | m/s | m/s | MVA
3 MW 22 kV | 22 | 3 | 3 | 0.1 | 4 | 13 | 25 | 30 | 3
3 MW 10 kV | 10 | 3 | 3 | 0.1 | 4 | 13 | 25 | 30 | 3
4 MW 10 kV | 10 | 4 | 3 | 0.1 | 4 | 13 | 25 | 30 | 4
5 MW 10 kV | 10 | 5 | 3 | 0.1 | 4 | 13 | 25 | 30 | 5
6 MW 10 kV | 10 | 6 | 3 | 0.1 | 4 | 13 | 25 | 30 | 6
8 MW 10 kV | 10 | 8 | 3 | 0.1 | 4 | 13 | 25 | 30 | 8
10 MW 10 kV | 10 | 10 | 3 | 0.1 | 4 | 13 | 25 | 30 | 10
Snom t/m Vision 9.0.1; Pnom vanaf Vision 9.1

## Fuse
Name | Shortname | Unom | Inom | ThreePhase | I1 | T1 | I2 | T2 | I3 | T3 | I4 | T4 | I5 | T5 | I6 | T6 | I7 | T7 | I8 | T8 | I9 | T9 | I10 | T10 | I11 | T11 | I12 | T12 | I13 | T13 | I14 | T14 | I15 | T15 | I16 | T16
|  | kV | A |  | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s
Voorbeeld 35 A | Fuse 35 | 0.5 | 35 | FALSE | 52 | 1000 | 52 | 500 | 53 | 200 | 55 | 100 | 58 | 50 | 61 | 20 | 70 | 10 | 80 | 5 | 90 | 2 | 105 | 1 | 125 | 0.5 | 160 | 0.2 | 205 | 0.1 | 265 | 0.05 | 380 | 0.02 | 525 | 0.01
Voorbeeld 50 A | Fuse 50 | 0.5 | 50 | FALSE | 79 | 1000 | 84 | 500 | 94 | 200 | 106 | 100 | 119 | 50 | 141 | 20 | 160 | 10 | 175 | 5 | 200 | 2 | 215 | 1 | 235 | 0.5 | 270 | 0.2 | 315 | 0.1 | 375 | 0.05 | 485 | 0.02 | 590 | 0.01
Voorbeeld 63 A | Fuse 63 | 0.5 | 63 | FALSE | 106 | 1000 | 112 | 500 | 126 | 200 | 141 | 100 | 158 | 50 | 178 | 20 | 210 | 10 | 230 | 5 | 260 | 2 | 290 | 1 | 325 | 0.5 | 380 | 0.2 | 435 | 0.1 | 525 | 0.05 | 680 | 0.02 | 870 | 0.01
Voorbeeld 80 A | Fuse 80 | 0.5 | 80 | FALSE | 133 | 1000 | 141 | 500 | 154 | 200 | 173 | 100 | 194 | 50 | 230 | 20 | 275 | 10 | 315 | 5 | 365 | 2 | 405 | 1 | 460 | 0.5 | 540 | 0.2 | 625 | 0.1 | 765 | 0.05 | 975 | 0.02 | 1230 | 0.01
Voorbeeld 100 A | Fuse 100 | 0.5 | 100 | FALSE | 163 | 1000 | 178 | 500 | 200 | 200 | 224 | 100 | 251 | 50 | 307 | 20 | 360 | 10 | 410 | 5 | 485 | 2 | 535 | 1 | 615 | 0.5 | 720 | 0.2 | 820 | 0.1 | 975 | 0.05 | 1285 | 0.02 | 1665 | 0.01
Voorbeeld 125 A | Fuse 125 | 0.5 | 125 | FALSE | 211 | 1000 | 230 | 500 | 266 | 200 | 299 | 100 | 345 | 50 | 410 | 20 | 490 | 10 | 555 | 5 | 645 | 2 | 720 | 1 | 810 | 0.5 | 935 | 0.2 | 1050 | 0.1 | 1250 | 0.05 | 1615 | 0.02 | 2095 | 0.01
Voorbeeld 160 A | Fuse 160 | 0.5 | 160 | FALSE | 295 | 1000 | 315 | 500 | 360 | 200 | 405 | 100 | 455 | 50 | 540 | 20 | 625 | 10 | 700 | 5 | 810 | 2 | 885 | 1 | 1005 | 0.5 | 1180 | 0.2 | 1380 | 0.1 | 1665 | 0.05 | 2155 | 0.02 | 2875 | 0.01
Voorbeeld 200 A | Fuse 200 | 0.5 | 200 | FALSE | 350 | 1000 | 375 | 500 | 430 | 200 | 485 | 100 | 555 | 50 | 665 | 20 | 755 | 10 | 845 | 5 | 975 | 2 | 1080 | 1 | 1250 | 0.5 | 1485 | 0.2 | 1740 | 0.1 | 2095 | 0.05 | 2795 | 0.02 | 3670 | 0.01
Voorbeeld 225 A | Fuse 225 | 0.5 | 225 | FALSE | 430 | 1000 | 470 | 500 | 540 | 200 | 625 | 100 | 720 | 50 | 860 | 20 | 965 | 10 | 1080 | 5 | 1265 | 2 | 1400 | 1 | 1615 | 0.5 | 1895 | 0.2 | 2185 | 0.1 | 2635 | 0.05 | 3465 | 0.02 | 4490 | 0.01
Voorbeeld 250 A | Fuse 250 | 0.5 | 250 | FALSE | 485 | 1000 | 540 | 500 | 645 | 200 | 720 | 100 | 835 | 50 | 965 | 20 | 1080 | 10 | 1215 | 5 | 1400 | 2 | 1550 | 1 | 1765 | 0.5 | 2095 | 0.2 | 2490 | 0.1 | 3045 | 0.05 | 4180 | 0.02 | 5415 | 0.01
Voorbeeld 315 A | Fuse 315 | 0.5 | 315 | FALSE | 630 | 1000 | 715 | 500 | 845 | 200 | 960 | 100 | 1105 | 50 | 1325 | 20 | 1575 | 10 | 1908 | 5 | 2413 | 2 | 2928 | 1 | 3467 | 0.5 | 4269 | 0.2 | 4941 | 0.1 | 5707 | 0.05 | 6955 | 0.02 | 8218 | 0.01
Jean Muller 25 A gL/gG | JMu 25 A | 0.5 | 25 | FALSE | 42.5 | 1000 | 46.6 | 500 | 52.3 | 200 | 57.4 | 100 | 62.9 | 50 | 72.4 | 20 | 80.5 | 10 | 91.9 | 5 | 108.1 | 2 | 128.1 | 1 | 153.9 | 0.5 | 202.5 | 0.2 | 265.4 | 0.1 | 358.2 | 0.05 | 593.6 | 0.02 | 919.8 | 0.01
Jean Muller 35 A gL/gG | JMu 35 A | 0.5 | 35 | FALSE | 58.7 | 1000 | 63.9 | 500 | 70.1 | 200 | 76.2 | 100 | 84.1 | 50 | 98.7 | 20 | 110.6 | 10 | 126.3 | 5 | 152.3 | 2 | 179 | 1 | 217 | 0.5 | 286.4 | 0.2 | 367.9 | 0.1 | 487.1 | 0.05 | 798.4 | 0.02 | 1243.6 | 0.01
Jean Muller 50 A gL/gG | JMu 50 A | 0.5 | 50 | FALSE | 86.8 | 1000 | 96.2 | 500 | 110.4 | 200 | 123 | 100 | 137.3 | 50 | 162.6 | 20 | 185.4 | 10 | 211.1 | 5 | 257.5 | 2 | 309.2 | 1 | 373.9 | 0.5 | 493.4 | 0.2 | 646.1 | 0.1 | 873.5 | 0.05 | 1426.2 | 0.02 | 2171.2 | 0.01
Jean Muller 63 A gL/gG | JMu 63 A | 0.5 | 63 | FALSE | 109.2 | 1000 | 121.7 | 500 | 139.7 | 200 | 155.8 | 100 | 172.8 | 50 | 202.2 | 20 | 233.2 | 10 | 268.8 | 5 | 330.7 | 2 | 385.1 | 1 | 472.2 | 0.5 | 609.3 | 0.2 | 822.7 | 0.1 | 1141.3 | 0.05 | 1815.7 | 0.02 | 2742.9 | 0.01
Jean Muller 80 A gL/gG | JMu 80 A | 0.5 | 80 | FALSE | 152.3 | 1000 | 167.9 | 500 | 195.5 | 200 | 213.5 | 100 | 240.8 | 50 | 280.8 | 20 | 323.2 | 10 | 373.2 | 5 | 456 | 2 | 533.8 | 1 | 623.8 | 0.5 | 818.2 | 0.2 | 1007.4 | 0.1 | 1357.5 | 0.05 | 2036.2 | 0.02 | 3098.9 | 0.01
Jean Muller 100 A gL/gG | JMu 100 A | 0.5 | 100 | FALSE | 190.8 | 1000 | 209.8 | 500 | 242.5 | 200 | 270.7 | 100 | 302.2 | 50 | 355 | 20 | 407.4 | 10 | 466.3 | 5 | 563.8 | 2 | 658.8 | 1 | 773.6 | 0.5 | 1005.3 | 0.2 | 1254.7 | 0.1 | 1661 | 0.05 | 2547.3 | 0.02 | 3790.5 | 0.01
Jean Muller 125 A gL/gG | JMu 125 A | 0.5 | 125 | FALSE | 231.8 | 1000 | 256.6 | 500 | 302.7 | 200 | 337 | 100 | 384.9 | 50 | 466.1 | 20 | 547.2 | 10 | 635.3 | 5 | 785.4 | 2 | 930.2 | 1 | 1095.5 | 0.5 | 1446.2 | 0.2 | 1777.6 | 0.1 | 2366.5 | 0.05 | 3549.9 | 0.02 | 5241.2 | 0.01
Jean Muller 160 A gL/gG | JMu 160 A | 0.5 | 160 | FALSE | 296.7 | 1000 | 330.1 | 500 | 385.7 | 200 | 434.1 | 100 | 487.8 | 50 | 584 | 20 | 677.6 | 10 | 796.4 | 5 | 995.4 | 2 | 1204.4 | 1 | 1451.6 | 0.5 | 1898.5 | 0.2 | 2325.9 | 0.1 | 2992 | 0.05 | 4466.5 | 0.02 | 6718.2 | 0.01
Jean Muller 200 A gL/gG | JMu 200 A | 0.5 | 200 | FALSE | 392.3 | 1000 | 443.6 | 500 | 515.7 | 200 | 586.8 | 100 | 664.7 | 50 | 782.3 | 20 | 887.2 | 10 | 1016.1 | 5 | 1241.5 | 2 | 1446.3 | 1 | 1680.1 | 0.5 | 2137.3 | 0.2 | 2655.8 | 0.1 | 3386.4 | 0.05 | 5473.7 | 0.02 | 8127.4 | 0.01
Jean Muller 224 A gL/gG | JMu 224 A | 0.5 | 224 | FALSE | 441.2 | 1000 | 497.7 | 500 | 589.9 | 200 | 672.8 | 100 | 767.5 | 50 | 903 | 20 | 1031.2 | 10 | 1206.3 | 5 | 1460.1 | 2 | 1694.2 | 1 | 1968.4 | 0.5 | 2493.5 | 0.2 | 3115.1 | 0.1 | 4002.1 | 0.05 | 6242.5 | 0.02 | 9347.1 | 0.01
Jean Muller 250 A gL/gG | JMu 250 A | 0.5 | 250 | FALSE | 496 | 1000 | 556.6 | 500 | 666.3 | 200 | 756.3 | 100 | 858.6 | 50 | 1029.7 | 20 | 1189.7 | 10 | 1377.7 | 5 | 1650.2 | 2 | 1910 | 1 | 2244.1 | 0.5 | 2841.7 | 0.2 | 3571.5 | 0.1 | 4654.5 | 0.05 | 7123.5 | 0.02 | 10789.4 | 0.01
Jean Muller 300 A gL/gG | JMu 300 A | 0.5 | 300 | FALSE | 565.7 | 1000 | 629 | 500 | 764.3 | 200 | 879.7 | 100 | 1038.3 | 50 | 1275.3 | 20 | 1493.9 | 10 | 1761.9 | 5 | 2137.9 | 2 | 2506.1 | 1 | 2945.3 | 0.5 | 3782.4 | 0.2 | 4722.9 | 0.1 | 6131.4 | 0.05 | 9597.5 | 0.02 | 14045.6 | 0.01
Jean Muller 315 A gL/gG | JMu 315 A | 0.5 | 315 | FALSE | 594.2 | 1000 | 659.9 | 500 | 805.8 | 200 | 933.9 | 100 | 1106.1 | 50 | 1364.3 | 20 | 1600.1 | 10 | 1905.1 | 5 | 2305 | 2 | 2724.6 | 1 | 3205.2 | 0.5 | 4052.7 | 0.2 | 5072.7 | 0.1 | 6585.9 | 0.05 | 10209.3 | 0.02 | 14846.5 | 0.01
Jean Muller 355 A gL/gG | JMu 355 A | 0.5 | 355 | FALSE | 669.6 | 1000 | 754.8 | 500 | 911.6 | 200 | 1042.4 | 100 | 1232.9 | 50 | 1506 | 20 | 1787 | 10 | 2098.2 | 5 | 2591.2 | 2 | 3090.6 | 1 | 3668.4 | 0.5 | 4691.8 | 0.2 | 5881.6 | 0.1 | 7648.8 | 0.05 | 11757.3 | 0.02 | 17285.4 | 0.01
Jean Muller 400 A gL/gG | JMu 400 A | 0.5 | 400 | FALSE | 749.6 | 1000 | 830.5 | 500 | 997.1 | 200 | 1153.8 | 100 | 1349 | 50 | 1632.6 | 20 | 1962.1 | 10 | 2331.7 | 5 | 2883.2 | 2 | 3406.5 | 1 | 4026.6 | 0.5 | 5185.8 | 0.2 | 6516.1 | 0.1 | 8387.3 | 0.05 | 12953.7 | 0.02 | 18862.7 | 0.01
Jean Muller 425 A gL/gG | JMu 425 A | 0.5 | 425 | FALSE | 924.3 | 1000 | 1023.5 | 500 | 1174.6 | 200 | 1301.5 | 100 | 1433.3 | 50 | 1739.1 | 20 | 2021 | 10 | 2431.8 | 5 | 3061.2 | 2 | 3708.7 | 1 | 4515.5 | 0.5 | 5801.8 | 0.2 | 7280.8 | 0.1 | 9410.9 | 0.05 | 14272.4 | 0.02 | 19973.8 | 0.01
Jean Muller 500 A gL/gG | JMu 500 A | 0.5 | 500 | FALSE | 1108.1 | 1000 | 1251.8 | 500 | 1465.5 | 200 | 1613 | 100 | 1816 | 50 | 2176.3 | 20 | 2609 | 10 | 3120.5 | 5 | 3889.3 | 2 | 4633.3 | 1 | 5532.1 | 0.5 | 7170.6 | 0.2 | 8912.2 | 0.1 | 11251.3 | 0.05 | 17242.3 | 0.02 | 23262.3 | 0.01
Jean Muller 630 A gL/gG | JMu 630 A | 0.5 | 630 | FALSE | 1416.9 | 1000 | 1623.9 | 500 | 1905.1 | 200 | 2119 | 100 | 2368.1 | 50 | 2891.3 | 20 | 3384.4 | 10 | 3981.7 | 5 | 5015 | 2 | 6031.2 | 1 | 7243.8 | 0.5 | 9264.1 | 0.2 | 11827.6 | 0.1 | 15534.7 | 0.05 | 23003.9 | 0.02 | 32250 | 0.01
Jean Muller 500 A gL/gG NH4a | JMu 500 A | 0.5 | 500 | FALSE | 993.8 | 1000 | 1097.8 | 500 | 1309.7 | 200 | 1507.7 | 100 | 1743.2 | 50 | 2185.3 | 20 | 2541.2 | 10 | 3015.4 | 5 | 3690.4 | 2 | 4327.4 | 1 | 5053.7 | 0.5 | 6136.5 | 0.2 | 7173.8 | 0.1 | 8314.1 | 0.05 | 10135.1 | 0.02 | 11795.5 | 0.01
Jean Muller 630 A gL/gG NH4a | JMu 630 A | 0.5 | 630 | FALSE | 1289.4 | 1000 | 1422.3 | 500 | 1679 | 200 | 1936.7 | 100 | 2222 | 50 | 2825.5 | 20 | 3261.7 | 10 | 3882.2 | 5 | 4734.3 | 2 | 5541.5 | 1 | 6452.8 | 0.5 | 7848.1 | 0.2 | 9120.2 | 0.1 | 10569.7 | 0.05 | 12882.7 | 0.02 | 14946.8 | 0.01
Jean Muller 800 A gL/gG | JMu 800 A | 0.5 | 800 | FALSE | 1647.9 | 1000 | 1848.3 | 500 | 2233.6 | 200 | 2577.1 | 100 | 2959.5 | 50 | 3680.4 | 20 | 4228.4 | 10 | 4992.8 | 5 | 6058.8 | 2 | 7136.7 | 1 | 8323.9 | 0.5 | 10086.4 | 0.2 | 11731.4 | 0.1 | 13591 | 0.05 | 16539.8 | 0.02 | 19219.1 | 0.01
Jean Muller 1000 A gL/gG | JMu 1000 A | 0.5 | 1000 | FALSE | 2179.5 | 1000 | 2455.2 | 500 | 2943 | 200 | 3402.2 | 100 | 3946.7 | 50 | 4911.8 | 20 | 5678.5 | 10 | 6702.6 | 5 | 8163.4 | 2 | 9616.7 | 1 | 11355.9 | 0.5 | 14077.4 | 0.2 | 16650.9 | 0.1 | 19242.5 | 0.05 | 23437 | 0.02 | 27336.8 | 0.01
Jean Muller 1250 A gL/gG | JMu 1250 A | 0.5 | 1250 | FALSE | 2718.6 | 1000 | 3051.2 | 500 | 3681.6 | 200 | 4249.9 | 100 | 4893.7 | 50 | 6064.1 | 20 | 6979.6 | 10 | 8259.7 | 5 | 10191.9 | 2 | 12314.2 | 1 | 14977.3 | 0.5 | 18865.6 | 0.2 | 22363.2 | 0.1 | 25933.6 | 0.05 | 31324.6 | 0.02 | 36261.3 | 0.01
Jean Muller 1500 A gL/gG | JMu 1500 A | 0.5 | 1500 | FALSE | 4469.1 | 1000 | 5058.1 | 500 | 6036.9 | 200 | 6857.1 | 100 | 7795.6 | 50 | 9625.1 | 20 | 11006 | 10 | 12993.7 | 5 | 15625.7 | 2 | 18520 | 1 | 21765.1 | 0.5 | 26369.8 | 0.2 | 30664.9 | 0.1 | 35989 | 0.05 | 44391.1 | 0.02 | 51718 | 0.01
Jean Muller 1600 A gL/gG | JMu 1600 A | 0.5 | 1600 | FALSE | 4896.1 | 1000 | 5494.4 | 500 | 6621.8 | 200 | 7676.6 | 100 | 8835.7 | 50 | 10902.3 | 20 | 12556.4 | 10 | 14766.7 | 5 | 17913.4 | 2 | 21226.5 | 1 | 25053.5 | 0.5 | 30642.7 | 0.2 | 36068.8 | 0.1 | 42059.9 | 0.05 | 51484.5 | 0.02 | 59813.7 | 0.01
IEC 2 A gG | IEC 2 A | 0.5 | 2 | FALSE | 4.5 | 1000 | 4.8 | 500 | 5.3 | 200 | 5.7 | 100 | 6.6 | 50 | 7.2 | 20 | 8.1 | 10 | 9.3 | 5 | 11 | 2 | 13 | 1 | 15 | 0.5 | 19 | 0.2 | 21.5 | 0.1 | 27.5 | 0.05 | 36.5 | 0.02 | 46 | 0.01
IEC 4 A gG | IEC 4 A | 0.5 | 4 | FALSE | 9.5 | 1000 | 10 | 500 | 11 | 200 | 12 | 100 | 13 | 50 | 14.8 | 20 | 16.5 | 10 | 18.7 | 5 | 22.5 | 2 | 26 | 1 | 30.5 | 0.5 | 38.5 | 0.2 | 47 | 0.1 | 58 | 0.05 | 78 | 0.02 | 97 | 0.01
IEC 6 A gG | IEC 6 A | 0.5 | 6 | FALSE | 13.5 | 1000 | 14.5 | 500 | 16 | 200 | 17 | 100 | 19 | 50 | 21.5 | 20 | 24 | 10 | 27 | 5 | 32.5 | 2 | 38 | 1 | 44 | 0.5 | 56 | 0.2 | 70 | 0.1 | 87 | 0.05 | 118 | 0.02 | 148 | 0.01
IEC 10 A gG | IEC 10 A | 0.5 | 10 | FALSE | 21 | 1000 | 23 | 500 | 26 | 200 | 28 | 100 | 31 | 50 | 36 | 20 | 41.5 | 10 | 48 | 5 | 57 | 2 | 66 | 1 | 78 | 0.5 | 96 | 0.2 | 115 | 0.1 | 139 | 0.05 | 190 | 0.02 | 240 | 0.01
IEC 16 A gG | IEC 16 A | 0.5 | 16 | FALSE | 31 | 1000 | 34 | 500 | 38 | 200 | 42 | 100 | 46 | 50 | 52 | 20 | 59 | 10 | 66 | 5 | 78 | 2 | 90 | 1 | 105 | 0.5 | 125 | 0.2 | 152 | 0.1 | 185 | 0.05 | 250 | 0.02 | 320 | 0.01
IEC 20 A gG | IEC 20 A | 0.5 | 20 | FALSE | 40 | 1000 | 44 | 500 | 49 | 200 | 55 | 100 | 60 | 50 | 69 | 20 | 76 | 10 | 87 | 5 | 105 | 2 | 120 | 1 | 140 | 0.5 | 170 | 0.2 | 200 | 0.1 | 250 | 0.05 | 345 | 0.02 | 440 | 0.01
IEC 25 A gG | IEC 25 A | 0.5 | 25 | FALSE | 51 | 1000 | 58 | 500 | 65 | 200 | 71 | 100 | 78 | 50 | 90 | 20 | 99 | 10 | 110 | 5 | 130 | 2 | 150 | 1 | 170 | 0.5 | 215 | 0.2 | 260 | 0.1 | 320 | 0.05 | 425 | 0.02 | 530 | 0.01
IEC 32 A gG | IEC 32 A | 0.5 | 32 | FALSE | 66 | 1000 | 75 | 500 | 85 | 200 | 95 | 100 | 107 | 50 | 125 | 20 | 139 | 10 | 156 | 5 | 190 | 2 | 225 | 1 | 255 | 0.5 | 310 | 0.2 | 360 | 0.1 | 435 | 0.05 | 580 | 0.02 | 730 | 0.01
IEC 50 A gG | IEC 50 A | 0.5 | 50 | FALSE | 108 | 1000 | 120 | 500 | 144 | 200 | 162 | 100 | 182 | 50 | 210 | 20 | 235 | 10 | 265 | 5 | 325 | 2 | 385 | 1 | 450 | 0.5 | 540 | 0.2 | 630 | 0.1 | 770 | 0.05 | 1020 | 0.02 | 1300 | 0.01
IEC 63 A gG | IEC 63 A | 0.5 | 63 | FALSE | 128 | 1000 | 145 | 500 | 173 | 200 | 196 | 100 | 220 | 50 | 250 | 20 | 280 | 10 | 320 | 5 | 380 | 2 | 440 | 1 | 520 | 0.5 | 660 | 0.2 | 810 | 0.1 | 1000 | 0.05 | 1320 | 0.02 | 1660 | 0.01
IEC 80 A gG | IEC 80 A | 0.5 | 80 | FALSE | 166 | 1000 | 183 | 500 | 210 | 200 | 238 | 100 | 273 | 50 | 328 | 20 | 381 | 10 | 445 | 5 | 545 | 2 | 665 | 1 | 790 | 0.5 | 965 | 0.2 | 1120 | 0.1 | 1340 | 0.05 | 1760 | 0.02 | 2190 | 0.01
IEC 100 A gG | IEC 100 A | 0.5 | 100 | FALSE | 220 | 1000 | 245 | 500 | 279 | 200 | 314 | 100 | 357 | 50 | 429 | 20 | 500 | 10 | 590 | 5 | 725 | 2 | 835 | 1 | 975 | 0.5 | 1220 | 0.2 | 1460 | 0.1 | 1790 | 0.05 | 2380 | 0.02 | 2970 | 0.01
IEC 125 A gG | IEC 125 A | 0.5 | 125 | FALSE | 260 | 1000 | 292 | 500 | 340 | 200 | 390 | 100 | 452 | 50 | 550 | 20 | 645 | 10 | 760 | 5 | 960 | 2 | 1170 | 1 | 1390 | 0.5 | 1690 | 0.2 | 1970 | 0.1 | 2350 | 0.05 | 3030 | 0.02 | 3780 | 0.01
IEC 160 A gG | IEC 160 A | 0.5 | 160 | FALSE | 325 | 1000 | 367 | 500 | 437 | 200 | 505 | 100 | 595 | 50 | 720 | 20 | 825 | 10 | 950 | 5 | 1160 | 2 | 1350 | 1 | 1610 | 0.5 | 2080 | 0.2 | 2540 | 0.1 | 3110 | 0.05 | 4050 | 0.02 | 4960 | 0.01
IEC 200 A gG | IEC 200 A | 0.5 | 200 | FALSE | 441 | 1000 | 510 | 500 | 610 | 200 | 710 | 100 | 815 | 50 | 990 | 20 | 1130 | 10 | 1320 | 5 | 1690 | 2 | 2030 | 1 | 2400 | 0.5 | 2940 | 0.2 | 3450 | 0.1 | 4090 | 0.05 | 5230 | 0.02 | 6370 | 0.01
IEC 224 A gG | IEC 224 A | 0.5 | 224 | FALSE | 504 | 1000 | 562 | 500 | 647 | 200 | 760 | 100 | 876 | 50 | 1061 | 20 | 1233 | 10 | 1451 | 5 | 1795 | 2 | 2138 | 1 | 2525 | 0.5 | 3241 | 0.2 | 3893 | 0.1 | 4654.5 | 0.05 | 6123.5 | 0.02 | 7289.4 | 0.01
IEC 250 A gG | IEC 250 A | 0.5 | 250 | FALSE | 520 | 1000 | 600 | 500 | 730 | 200 | 865 | 100 | 1020 | 50 | 1230 | 20 | 1410 | 10 | 1640 | 5 | 1990 | 2 | 2350 | 1 | 2820 | 0.5 | 3640 | 0.2 | 4470 | 0.1 | 5480 | 0.05 | 7100 | 0.02 | 8690 | 0.01
IEC 315 A gG | IEC 315 A | 0.5 | 315 | FALSE | 740 | 1000 | 860 | 500 | 1030 | 200 | 1190 | 100 | 1370 | 50 | 1660 | 20 | 1920 | 10 | 2240 | 5 | 2730 | 2 | 3230 | 1 | 3830 | 0.5 | 4870 | 0.2 | 5880 | 0.1 | 7100 | 0.05 | 9190 | 0.02 | 11300 | 0.01
IEC 400 A gG | IEC 400 A | 0.5 | 400 | FALSE | 915 | 1000 | 1050 | 500 | 1240 | 200 | 1410 | 100 | 1610 | 50 | 1950 | 20 | 2340 | 10 | 2730 | 5 | 3590 | 2 | 4330 | 1 | 5230 | 0.5 | 6640 | 0.2 | 8020 | 0.1 | 9770 | 0.05 | 12600 | 0.02 | 15400 | 0.01
IEC 500 A gG | IEC 500 A | 0.5 | 500 | FALSE | 1210 | 1000 | 1390 | 500 | 1700 | 200 | 1980 | 100 | 2330 | 50 | 2840 | 20 | 3330 | 10 | 3870 | 5 | 4760 | 2 | 5610 | 1 | 6670 | 0.5 | 8530 | 0.2 | 10600 | 0.1 | 13100 | 0.05 | 16800 | 0.02 | 19700 | 0.01
IEC 630 A gG | IEC 630 A | 0.5 | 630 | FALSE | 1620 | 1000 | 1850 | 500 | 2240 | 200 | 2620 | 100 | 3030 | 50 | 3690 | 20 | 4330 | 10 | 5080 | 5 | 6310 | 2 | 7440 | 1 | 8980 | 0.5 | 11700 | 0.2 | 14400 | 0.1 | 17800 | 0.05 | 23400 | 0.02 | 29000 | 0.01
IEC 800 A gG | IEC 800 A | 0.5 | 800 | FALSE | 2040 | 1000 | 2370 | 500 | 2850 | 200 | 3370 | 100 | 3980 | 50 | 4990 | 20 | 5920 | 10 | 7000 | 5 | 8770 | 2 | 10400 | 1 | 12500 | 0.5 | 16100 | 0.2 | 19600 | 0.1 | 23800 | 0.05 | 30600 | 0.02 | 37200 | 0.01
IEC 1000 A gG | IEC 1000 A | 0.5 | 1000 | FALSE | 2510 | 1000 | 2880 | 500 | 3500 | 200 | 4110 | 100 | 4960 | 50 | 6340 | 20 | 7690 | 10 | 9370 | 5 | 11700 | 2 | 13400 | 1 | 15800 | 0.5 | 19900 | 0.2 | 24200 | 0.1 | 29600 | 0.05 | 39600 | 0.02 | 48900 | 0.01
Weber NH 25 A | We 25 A | 0.5 | 25 | FALSE | 46.8 | 1000 | 50.9 | 500 | 57.4 | 200 | 63 | 100 | 70.1 | 50 | 81.5 | 20 | 92.7 | 10 | 104 | 5 | 123 | 2 | 140 | 1 | 161 | 0.5 | 199 | 0.2 | 235 | 0.1 | 277 | 0.05 | 361 | 0.02 | 439 | 0.01
Weber NH 35 A | We 35 A | 0.5 | 35 | FALSE | 65.5 | 1000 | 71 | 500 | 78.7 | 200 | 85.6 | 100 | 94.8 | 50 | 108 | 20 | 123 | 10 | 140 | 5 | 170 | 2 | 197 | 1 | 234 | 0.5 | 300 | 0.2 | 368 | 0.1 | 424 | 0.05 | 604 | 0.02 | 766 | 0.01
Weber NH 50 A | We 50 A | 0.5 | 50 | FALSE | 89.9 | 1000 | 96.5 | 500 | 106 | 200 | 116 | 100 | 128 | 50 | 149 | 20 | 172 | 10 | 197 | 5 | 244 | 2 | 291 | 1 | 346 | 0.5 | 455 | 0.2 | 564 | 0.1 | 679 | 0.05 | 919 | 0.02 | 1132 | 0.01
Weber NH 63 A | We 63 A | 0.5 | 63 | FALSE | 115 | 1000 | 123 | 500 | 137 | 200 | 149 | 100 | 164 | 50 | 189 | 20 | 216 | 10 | 247 | 5 | 305 | 2 | 365 | 1 | 430 | 0.5 | 569 | 0.2 | 701 | 0.1 | 859 | 0.05 | 1171 | 0.02 | 1459 | 0.01
Weber NH 80 A | We 80 A | 0.5 | 80 | FALSE | 146 | 1000 | 162 | 500 | 186 | 200 | 206 | 100 | 234 | 50 | 279 | 20 | 315 | 10 | 360 | 5 | 430 | 2 | 495 | 1 | 571 | 0.5 | 707 | 0.2 | 845 | 0.1 | 991 | 0.05 | 1306 | 0.02 | 1616 | 0.01
Weber NH 100 A | We 100 A | 0.5 | 100 | FALSE | 188 | 1000 | 209 | 500 | 242 | 200 | 272 | 100 | 315 | 50 | 381 | 20 | 432 | 10 | 502 | 5 | 613 | 2 | 716 | 1 | 837 | 0.5 | 1045 | 0.2 | 1227 | 0.1 | 1440 | 0.05 | 1822 | 0.02 | 2138 | 0.01
Weber NH 125 A | We 125 A | 0.5 | 125 | FALSE | 226 | 1000 | 251 | 500 | 289 | 200 | 323 | 100 | 371 | 50 | 447 | 20 | 513 | 10 | 589 | 5 | 716 | 2 | 833 | 1 | 952 | 0.5 | 1173 | 0.2 | 1396 | 0.1 | 1638 | 0.05 | 2110 | 0.02 | 2612 | 0.01
Weber NH 160 A | We 160 A | 0.5 | 160 | FALSE | 304 | 1000 | 337 | 500 | 388 | 200 | 436 | 100 | 502 | 50 | 608 | 20 | 704 | 10 | 815 | 5 | 1000 | 2 | 1113 | 1 | 1359 | 0.5 | 1638 | 0.2 | 2009 | 0.1 | 2369 | 0.05 | 3011 | 0.02 | 3662 | 0.01
Weber NH 200 A | We 200 A | 0.5 | 200 | FALSE | 399 | 1000 | 447 | 500 | 525 | 200 | 600 | 100 | 691 | 50 | 833 | 20 | 961 | 10 | 1112 | 5 | 1347 | 2 | 1567 | 1 | 1822 | 0.5 | 2246 | 0.2 | 2635 | 0.1 | 3065 | 0.05 | 3845 | 0.02 | 4532 | 0.01
Weber NH 224 A | We 224 A | 0.5 | 224 | FALSE | 445 | 1000 | 498 | 500 | 581 | 200 | 661 | 100 | 759 | 50 | 944 | 20 | 1112 | 10 | 1329 | 5 | 1667 | 2 | 2000 | 1 | 2296 | 0.5 | 2817 | 0.2 | 3335 | 0.1 | 3845 | 0.05 | 4976 | 0.02 | 6064 | 0.01
Weber NH 250 A | We 250 A | 0.5 | 250 | FALSE | 502 | 1000 | 569 | 500 | 655 | 200 | 739 | 100 | 852 | 50 | 1045 | 20 | 1221 | 10 | 1453 | 5 | 1830 | 2 | 2177 | 1 | 2487 | 0.5 | 3065 | 0.2 | 3629 | 0.1 | 4259 | 0.05 | 5487 | 0.02 | 6555 | 0.01
Weber NH 315 A | We 315 A | 0.5 | 315 | FALSE | 670 | 1000 | 773 | 500 | 915 | 200 | 1059 | 100 | 1216 | 50 | 1479 | 20 | 1705 | 10 | 1992 | 5 | 2465 | 2 | 2880 | 1 | 3365 | 0.5 | 4110 | 0.2 | 4717 | 0.1 | 5463 | 0.05 | 6914 | 0.02 | 8370 | 0.01
Weber NH 355 A | We 355 A | 0.5 | 355 | FALSE | 701 | 1000 | 808 | 500 | 957 | 200 | 1108 | 100 | 1271 | 50 | 1546 | 20 | 1822 | 10 | 2110 | 5 | 2623 | 2 | 3092 | 1 | 3581 | 0.5 | 4394 | 0.2 | 5110 | 0.1 | 5971 | 0.05 | 7557 | 0.02 | 9027 | 0.01
Weber NH 400 A | We 400 A | 0.5 | 400 | FALSE | 776 | 1000 | 887 | 500 | 1045 | 200 | 1184 | 100 | 1383 | 50 | 1690 | 20 | 1992 | 10 | 2369 | 5 | 2867 | 2 | 3350 | 1 | 3828 | 0.5 | 4676 | 0.2 | 5414 | 0.1 | 6298 | 0.05 | 8150 | 0.02 | 9910 | 0.01
Weber NH 500 A | We 500 A | 0.5 | 500 | FALSE | 1050 | 1000 | 1195 | 500 | 1427 | 200 | 1667 | 100 | 1965 | 50 | 2545 | 20 | 2906 | 10 | 3456 | 5 | 4259 | 2 | 4910 | 1 | 5585 | 0.5 | 6702 | 0.2 | 7727 | 0.1 | 8947 | 0.05 | 11324 | 0.02 | 13709 | 0.01
Weber NH 630 A | We 630 A | 0.5 | 630 | FALSE | 1317 | 1000 | 1525 | 500 | 1830 | 200 | 2148 | 100 | 2532 | 50 | 3176 | 20 | 3794 | 10 | 4492 | 5 | 5536 | 2 | 6199 | 1 | 7228 | 0.5 | 8673 | 0.2 | 9825 | 0.1 | 11579 | 0.05 | 14590 | 0.02 | 17585 | 0.01
Weber NH 16 A gF | We 16 A gF | 0.5 | 16 | FALSE | 28 | 1000 | 30 | 500 | 33 | 200 | 35 | 100 | 38 | 50 | 41 | 20 | 44 | 10 | 48 | 5 | 54 | 2 | 59 | 1 | 66 | 0.5 | 77 | 0.2 | 90 | 0.1 | 106 | 0.05 | 141 | 0.02 | 182 | 0.01
Weber NH 20 A gF | We 20 A gF | 0.5 | 20 | FALSE | 36 | 1000 | 38 | 500 | 41 | 200 | 44 | 100 | 47 | 50 | 52 | 20 | 56 | 10 | 62 | 5 | 69 | 2 | 77 | 1 | 86 | 0.5 | 103 | 0.2 | 121 | 0.1 | 144 | 0.05 | 193 | 0.02 | 252 | 0.01
Weber NH 25 A gF | We 25 A gF | 0.5 | 25 | FALSE | 45 | 1000 | 48 | 500 | 52 | 200 | 56 | 100 | 60 | 50 | 67 | 20 | 72 | 10 | 79 | 5 | 90 | 2 | 100 | 1 | 112 | 0.5 | 133 | 0.2 | 155 | 0.1 | 186 | 0.05 | 245 | 0.02 | 315 | 0.01
Weber NH 35 A gF | We 35 A gF | 0.5 | 35 | FALSE | 57 | 1000 | 60 | 500 | 65 | 200 | 69 | 100 | 74 | 50 | 81 | 20 | 89 | 10 | 97 | 5 | 111 | 2 | 125 | 1 | 143 | 0.5 | 175 | 0.2 | 210 | 0.1 | 259 | 0.05 | 358 | 0.02 | 464 | 0.01
Weber NH 50 A gF | We 50 A gF | 0.5 | 50 | FALSE | 81 | 1000 | 87 | 500 | 94 | 200 | 101 | 100 | 109 | 50 | 121 | 20 | 130 | 10 | 143 | 5 | 163 | 2 | 183 | 1 | 206 | 0.5 | 247 | 0.2 | 291 | 0.1 | 349 | 0.05 | 456 | 0.02 | 578 | 0.01
Weber NH 63 A gF | We 63 A gF | 0.5 | 63 | FALSE | 102 | 1000 | 109 | 500 | 120 | 200 | 130 | 100 | 141 | 50 | 159 | 20 | 175 | 10 | 196 | 5 | 230 | 2 | 264 | 1 | 307 | 0.5 | 382 | 0.2 | 464 | 0.1 | 573 | 0.05 | 784 | 0.02 | 1011 | 0.01
Weber NH 80 A gF | We 80 A gF | 0.5 | 80 | FALSE | 145 | 1000 | 154 | 500 | 168 | 200 | 181 | 100 | 199 | 50 | 229 | 20 | 254 | 10 | 278 | 5 | 311 | 2 | 348 | 1 | 397 | 0.5 | 488 | 0.2 | 590 | 0.1 | 726 | 0.05 | 990 | 0.02 | 1293 | 0.01
Weber NH 100 A gF | We 100 A gF | 0.5 | 100 | FALSE | 188 | 1000 | 204 | 500 | 227 | 200 | 247 | 100 | 271 | 50 | 303 | 20 | 333 | 10 | 369 | 5 | 429 | 2 | 486 | 1 | 563 | 0.5 | 695 | 0.2 | 830 | 0.1 | 1007 | 0.05 | 1332 | 0.02 | 1674 | 0.01
Weber NH 125 A gF | We 125 A gF | 0.5 | 125 | FALSE | 237 | 1000 | 258 | 500 | 288 | 200 | 313 | 100 | 343 | 50 | 387 | 20 | 427 | 10 | 472 | 5 | 546 | 2 | 616 | 1 | 707 | 0.5 | 862 | 0.2 | 1025 | 0.1 | 1238 | 0.05 | 1653 | 0.02 | 2094 | 0.01
Weber NH 160 A gF | We 160 A gF | 0.5 | 160 | FALSE | 289 | 1000 | 315 | 500 | 349 | 200 | 382 | 100 | 418 | 50 | 474 | 20 | 523 | 10 | 585 | 5 | 689 | 2 | 784 | 1 | 916 | 0.5 | 1136 | 0.2 | 1385 | 0.1 | 1703 | 0.05 | 2342 | 0.02 | 3020 | 0.01
Weber NH 200 A gF | We 200 A gF | 0.5 | 200 | FALSE | 364 | 1000 | 392 | 500 | 435 | 200 | 472 | 100 | 519 | 50 | 585 | 20 | 652 | 10 | 735 | 5 | 862 | 2 | 994 | 1 | 1161 | 0.5 | 1446 | 0.2 | 1763 | 0.1 | 2168 | 0.05 | 2943 | 0.02 | 3762 | 0.01
Weber NH 224 A gF | We 224 A gF | 0.5 | 224 | FALSE | 408 | 1000 | 441 | 500 | 497 | 200 | 546 | 100 | 603 | 50 | 689 | 20 | 768 | 10 | 862 | 5 | 1011 | 2 | 1156 | 1 | 1338 | 0.5 | 1660 | 0.2 | 1989 | 0.1 | 2445 | 0.05 | 3291 | 0.02 | 4225 | 0.01
Weber NH 250 A gF | We 250 A gF | 0.5 | 250 | FALSE | 464 | 1000 | 501 | 500 | 558 | 200 | 611 | 100 | 672 | 50 | 768 | 20 | 851 | 10 | 960 | 5 | 1122 | 2 | 1282 | 1 | 1484 | 0.5 | 1840 | 0.2 | 2205 | 0.1 | 2688 | 0.05 | 3619 | 0.02 | 4605 | 0.01
Weber NH 315 A gF | We 315 A gF | 0.5 | 315 | FALSE | 575 | 1000 | 624 | 500 | 698 | 200 | 758 | 100 | 837 | 50 | 952 | 20 | 1060 | 10 | 1191 | 5 | 1403 | 2 | 1603 | 1 | 1856 | 0.5 | 2283 | 0.2 | 2735 | 0.1 | 3320 | 0.05 | 4411 | 0.02 | 5614 | 0.01
Weber NH 355 A gF | We 355 A gF | 0.5 | 355 | FALSE | 678 | 1000 | 745 | 500 | 848 | 200 | 932 | 100 | 1033 | 50 | 1191 | 20 | 1327 | 10 | 1490 | 5 | 1755 | 2 | 2006 | 1 | 2322 | 0.5 | 2855 | 0.2 | 3436 | 0.1 | 4171 | 0.05 | 5542 | 0.02 | 6993 | 0.01
Weber NH 400 A gF | We 400 A gF | 0.5 | 400 | FALSE | 764 | 1000 | 840 | 500 | 952 | 200 | 1051 | 100 | 1176 | 50 | 1356 | 20 | 1529 | 10 | 1733 | 5 | 2050 | 2 | 2342 | 1 | 2712 | 0.5 | 3306 | 0.2 | 3978 | 0.1 | 4829 | 0.05 | 6500 | 0.02 | 8308 | 0.01
Weber NH 500 A gF | We 500 A gF | 0.5 | 500 | FALSE | 948 | 1000 | 1033 | 500 | 1161 | 200 | 1271 | 100 | 1403 | 50 | 1597 | 20 | 1786 | 10 | 2006 | 5 | 2352 | 2 | 2688 | 1 | 3126 | 0.5 | 3893 | 0.2 | 4685 | 0.1 | 5737 | 0.05 | 7822 | 0.02 | 10085 | 0.01
Weber NH 630 A gF | We 630 A gF | 0.5 | 630 | FALSE | 1254 | 1000 | 1385 | 500 | 1576 | 200 | 1748 | 100 | 1946 | 50 | 2234 | 20 | 2477 | 10 | 2795 | 5 | 3277 | 2 | 3729 | 1 | 4317 | 0.5 | 5309 | 0.2 | 6334 | 0.1 | 7688 | 0.05 | 10216 | 0.02 | 12780 | 0.01
Weber NH 80 A gFF | We 80 A gFF | 0.5 | 80 | FALSE | 144 | 1000 | 153 | 500 | 169 | 200 | 182 | 100 | 196 | 50 | 223 | 20 | 244 | 10 | 265 | 5 | 304 | 2 | 342 | 1 | 386 | 0.5 | 474 | 0.2 | 551 | 0.1 | 664 | 0.05 | 884 | 0.02 | 1097 | 0.01
Weber NH 100 A gFF | We 100 A gFF | 0.5 | 100 | FALSE | 183 | 1000 | 197 | 500 | 222 | 200 | 240 | 100 | 265 | 50 | 296 | 20 | 329 | 10 | 355 | 5 | 405 | 2 | 461 | 1 | 519 | 0.5 | 618 | 0.2 | 714 | 0.1 | 864 | 0.05 | 1088 | 0.02 | 1394 | 0.01
Weber NH 125 A gFF | We 125 A gFF | 0.5 | 125 | FALSE | 228 | 1000 | 242 | 500 | 269 | 200 | 291 | 100 | 318 | 50 | 359 | 20 | 394 | 10 | 437 | 5 | 510 | 2 | 571 | 1 | 651 | 0.5 | 786 | 0.2 | 906 | 0.1 | 1080 | 0.05 | 1367 | 0.02 | 1633 | 0.01
Weber NH 160 A gFF | We 160 A gFF | 0.5 | 160 | FALSE | 290 | 1000 | 309 | 500 | 336 | 200 | 366 | 100 | 395 | 50 | 442 | 20 | 483 | 10 | 541 | 5 | 620 | 2 | 701 | 1 | 800 | 0.5 | 965 | 0.2 | 1158 | 0.1 | 1376 | 0.05 | 1793 | 0.02 | 2269 | 0.01
Weber NH 200 A gFF | We 200 A gFF | 0.5 | 200 | FALSE | 364 | 1000 | 386 | 500 | 423 | 200 | 455 | 100 | 492 | 50 | 548 | 20 | 596 | 10 | 660 | 5 | 761 | 2 | 855 | 1 | 976 | 0.5 | 1177 | 0.2 | 1369 | 0.1 | 1643 | 0.05 | 2196 | 0.02 | 2742 | 0.01
Weber NH 224 A gFF | We 224 A gFF | 0.5 | 224 | FALSE | 406 | 1000 | 435 | 500 | 476 | 200 | 508 | 100 | 550 | 50 | 615 | 20 | 673 | 10 | 743 | 5 | 852 | 2 | 956 | 1 | 1089 | 0.5 | 1340 | 0.2 | 1545 | 0.1 | 1858 | 0.05 | 2445 | 0.02 | 3016 | 0.01
Weber NH 250 A gFF | We 250 A gFF | 0.5 | 250 | FALSE | 445 | 1000 | 476 | 500 | 525 | 200 | 562 | 100 | 609 | 50 | 683 | 20 | 750 | 10 | 830 | 5 | 958 | 2 | 1094 | 1 | 1263 | 0.5 | 1547 | 0.2 | 1831 | 0.1 | 2185 | 0.05 | 2882 | 0.02 | 3565 | 0.01
Weber NH 315 A gFF | We 315 A gFF | 0.5 | 315 | FALSE | 557 | 1000 | 595 | 500 | 655 | 200 | 706 | 100 | 770 | 50 | 858 | 20 | 955 | 10 | 1053 | 5 | 1234 | 2 | 1396 | 1 | 1591 | 0.5 | 1942 | 0.2 | 2322 | 0.1 | 2803 | 0.05 | 3745 | 0.02 | 4682 | 0.01
Eaton NH 35 A gFF | Ea 35 A gFF | 0.4 | 35 | FALSE | 60 | 1000 | 65 | 500 | 71 | 200 | 76 | 100 | 81 | 50 | 89 | 20 | 95 | 10 | 103 | 5 | 119 | 2 | 139 | 1 | 163 | 0.5 | 206 | 0.2 | 253 | 0.1 | 311 | 0.05 | 406 | 0.02 | 499 | 0.01
Eaton NH 50 A gFF | Ea 50 A gFF | 0.4 | 50 | FALSE | 89 | 1000 | 95 | 500 | 104 | 200 | 112 | 100 | 119 | 50 | 133 | 20 | 141 | 10 | 153 | 5 | 173 | 2 | 191 | 1 | 211 | 0.5 | 245 | 0.2 | 281 | 0.1 | 354 | 0.05 | 520 | 0.02 | 730 | 0.01
Eaton NH 63 A gFF | Ea 63 A gFF | 0.4 | 63 | FALSE | 106 | 1000 | 111 | 500 | 121 | 200 | 130 | 100 | 140 | 50 | 155 | 20 | 165 | 10 | 180 | 5 | 202 | 2 | 227 | 1 | 255 | 0.5 | 314 | 0.2 | 382 | 0.1 | 503 | 0.05 | 751 | 0.02 | 1046 | 0.01
Eaton NH 80 A gFF | Ea 80 A gFF | 0.4 | 80 | FALSE | 141 | 1000 | 148 | 500 | 162 | 200 | 174 | 100 | 187 | 50 | 206 | 20 | 221 | 10 | 241 | 5 | 278 | 2 | 315 | 1 | 357 | 0.5 | 459 | 0.2 | 577 | 0.1 | 755 | 0.05 | 1123 | 0.02 | 1569 | 0.01
Eaton NH 100 A gFF | Ea 100 A gFF | 0.4 | 100 | FALSE | 172 | 1000 | 180 | 500 | 193 | 200 | 206 | 100 | 221 | 50 | 244 | 20 | 263 | 10 | 288 | 5 | 333 | 2 | 375 | 1 | 427 | 0.5 | 551 | 0.2 | 694 | 0.1 | 907 | 0.05 | 1355 | 0.02 | 1917 | 0.01
Eaton NH 125 A gFF | Ea 125 A gFF | 0.4 | 125 | FALSE | 221 | 1000 | 235 | 500 | 258 | 200 | 277 | 100 | 297 | 50 | 326 | 20 | 351 | 10 | 385 | 5 | 446 | 2 | 503 | 1 | 568 | 0.5 | 697 | 0.2 | 863 | 0.1 | 1127 | 0.05 | 1677 | 0.02 | 2343 | 0.01
Eaton NH 160 A gFF | Ea 160 A gFF | 0.4 | 160 | FALSE | 290 | 1000 | 311 | 500 | 341 | 200 | 366 | 100 | 393 | 50 | 433 | 20 | 468 | 10 | 509 | 5 | 590 | 2 | 668 | 1 | 764 | 0.5 | 970 | 0.2 | 1200 | 0.1 | 1562 | 0.05 | 2343 | 0.02 | 3247 | 0.01
Eaton NH 200 A gFF | Ea 200 A gFF | 0.4 | 200 | FALSE | 347 | 1000 | 374 | 500 | 415 | 200 | 447 | 100 | 482 | 50 | 529 | 20 | 570 | 10 | 617 | 5 | 697 | 2 | 793 | 1 | 911 | 0.5 | 1180 | 0.2 | 1467 | 0.1 | 1917 | 0.05 | 2864 | 0.02 | 3969 | 0.01
Eaton NH 224 A gFF | Ea 224 A gFF | 0.4 | 224 | FALSE | 390 | 1000 | 422 | 500 | 467 | 200 | 503 | 100 | 540 | 50 | 595 | 20 | 641 | 10 | 697 | 5 | 807 | 2 | 911 | 1 | 1037 | 0.5 | 1294 | 0.2 | 1602 | 0.1 | 2085 | 0.05 | 3114 | 0.02 | 4333 | 0.01
Eaton NH 250 A gFF | Ea 250 A gFF | 0.4 | 250 | FALSE | 418 | 1000 | 455 | 500 | 514 | 200 | 556 | 100 | 600 | 50 | 652 | 20 | 697 | 10 | 761 | 5 | 870 | 2 | 982 | 1 | 1127 | 0.5 | 1455 | 0.2 | 1816 | 0.1 | 2393 | 0.05 | 3650 | 0.02 | 5079 | 0.01
Eaton NH 315 A gFF | Ea 315 A gFF | 0.4 | 315 | FALSE | 551 | 1000 | 611 | 500 | 701 | 200 | 784 | 100 | 899 | 50 | 1078 | 20 | 1242 | 10 | 1446 | 5 | 1758 | 2 | 2046 | 1 | 2381 | 0.5 | 2868 | 0.2 | 3288 | 0.1 | 3698 | 0.05 | 4179 | 0.02 | 4564 | 0.01
Eaton NH 355 A gFF | Ea 355 A gFF | 0.4 | 355 | FALSE | 667 | 1000 | 740 | 500 | 852 | 200 | 958 | 100 | 1099 | 50 | 1324 | 20 | 1533 | 10 | 1828 | 5 | 2245 | 2 | 2575 | 1 | 2997 | 0.5 | 3644 | 0.2 | 4118 | 0.1 | 4564 | 0.05 | 5209 | 0.02 | 5744 | 0.01
Eaton NH 400 A gFF | Ea 400 A gFF | 0.4 | 400 | FALSE | 758 | 1000 | 844 | 500 | 973 | 200 | 1088 | 100 | 1273 | 50 | 1548 | 20 | 1802 | 10 | 2128 | 5 | 2626 | 2 | 3071 | 1 | 3609 | 0.5 | 4325 | 0.2 | 4864 | 0.1 | 5416 | 0.05 | 6181 | 0.02 | 6817 | 0.01
Eaton NH 450 A gFF | Ea 450 A gFF | 0.4 | 450 | FALSE | 834 | 1000 | 930 | 500 | 1079 | 200 | 1209 | 100 | 1369 | 50 | 1628 | 20 | 1852 | 10 | 2127 | 5 | 2594 | 2 | 3024 | 1 | 3457 | 0.5 | 4051 | 0.2 | 4540 | 0.1 | 5063 | 0.05 | 5817 | 0.02 | 6487 | 0.01
Eaton NH 500 A gFF | Ea 500 A gFF | 0.4 | 500 | FALSE | 935 | 1000 | 1053 | 500 | 1258 | 200 | 1453 | 100 | 1694 | 50 | 2075 | 20 | 2372 | 10 | 2712 | 5 | 3226 | 2 | 3687 | 1 | 4257 | 0.5 | 5063 | 0.2 | 5619 | 0.1 | 6266 | 0.05 | 7199 | 0.02 | 8028 | 0.01
Eaton NH 630 A gFF | Ea 630 A gFF | 0.4 | 630 | FALSE | 1335 | 1000 | 1526 | 500 | 1879 | 200 | 2213 | 100 | 2594 | 50 | 3162 | 20 | 3651 | 10 | 4236 | 5 | 5139 | 2 | 5904 | 1 | 6817 | 0.5 | 8108 | 0.2 | 8997 | 0.1 | 9983 | 0.05 | 11526 | 0.02 | 12854 | 0.01
HOLEC T 35 | HoT 35 A | 0.5 | 35 | FALSE | 60 | 1000 | 64 | 500 | 70 | 200 | 75 | 100 | 82 | 50 | 94 | 20 | 105 | 10 | 122 | 5 | 153 | 2 | 175 | 1 | 212 | 0.5 | 278 | 0.2 | 346 | 0.1 | 417 | 0.05 | 600 | 0.02 | 765 | 0.01
HOLEC T 50 | HoT 50 A | 0.5 | 50 | FALSE | 87 | 1000 | 93 | 500 | 105 | 200 | 114 | 100 | 126 | 50 | 146 | 20 | 163 | 10 | 187 | 5 | 227 | 2 | 262 | 1 | 315 | 0.5 | 410 | 0.2 | 503 | 0.1 | 600 | 0.05 | 845 | 0.02 | 1085 | 0.01
HOLEC T 63 | HoT 63 A | 0.5 | 63 | FALSE | 103 | 1000 | 110 | 500 | 123 | 200 | 135 | 100 | 149 | 50 | 174 | 20 | 196 | 10 | 215 | 5 | 263 | 2 | 313 | 1 | 381 | 0.5 | 505 | 0.2 | 615 | 0.1 | 770 | 0.05 | 1065 | 0.02 | 1345 | 0.01
HOLEC T 80 | HoT 80 A | 0.5 | 80 | FALSE | 153 | 1000 | 168 | 500 | 193 | 200 | 216 | 100 | 248 | 50 | 303 | 20 | 336 | 10 | 400 | 5 | 500 | 2 | 585 | 1 | 695 | 0.5 | 900 | 0.2 | 1025 | 0.1 | 1195 | 0.05 | 1525 | 0.02 | 1835 | 0.01
HOLEC T 100 | HoT 100 A | 0.5 | 100 | FALSE | 184 | 1000 | 202 | 500 | 238 | 200 | 270 | 100 | 313 | 50 | 381 | 20 | 420 | 10 | 495 | 5 | 620 | 2 | 740 | 1 | 885 | 0.5 | 1085 | 0.2 | 1235 | 0.1 | 1465 | 0.05 | 1890 | 0.02 | 2310 | 0.01
HOLEC T 125 | HoT 125 A | 0.5 | 125 | FALSE | 224 | 1000 | 248 | 500 | 290 | 200 | 330 | 100 | 388 | 50 | 482 | 20 | 539 | 10 | 640 | 5 | 795 | 2 | 945 | 1 | 1135 | 0.5 | 1400 | 0.2 | 1615 | 0.1 | 1925 | 0.05 | 2450 | 0.02 | 3045 | 0.01
HOLEC T 160 | HoT 160 A | 0.5 | 160 | FALSE | 302 | 1000 | 337 | 500 | 369 | 200 | 452 | 100 | 525 | 50 | 650 | 20 | 715 | 10 | 840 | 5 | 1010 | 2 | 1250 | 1 | 1450 | 0.5 | 1800 | 0.2 | 2200 | 0.1 | 2400 | 0.05 | 3050 | 0.02 | 3750 | 0.01
HOLEC T 200 | HoT 200 A | 0.5 | 200 | FALSE | 386 | 1000 | 428 | 500 | 499 | 200 | 565 | 100 | 665 | 50 | 830 | 20 | 910 | 10 | 1150 | 5 | 1400 | 2 | 1600 | 1 | 1900 | 0.5 | 2300 | 0.2 | 2750 | 0.1 | 3150 | 0.05 | 4000 | 0.02 | 4800 | 0.01
HOLEC T 225 | HoT 225 A | 0.5 | 225 | FALSE | 441 | 1000 | 490 | 500 | 575 | 200 | 650 | 100 | 745 | 50 | 920 | 20 | 1090 | 10 | 1290 | 5 | 1670 | 2 | 1970 | 1 | 2390 | 0.5 | 2890 | 0.2 | 3300 | 0.1 | 3860 | 0.05 | 5010 | 0.02 | 5960 | 0.01
HOLEC T 250 | HoT 250 A | 0.5 | 250 | FALSE | 486 | 1000 | 545 | 500 | 650 | 200 | 745 | 100 | 855 | 50 | 1075 | 20 | 1290 | 10 | 1540 | 5 | 1960 | 2 | 2310 | 1 | 2720 | 0.5 | 3280 | 0.2 | 3760 | 0.1 | 4420 | 0.05 | 5620 | 0.02 | 6770 | 0.01
HOLEC S 25 | HoS 25 A | 0.5 | 25 | FALSE | 40 | 1000 | 41 | 500 | 43 | 200 | 45 | 100 | 47 | 50 | 51 | 20 | 54 | 10 | 59 | 5 | 69 | 2 | 79 | 1 | 91 | 0.5 | 117 | 0.2 | 145 | 0.1 | 188 | 0.05 | 266 | 0.02 | 349 | 0.01
HOLEC S 35 | HoS 35 A | 0.5 | 35 | FALSE | 56 | 1000 | 57 | 500 | 60 | 200 | 61 | 100 | 63 | 50 | 68 | 20 | 73 | 10 | 82 | 5 | 94 | 2 | 106 | 1 | 126 | 0.5 | 167 | 0.2 | 207 | 0.1 | 262 | 0.05 | 371 | 0.02 | 486 | 0.01
HOLEC S 50 | HoS 50 A | 0.5 | 50 | FALSE | 88 | 1000 | 95 | 500 | 106 | 200 | 115 | 100 | 125 | 50 | 142 | 20 | 160 | 10 | 175 | 5 | 200 | 2 | 215 | 1 | 235 | 0.5 | 270 | 0.2 | 315 | 0.1 | 375 | 0.05 | 485 | 0.02 | 590 | 0.01
HOLEC S 63 | HoS 63 A | 0.5 | 63 | FALSE | 107 | 1000 | 117 | 500 | 133 | 200 | 146 | 100 | 161 | 50 | 183 | 20 | 198 | 10 | 230 | 5 | 260 | 2 | 290 | 1 | 325 | 0.5 | 380 | 0.2 | 435 | 0.1 | 525 | 0.05 | 680 | 0.02 | 870 | 0.01
HOLEC S 80 | HoS 80 A | 0.5 | 80 | FALSE | 150 | 1000 | 162 | 500 | 180 | 200 | 196 | 100 | 212 | 50 | 244 | 20 | 275 | 10 | 315 | 5 | 365 | 2 | 405 | 1 | 460 | 0.5 | 540 | 0.2 | 625 | 0.1 | 765 | 0.05 | 975 | 0.02 | 1230 | 0.01
HOLEC S 100 | HoS 100 A | 0.5 | 100 | FALSE | 179 | 1000 | 192 | 500 | 213 | 200 | 232 | 100 | 253 | 50 | 290 | 20 | 320 | 10 | 357 | 5 | 415 | 2 | 460 | 1 | 520 | 0.5 | 620 | 0.2 | 710 | 0.1 | 845 | 0.05 | 1075 | 0.02 | 1330 | 0.01
HOLEC S 125 | HoS 125 A | 0.5 | 125 | FALSE | 241 | 1000 | 262 | 500 | 297 | 200 | 328 | 100 | 365 | 50 | 427 | 20 | 490 | 10 | 555 | 5 | 645 | 2 | 720 | 1 | 810 | 0.5 | 935 | 0.2 | 1050 | 0.1 | 1250 | 0.05 | 1615 | 0.02 | 2095 | 0.01
HOLEC S 160 | HoS 160 A | 0.5 | 160 | FALSE | 293 | 1000 | 320 | 500 | 369 | 200 | 410 | 100 | 456 | 50 | 535 | 20 | 625 | 10 | 700 | 5 | 810 | 2 | 885 | 1 | 1005 | 0.5 | 1180 | 0.2 | 1380 | 0.1 | 1665 | 0.05 | 2155 | 0.02 | 2875 | 0.01
HOLEC S 200 | HoS 200 A | 0.5 | 200 | FALSE | 365 | 1000 | 401 | 500 | 465 | 200 | 515 | 100 | 575 | 50 | 685 | 20 | 755 | 10 | 845 | 5 | 975 | 2 | 1080 | 1 | 1250 | 0.5 | 1485 | 0.2 | 1740 | 0.1 | 2095 | 0.05 | 2795 | 0.02 | 3670 | 0.01
HOLEC S 225 | HoS 225 A | 0.5 | 225 | FALSE | 424 | 1000 | 476 | 500 | 550 | 200 | 620 | 100 | 705 | 50 | 850 | 20 | 965 | 10 | 1080 | 5 | 1265 | 2 | 1400 | 1 | 1615 | 0.5 | 1895 | 0.2 | 2185 | 0.1 | 2635 | 0.05 | 3465 | 0.02 | 4490 | 0.01
HOLEC S 250 | HoS 250 A | 0.5 | 250 | FALSE | 515 | 1000 | 545 | 500 | 635 | 200 | 715 | 100 | 820 | 50 | 990 | 20 | 1080 | 10 | 1215 | 5 | 1400 | 2 | 1550 | 1 | 1765 | 0.5 | 2095 | 0.2 | 2490 | 0.1 | 3045 | 0.05 | 4180 | 0.02 | 5415 | 0.01
SIBA 25 A gL/gG | Si 25 A | 0.5 | 25 | FALSE | 44 | 1000 | 46 | 500 | 50 | 200 | 54 | 100 | 60 | 50 | 68 | 20 | 75 | 10 | 88 | 5 | 109 | 2 | 128 | 1 | 154 | 0.5 | 195 | 0.2 | 236 | 0.1 | 290 | 0.05 | 383 | 0.02 | 481 | 0.01
SIBA 35 A gL/gG | Si 35 A | 0.5 | 35 | FALSE | 61 | 1000 | 64 | 500 | 70 | 200 | 75 | 100 | 82 | 50 | 92 | 20 | 105 | 10 | 123 | 5 | 150 | 2 | 176 | 1 | 213 | 0.5 | 273 | 0.2 | 330 | 0.1 | 404 | 0.05 | 547 | 0.02 | 685 | 0.01
SIBA 50 A gL/gG | Si 50 A | 0.5 | 50 | FALSE | 87 | 1000 | 95 | 500 | 108 | 200 | 118 | 100 | 131 | 50 | 146 | 20 | 168 | 10 | 194 | 5 | 234 | 2 | 273 | 1 | 320 | 0.5 | 400 | 0.2 | 475 | 0.1 | 567 | 0.05 | 756 | 0.02 | 943 | 0.01
SIBA 63 A gL/gG | Si 63 A | 0.5 | 63 | FALSE | 107 | 1000 | 116 | 500 | 132 | 200 | 148 | 100 | 171 | 50 | 203 | 20 | 231 | 10 | 269 | 5 | 327 | 2 | 380 | 1 | 443 | 0.5 | 549 | 0.2 | 644 | 0.1 | 772 | 0.05 | 1007 | 0.02 | 1232 | 0.01
SIBA 80 A gL/gG | Si 80 A | 0.5 | 80 | FALSE | 146 | 1000 | 157 | 500 | 174 | 200 | 189 | 100 | 216 | 50 | 253 | 20 | 295 | 10 | 346 | 5 | 421 | 2 | 498 | 1 | 578 | 0.5 | 708 | 0.2 | 831 | 0.1 | 987 | 0.05 | 1266 | 0.02 | 1538 | 0.01
SIBA 100 A gL/gG | Si 100 A | 0.5 | 100 | FALSE | 181 | 1000 | 199 | 500 | 227 | 200 | 252 | 100 | 290 | 50 | 355 | 20 | 403 | 10 | 477 | 5 | 589 | 2 | 688 | 1 | 807 | 0.5 | 987 | 0.2 | 1155 | 0.1 | 1369 | 0.05 | 1778 | 0.02 | 2216 | 0.01
SIBA 125 A gL/gG | Si 125 A | 0.5 | 125 | FALSE | 236 | 1000 | 260 | 500 | 296 | 200 | 330 | 100 | 373 | 50 | 441 | 20 | 525 | 10 | 617 | 5 | 761 | 2 | 902 | 1 | 1053 | 0.5 | 1344 | 0.2 | 1572 | 0.1 | 1846 | 0.05 | 2297 | 0.02 | 2730 | 0.01
SIBA 160 A gL/gG | Si 160 A | 0.5 | 160 | FALSE | 301 | 1000 | 330 | 500 | 377 | 200 | 418 | 100 | 480 | 50 | 585 | 20 | 698 | 10 | 840 | 5 | 1054 | 2 | 1264 | 1 | 1506 | 0.5 | 1831 | 0.2 | 2106 | 0.1 | 2443 | 0.05 | 3002 | 0.02 | 3576 | 0.01
SIBA 200 A gL/gG | Si 200 A | 0.5 | 200 | FALSE | 376 | 1000 | 411 | 500 | 473 | 200 | 525 | 100 | 595 | 50 | 710 | 20 | 858 | 10 | 1050 | 5 | 1342 | 2 | 1598 | 1 | 1924 | 0.5 | 2364 | 0.2 | 2708 | 0.1 | 3147 | 0.05 | 3883 | 0.02 | 4607 | 0.01
SIBA 224 A gL/gG | Si 224 A | 0.5 | 224 | FALSE | 420 | 1000 | 463 | 500 | 525 | 200 | 585 | 100 | 685 | 50 | 810 | 20 | 979 | 10 | 1193 | 5 | 1527 | 2 | 1858 | 1 | 2190 | 0.5 | 2680 | 0.2 | 3077 | 0.1 | 3598 | 0.05 | 4485 | 0.02 | 5421 | 0.01
SIBA 250 A gL/gG | Si 250 A | 0.5 | 250 | FALSE | 482 | 1000 | 530 | 500 | 615 | 200 | 695 | 100 | 810 | 50 | 990 | 20 | 1198 | 10 | 1460 | 5 | 1877 | 2 | 2268 | 1 | 2686 | 0.5 | 3300 | 0.2 | 3765 | 0.1 | 4367 | 0.05 | 5343 | 0.02 | 6392 | 0.01
SIBA 315 A gL/gG | Si 315 A | 0.5 | 315 | FALSE | 630 | 1000 | 715 | 500 | 845 | 200 | 960 | 100 | 1105 | 50 | 1325 | 20 | 1575 | 10 | 1908 | 5 | 2413 | 2 | 2928 | 1 | 3467 | 0.5 | 4269 | 0.2 | 4941 | 0.1 | 5707 | 0.05 | 6955 | 0.02 | 8218 | 0.01
SIBA 355 A gL/gG | Si 355 A | 0.5 | 355 | FALSE | 720 | 1000 | 810 | 500 | 955 | 200 | 1090 | 100 | 1280 | 50 | 1575 | 20 | 1908 | 10 | 2311 | 5 | 2959 | 2 | 3576 | 1 | 4251 | 0.5 | 5223 | 0.2 | 5960 | 0.1 | 6912 | 0.05 | 8475 | 0.02 | 9994 | 0.01
SIBA 630 A gL/gG | Si 630 A | 0.5 | 630 | FALSE | 1280 | 1000 | 1455 | 500 | 1725 | 200 | 1975 | 100 | 2290 | 50 | 2820 | 20 | 3250 | 10 | 3857 | 5 | 4909 | 2 | 5778 | 1 | 6875 | 0.5 | 8333 | 0.2 | 9500 | 0.1 | 11250 | 0.05 | 14000 | 0.02 | 16429 | 0.01
SIBA 1000 A gL/gG | Si 1000 A | 0.5 | 1000 | FALSE | 2105 | 1000 | 2365 | 500 | 2785 | 200 | 3160 | 100 | 3740 | 50 | 4625 | 20 | 5333 | 10 | 6400 | 5 | 8000 | 2 | 9667 | 1 | 11500 | 0.5 | 14000 | 0.2 | 16429 | 0.1 | 19286 | 0.05 | 25000 | 0.02 | 30000 | 0.01
SIBA 1600 A gL/gG | Si 1600 A | 0.5 | 1600 | FALSE | 3350 | 1000 | 3830 | 500 | 4720 | 200 | 5585 | 100 | 6690 | 50 | 8415 | 20 | 9550 | 10 | 11180 | 5 | 13980 | 2 | 16700 | 1 | 19480 | 0.5 | 24460 | 0.2 | 28750 | 0.1 | 34640 | 0.05 | 45150 | 0.02 | 56580 | 0.01
6 A T DII gG | WeD 6 A | 0.5 | 6 | FALSE | 12.1 | 1000 | 12.5 | 500 | 13.4 | 200 | 14.1 | 100 | 14.7 | 50 | 15.7 | 20 | 16.4 | 10 | 17.5 | 5 | 19.6 | 2 | 22 | 1 | 25.8 | 0.5 | 33.3 | 0.2 | 41 | 0.1 | 52 | 0.05 | 73 | 0.02 | 100 | 0.01
10 A T DII gG | WeD 10 A | 0.5 | 10 | FALSE | 20.6 | 1000 | 22.2 | 500 | 24.4 | 200 | 26.3 | 100 | 28.4 | 50 | 31.8 | 20 | 35 | 10 | 38.7 | 5 | 44.1 | 2 | 49.3 | 1 | 55.8 | 0.5 | 66.5 | 0.2 | 78 | 0.1 | 92 | 0.05 | 118 | 0.02 | 145 | 0.01
16 A T DII gG | WeD 16 A | 0.5 | 16 | FALSE | 28.7 | 1000 | 30.3 | 500 | 32.9 | 200 | 35 | 100 | 37.5 | 50 | 43 | 20 | 47 | 10 | 53 | 5 | 64 | 2 | 75 | 1 | 89 | 0.5 | 110 | 0.2 | 131 | 0.1 | 161 | 0.05 | 206 | 0.02 | 248 | 0.01
20 A T DII gG | WeD 20 A | 0.5 | 20 | FALSE | 37.1 | 1000 | 40 | 500 | 44 | 200 | 48 | 100 | 53 | 50 | 61 | 20 | 69 | 10 | 80 | 5 | 96 | 2 | 112 | 1 | 130 | 0.5 | 163 | 0.2 | 189 | 0.1 | 225 | 0.05 | 287 | 0.02 | 345 | 0.01
25 A T DII gG | WeD 25 A | 0.5 | 25 | FALSE | 47 | 1000 | 50 | 500 | 55 | 200 | 59 | 100 | 64 | 50 | 73 | 20 | 82 | 10 | 95 | 5 | 114 | 2 | 135 | 1 | 161 | 0.5 | 203 | 0.2 | 246 | 0.1 | 295 | 0.05 | 382 | 0.02 | 468 | 0.01
35 A T DIII gG | WeD 35 A | 0.5 | 35 | FALSE | 65 | 1000 | 71 | 500 | 80 | 200 | 87 | 100 | 97 | 50 | 112 | 20 | 127 | 10 | 147 | 5 | 179 | 2 | 213 | 1 | 254 | 0.5 | 314 | 0.2 | 361 | 0.1 | 445 | 0.05 | 557 | 0.02 | 694 | 0.01
50 A T DIII gG | WeD 50 A | 0.5 | 50 | FALSE | 92 | 1000 | 101 | 500 | 114 | 200 | 125 | 100 | 139 | 50 | 160 | 20 | 190 | 10 | 210 | 5 | 250 | 2 | 304 | 1 | 344 | 0.5 | 439 | 0.2 | 508 | 0.1 | 594 | 0.05 | 757 | 0.02 | 913 | 0.01
63 A T DIII gG | WeD 63 A | 0.5 | 63 | FALSE | 115 | 1000 | 126 | 500 | 141 | 200 | 156 | 100 | 176 | 50 | 205 | 20 | 233 | 10 | 273 | 5 | 325 | 2 | 375 | 1 | 425 | 0.5 | 520 | 0.2 | 623 | 0.1 | 731 | 0.05 | 936 | 0.02 | 1112 | 0.01
50 kVA | 50 kVA | 0.5 | 69 | FALSE | 129 | 1000 | 138 | 500 | 155 | 200 | 170 | 100 | 189 | 50 | 222 | 20 | 256 | 10 | 297 | 5 | 359 | 2 | 408 | 1 | 459 | 0.5 | 524 | 0.2 | 585 | 0.1 | 665 | 0.05 | 832 | 0.02 | 1021 | 0.01
100 kVA | 100 kVA | 0.5 | 137 | FALSE | 252 | 1000 | 275 | 500 | 314 | 200 | 350 | 100 | 398 | 50 | 473 | 20 | 545 | 10 | 637 | 5 | 776 | 2 | 874 | 1 | 987 | 0.5 | 1140 | 0.2 | 1279 | 0.1 | 1464 | 0.05 | 1841 | 0.02 | 2278 | 0.01
160 kVA | 160 kVA | 0.5 | 220 | FALSE | 439 | 1000 | 482 | 500 | 559 | 200 | 631 | 100 | 726 | 50 | 873 | 20 | 1021 | 10 | 1178 | 5 | 1446 | 2 | 1642 | 1 | 1864 | 0.5 | 2178 | 0.2 | 2442 | 0.1 | 2796 | 0.05 | 3488 | 0.02 | 4281 | 0.01
250 kVA | 250 kVA | 0.5 | 344 | FALSE | 683 | 1000 | 760 | 500 | 895 | 200 | 1012 | 100 | 1168 | 50 | 1428 | 20 | 1669 | 10 | 1938 | 5 | 2373 | 2 | 2706 | 1 | 3085 | 0.5 | 3634 | 0.2 | 4092 | 0.1 | 4743 | 0.05 | 6015 | 0.02 | 7400 | 0.01
315 kVA | 315 kVA | 0.5 | 455 | FALSE | 865 | 1000 | 956 | 500 | 1140 | 200 | 1310 | 100 | 1500 | 50 | 1840 | 20 | 2240 | 10 | 2530 | 5 | 3070 | 2 | 3530 | 1 | 4010 | 0.5 | 4740 | 0.2 | 5400 | 0.1 | 6230 | 0.05 | 7800 | 0.02 | 9640 | 0.01
400 kVA | 400 kVA | 0.5 | 550 | FALSE | 1085 | 1000 | 1219 | 500 | 1440 | 200 | 1655 | 100 | 1926 | 50 | 2344 | 20 | 2762 | 10 | 3214 | 5 | 3960 | 2 | 4552 | 1 | 5190 | 0.5 | 5893 | 0.2 | 7028 | 0.1 | 8178 | 0.05 | 10204 | 0.02 | 12600 | 0.01
630 kVA | 630 kVA | 0.5 | 866 | FALSE | 1703 | 1000 | 1934 | 500 | 2325 | 200 | 2683 | 100 | 3149 | 50 | 3888 | 20 | 4590 | 10 | 5341 | 5 | 6582 | 2 | 7535 | 1 | 8732 | 0.5 | 10436 | 0.2 | 11922 | 0.1 | 13845 | 0.05 | 17309 | 0.02 | 21245 | 0.01
800 kVA | 800 kVA | 0.5 | 1100 | FALSE | 2232 | 1000 | 2534 | 500 | 3060 | 200 | 3560 | 100 | 4194 | 50 | 5211 | 20 | 6165 | 10 | 7203 | 5 | 8877 | 2 | 10245 | 1 | 11874 | 0.5 | 14336 | 0.2 | 16479 | 0.1 | 19098 | 0.05 | 23730 | 0.02 | 29124 | 0.01
1000 kVA | 1000 kVA | 0.5 | 1375 | FALSE | 2762 | 1000 | 3161 | 500 | 3864 | 200 | 4525 | 100 | 5363 | 50 | 6662 | 20 | 7915 | 10 | 9286 | 5 | 11444 | 2 | 13208 | 1 | 15370 | 0.5 | 18482 | 0.2 | 21245 | 0.1 | 24621 | 0.05 | 30718 | 0.02 | 38011 | 0.01
Bussmann (10 kV) 16 A | Bu 16 A | 12 | 16 | FALSE | 31 | 1000 | 33 | 500 | 34.5 | 200 | 40 | 100 | 45 | 50 | 53 | 20 | 60 | 10 | 70 | 5 | 90 | 2 | 110 | 1 | 130 | 0.5 | 170 | 0.2 | 205 | 0.1 | 255 | 0.05 | 345 | 0.02 | 440 | 0.01
Bussmann (10 kV) 31,5 A | Bu 31,5 A | 12 | 31.5 | FALSE | 51 | 1000 | 55 | 500 | 62 | 200 | 68 | 100 | 76 | 50 | 92 | 20 | 120 | 10 | 130 | 5 | 175 | 2 | 220 | 1 | 275 | 0.5 | 380 | 0.2 | 440 | 0.1 | 540 | 0.05 | 725 | 0.02 | 925 | 0.01
Bussmann (10 kV) 50 A | Bu 50 A | 12 | 50 | FALSE | 106 | 1000 | 114 | 500 | 128 | 200 | 140 | 100 | 152 | 50 | 175 | 20 | 200 | 10 | 230 | 5 | 305 | 2 | 400 | 1 | 520 | 0.5 | 625 | 0.2 | 740 | 0.1 | 875 | 0.05 | 1150 | 0.02 | 1400 | 0.01
Bussmann (10 kV) 63 A | Bu 63 A | 12 | 63 | FALSE | 118 | 1000 | 128 | 500 | 140 | 200 | 150 | 100 | 168 | 50 | 192 | 20 | 220 | 10 | 265 | 5 | 346 | 2 | 440 | 1 | 580 | 0.5 | 710 | 0.2 | 840 | 0.1 | 1000 | 0.05 | 1270 | 0.02 | 1550 | 0.01
Bussmann (10 kV) 80 A | Bu 80 A | 12 | 80 | FALSE | 145 | 1000 | 165 | 500 | 175 | 200 | 185 | 100 | 200 | 50 | 230 | 20 | 270 | 10 | 345 | 5 | 410 | 2 | 480 | 1 | 585 | 0.5 | 790 | 0.2 | 1000 | 0.1 | 1275 | 0.05 | 1800 | 0.02 | 2300 | 0.01
Bussmann (10 kV) 100 A | Bu 100 A | 12 | 100 | FALSE | 200 | 1000 | 218 | 500 | 240 | 200 | 255 | 100 | 275 | 50 | 315 | 20 | 370 | 10 | 450 | 5 | 570 | 2 | 675 | 1 | 810 | 0.5 | 1100 | 0.2 | 1400 | 0.1 | 1775 | 0.05 | 2500 | 0.02 | 3200 | 0.01
Bussmann (20 kV) 10 A | Bu 10 A | 24 | 10 | FALSE | 17.5 | 1000 | 18.6 | 500 | 20.2 | 200 | 21.8 | 100 | 23 | 50 | 25.5 | 20 | 28 | 10 | 32 | 5 | 40 | 2 | 48 | 1 | 60 | 0.5 | 84 | 0.2 | 103 | 0.1 | 125 | 0.05 | 160 | 0.02 | 205 | 0.01
Bussmann (20 kV) 16 A | Bu 16 A | 24 | 16 | FALSE | 28 | 1000 | 30 | 500 | 33.4 | 200 | 36 | 100 | 39 | 50 | 42 | 20 | 50 | 10 | 58 | 5 | 76 | 2 | 96 | 1 | 122 | 0.5 | 165 | 0.2 | 200 | 0.1 | 245 | 0.05 | 320 | 0.02 | 400 | 0.01
Bussmann (20 kV) 25 A | Bu 25 A | 24 | 25 | FALSE | 49 | 1000 | 53 | 500 | 58 | 200 | 61 | 100 | 66 | 50 | 75 | 20 | 90 | 10 | 110 | 5 | 148 | 2 | 190 | 1 | 240 | 0.5 | 325 | 0.2 | 400 | 0.1 | 500 | 0.05 | 650 | 0.02 | 850 | 0.01
Bussmann (20 kV) 31,5 A | Bu 31,5 A | 24 | 31.5 | FALSE | 59.5 | 1000 | 64 | 500 | 70 | 200 | 75 | 100 | 82 | 50 | 95 | 20 | 110 | 10 | 132 | 5 | 180 | 2 | 230 | 1 | 300 | 0.5 | 390 | 0.2 | 480 | 0.1 | 600 | 0.05 | 800 | 0.02 | 1040 | 0.01
Bussmann (20 kV) 45 A | Bu 45 A | 24 | 45 | FALSE | 85 | 1000 | 93 | 500 | 102 | 200 | 110 | 100 | 120 | 50 | 138 | 20 | 160 | 10 | 190 | 5 | 265 | 2 | 340 | 1 | 440 | 0.5 | 590 | 0.2 | 725 | 0.1 | 875 | 0.05 | 1150 | 0.02 | 1450 | 0.01
Siba (10 kV) 16 A | Si 16 A | 12 | 16 | FALSE | 36.4 | 1000 | 39 | 500 | 42.9 | 200 | 46.3 | 100 | 51 | 50 | 56.3 | 20 | 61.6 | 10 | 67.8 | 5 | 78.9 | 2 | 90.5 | 1 | 104 | 0.5 | 126 | 0.2 | 148 | 0.1 | 182 | 0.05 | 239 | 0.02 | 297 | 0.01
Siba (10 kV) 25 A | Si 25 A | 12 | 25 | FALSE | 52.8 | 1000 | 56.4 | 500 | 62.2 | 200 | 67.8 | 100 | 74.5 | 50 | 83.8 | 20 | 92.9 | 10 | 106 | 5 | 121 | 2 | 139 | 1 | 162 | 0.5 | 198 | 0.2 | 234 | 0.1 | 289 | 0.05 | 382 | 0.02 | 478 | 0.01
Siba (10 kV) 31,5 A | Si 31,5 A | 12 | 31.5 | FALSE | 66.9 | 1000 | 71.7 | 500 | 78.9 | 200 | 86 | 100 | 93.7 | 50 | 105 | 20 | 116 | 10 | 128 | 5 | 150 | 2 | 173 | 1 | 201 | 0.5 | 245 | 0.2 | 289 | 0.1 | 355 | 0.05 | 470 | 0.02 | 593 | 0.01
Siba (10 kV) 50 A | Si 50 A | 12 | 50 | FALSE | 104 | 1000 | 111 | 500 | 122 | 200 | 132 | 100 | 144 | 50 | 162 | 20 | 178 | 10 | 199 | 5 | 235 | 2 | 272 | 1 | 318 | 0.5 | 393 | 0.2 | 468 | 0.1 | 575 | 0.05 | 762 | 0.02 | 954 | 0.01
Siba (10 kV) 63 A | Si 63 A | 12 | 63 | FALSE | 127 | 1000 | 136 | 500 | 149 | 200 | 161 | 100 | 175 | 50 | 197 | 20 | 219 | 10 | 245 | 5 | 291 | 2 | 337 | 1 | 393 | 0.5 | 488 | 0.2 | 580 | 0.1 | 720 | 0.05 | 954 | 0.02 | 1199 | 0.01
Siba (10 kV) 80 A | Si 80 A | 12 | 80 | FALSE | 161 | 1000 | 173 | 500 | 189 | 200 | 206 | 100 | 224 | 50 | 253 | 20 | 282 | 10 | 318 | 5 | 378 | 2 | 440 | 1 | 525 | 0.5 | 661 | 0.2 | 795 | 0.1 | 983 | 0.05 | 1302 | 0.02 | 1615 | 0.01
Siba (10 kV) 100 A | Si 100 A | 12 | 100 | FALSE | 199 | 1000 | 213 | 500 | 236 | 200 | 257 | 100 | 280 | 50 | 316 | 20 | 351 | 10 | 403 | 5 | 488 | 2 | 567 | 1 | 672 | 0.5 | 850 | 0.2 | 1030 | 0.1 | 1303 | 0.05 | 1720 | 0.02 | 2139 | 0.01
Siba (20 kV) 10 A | Si 10 A | 24 | 10 | FALSE | 30 | 1000 | 30.9 | 500 | 32.2 | 200 | 33.7 | 100 | 35.8 | 50 | 37.5 | 20 | 39.7 | 10 | 43.8 | 5 | 51.6 | 2 | 60.1 | 1 | 71.4 | 0.5 | 91.7 | 0.2 | 112 | 0.1 | 141 | 0.05 | 189 | 0.02 | 241 | 0.01
Siba (20 kV) 16 A | Si 16 A | 24 | 16 | FALSE | 36.4 | 1000 | 39 | 500 | 42.9 | 200 | 46.3 | 100 | 51 | 50 | 56.3 | 20 | 61.6 | 10 | 67.8 | 5 | 78.9 | 2 | 90.5 | 1 | 104 | 0.5 | 126 | 0.2 | 148 | 0.1 | 182 | 0.05 | 239 | 0.02 | 297 | 0.01
Siba (20 kV) 25 A | Si 25 A | 24 | 25 | FALSE | 52.8 | 1000 | 56.4 | 500 | 62.2 | 200 | 67.8 | 100 | 74.5 | 50 | 83.8 | 20 | 92.9 | 10 | 106 | 5 | 121 | 2 | 139 | 1 | 162 | 0.5 | 198 | 0.2 | 234 | 0.1 | 289 | 0.05 | 382 | 0.02 | 478 | 0.01
Siba (20 kV) 31,5 A | Si 31,5 A | 24 | 31.5 | FALSE | 66.9 | 1000 | 71.7 | 500 | 78.9 | 200 | 86 | 100 | 93.7 | 50 | 105 | 20 | 116 | 10 | 128 | 5 | 150 | 2 | 173 | 1 | 201 | 0.5 | 245 | 0.2 | 289 | 0.1 | 355 | 0.05 | 470 | 0.02 | 593 | 0.01
Siba (20 kV) 50 A | Si 50 A | 24 | 50 | FALSE | 104 | 1000 | 111 | 500 | 122 | 200 | 132 | 100 | 144 | 50 | 162 | 20 | 178 | 10 | 199 | 5 | 235 | 2 | 272 | 1 | 318 | 0.5 | 393 | 0.2 | 468 | 0.1 | 575 | 0.05 | 762 | 0.02 | 954 | 0.01
HOLEC Flran 6,3 A | Ho 6,3 A | 10 | 6.3 | FALSE | 17.8 | 1000 | 21.2 | 500 | 25.6 | 200 | 29.4 | 100 | 32.8 | 50 | 37.1 | 20 | 40 | 10 | 43 | 5 | 47 | 2 | 49 | 1 | 51 | 0.5 | 53 | 0.2 | 54 | 0.1 | 55 | 0.05 | 57 | 0.02 | 60 | 0.01
HOLEC Flran 8 A | Ho 8 A | 10 | 8 | FALSE | 22.6 | 1000 | 26.7 | 500 | 32 | 200 | 37.1 | 100 | 42.2 | 50 | 47.6 | 20 | 52 | 10 | 57 | 5 | 60 | 2 | 63 | 1 | 66 | 0.5 | 69 | 0.2 | 70 | 0.1 | 73 | 0.05 | 76 | 0.02 | 80 | 0.01
HOLEC Flran 10 A | Ho 10 A | 10 | 10 | FALSE | 27.6 | 1000 | 32.7 | 500 | 39.2 | 200 | 44.2 | 100 | 49.7 | 50 | 56.6 | 20 | 63 | 10 | 69 | 5 | 73 | 2 | 77 | 1 | 80 | 0.5 | 83 | 0.2 | 86 | 0.1 | 88 | 0.05 | 90 | 0.02 | 98 | 0.01
HOLEC Flran 12,5 A | Ho 12,5 A | 10 | 12.5 | FALSE | 33.1 | 1000 | 39.6 | 500 | 47.8 | 200 | 54.1 | 100 | 60.9 | 50 | 70.4 | 20 | 80 | 10 | 86 | 5 | 90 | 2 | 95 | 1 | 98 | 0.5 | 100 | 0.2 | 102 | 0.1 | 110 | 0.05 | 125 | 0.02 | 140 | 0.01
HOLEC Flran 16 A | Ho 16 A | 10 | 16 | FALSE | 39.4 | 1000 | 47.8 | 500 | 57.4 | 200 | 67 | 100 | 79.2 | 50 | 93 | 20 | 105 | 10 | 120 | 5 | 135 | 2 | 138 | 1 | 144 | 0.5 | 144 | 0.2 | 145 | 0.1 | 146 | 0.05 | 149 | 0.02 | 157 | 0.01
HOLEC Flran 20 A | Ho 20 A | 10 | 20 | FALSE | 48.5 | 1000 | 58 | 500 | 71.2 | 200 | 84.9 | 100 | 103 | 50 | 124 | 20 | 140 | 10 | 150 | 5 | 168 | 2 | 178 | 1 | 182 | 0.5 | 182 | 0.2 | 186 | 0.1 | 186 | 0.05 | 193 | 0.02 | 208 | 0.01
HOLEC Flran 25 A | Ho 25 A | 10 | 25 | FALSE | 59.5 | 1000 | 70.4 | 500 | 87.1 | 200 | 104 | 100 | 125 | 50 | 152 | 20 | 175 | 10 | 200 | 5 | 225 | 2 | 240 | 1 | 247 | 0.5 | 250 | 0.2 | 250 | 0.1 | 256 | 0.05 | 275 | 0.02 | 300 | 0.01
HOLEC Flran 31,5 A | Ho 31,5 A | 10 | 31.5 | FALSE | 72.5 | 1000 | 86.2 | 500 | 108 | 200 | 129 | 100 | 154 | 50 | 189 | 20 | 222 | 10 | 250 | 5 | 275 | 2 | 294 | 1 | 300 | 0.5 | 320 | 0.2 | 330 | 0.1 | 340 | 0.05 | 367 | 0.02 | 425 | 0.01
HOLEC Flran 40 A | Ho 40 A | 10 | 40 | FALSE | 93.3 | 1000 | 112 | 500 | 138 | 200 | 166 | 100 | 199 | 50 | 240 | 20 | 275 | 10 | 320 | 5 | 350 | 2 | 383 | 1 | 400 | 0.5 | 418 | 0.2 | 427 | 0.1 | 450 | 0.05 | 500 | 0.02 | 570 | 0.01
HOLEC Flran 50 A | Ho 50 A | 10 | 50 | FALSE | 104 | 1000 | 131 | 500 | 172 | 200 | 217 | 100 | 276 | 50 | 343 | 20 | 383 | 10 | 413 | 5 | 450 | 2 | 480 | 1 | 500 | 0.5 | 525 | 0.2 | 567 | 0.1 | 633 | 0.05 | 750 | 0.02 | 850 | 0.01
HOLEC Flran 63 A | Ho 63 A | 10 | 63 | FALSE | 133 | 1000 | 164 | 500 | 221 | 200 | 278 | 100 | 355 | 50 | 455 | 20 | 525 | 10 | 575 | 5 | 616 | 2 | 644 | 1 | 666 | 0.5 | 710 | 0.2 | 775 | 0.1 | 845 | 0.05 | 975 | 0.02 | 1188 | 0.01
HOLEC Flran 80 A | Ho 80 A | 10 | 80 | FALSE | 175 | 1000 | 214 | 500 | 283 | 200 | 353 | 100 | 453 | 50 | 576 | 20 | 670 | 10 | 740 | 5 | 800 | 2 | 840 | 1 | 865 | 0.5 | 900 | 0.2 | 980 | 0.1 | 1095 | 0.05 | 1313 | 0.02 | 1500 | 0.01
HOLEC 3 kV Ma 10 A | Ma 10 A | 3 | 10 | FALSE | 18.2 | 1000 | 19.6 | 500 | 22.2 | 200 | 25.1 | 100 | 29.3 | 50 | 37.1 | 20 | 42 | 10 | 52 | 5 | 64 | 2 | 71 | 1 | 80 | 0.5 | 90 | 0.2 | 99 | 0.1 | 110 | 0.05 | 135 | 0.02 | 150 | 0.01
HOLEC 3 kV Mg 10 A | Mg 10 A | 3 | 10 | FALSE | 25.3 | 1000 | 27.5 | 500 | 31.1 | 200 | 34.2 | 100 | 37.7 | 50 | 43.2 | 20 | 48 | 10 | 55 | 5 | 63 | 2 | 70 | 1 | 77 | 0.5 | 88 | 0.2 | 100 | 0.1 | 116 | 0.05 | 138 | 0.02 | 157 | 0.01
HOLEC 3 kV Mg 20 A | Mg 20 A | 3 | 20 | FALSE | 39 | 1000 | 43.4 | 500 | 50 | 200 | 54.6 | 100 | 61.8 | 50 | 72.6 | 20 | 82 | 10 | 93 | 5 | 114 | 2 | 128 | 1 | 147 | 0.5 | 181 | 0.2 | 214 | 0.1 | 248 | 0.05 | 298 | 0.02 | 350 | 0.01
HOLEC 3 kV Mg 40 A | Mg 40 A | 3 | 40 | FALSE | 67.9 | 1000 | 75.7 | 500 | 90 | 200 | 100 | 100 | 116 | 50 | 138 | 20 | 163 | 10 | 188 | 5 | 221 | 2 | 250 | 1 | 283 | 0.5 | 338 | 0.2 | 398 | 0.1 | 457 | 0.05 | 558 | 0.02 | 640 | 0.01
HOLEC 3 kV Mg 60 A | Mg 60 A | 3 | 60 | FALSE | 98.8 | 1000 | 108 | 500 | 127 | 200 | 143 | 100 | 168 | 50 | 201 | 20 | 240 | 10 | 270 | 5 | 350 | 2 | 400 | 1 | 498 | 0.5 | 600 | 0.2 | 700 | 0.1 | 750 | 0.05 | 1100 | 0.02 | 1225 | 0.01
HOLEC 3 kV Mg 80 A | Mg 80 A | 3 | 80 | FALSE | 149 | 1000 | 171 | 500 | 207 | 200 | 236 | 100 | 284 | 50 | 348 | 20 | 420 | 10 | 495 | 5 | 610 | 2 | 700 | 1 | 747 | 0.5 | 1050 | 0.2 | 1275 | 0.1 | 1500 | 0.05 | 1928 | 0.02 | 2250 | 0.01

## Switch
Name | Shortname | Unom | Inom | Ik_make | Ik_dynamic | Ik_thermic | T_thermic
|  | kV | A | kA | kA | kA | s
Voorbeeld 200 A | ls 200 A | 10 | 200 | 12 | 25 | 16 | 1

## Breaker
Name | Shortname | Unom | Inom | Switchtime | Ik_make | Ik_break | Ik_dynamic | Ik_thermic | T_thermic
|  | kV | A | s | kA | kA | kA | kA | s
Voorbeeld 300 A | vs 300 A | 10 | 300 | 0.06 | 15 | 10 | 30 | 20 | 1

## Current
Name | Shortname | Setting | Inom | I1 | t1 | I2 | t2 | I3 | t3 | I4 | t4 | I5 | t5 | I6 | t6 | I7 | t7 | I8 | t8 | I9 | t9 | I10 | t10 | I11 | t11 | I12 | t12 | I13 | t13 | I14 | t14 | I15 | t15 | I16 | t16
|  |  | A | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s | A | s
Voorbeeld curve 200 A | Voorbeeld | 0 | 200 | 711 | 10 | 800 | 5 | 930 | 2 | 1031 | 1 | 1200 | 0.5 | 1406 | 0.2 | 1625 | 0.1 | 2000 | 0.05 | 2612 | 0.02 | 3488 | 0.01
Aardlek 30 mA | Aardlek 30 mA | 0 | 0.03 | 0.03 | 1000 | 0.03 | 500 | 0.03 | 200 | 0.03 | 100 | 0.03 | 50 | 0.03 | 20 | 0.03 | 10 | 0.03 | 5 | 0.03 | 2 | 0.03 | 1 | 0.03 | 0.5 | 0.05 | 0.2 | 0.09 | 0.1 | 0.13 | 0.05 | 0.25 | 0.02 | 0.75 | 0.01
Aardlek 300 mA | Aardlek 300 mA | 0 | 0.3 | 0.3 | 1000 | 0.3 | 500 | 0.3 | 200 | 0.3 | 100 | 0.3 | 50 | 0.3 | 20 | 0.3 | 10 | 0.3 | 5 | 0.3 | 2 | 0.3 | 1 | 0.3 | 0.5 | 0.6 | 0.2 | 0.9 | 0.1 | 1.3 | 0.05 | 3 | 0.02 | 9 | 0.01
B-6 aut IEC 898 | Baut 6 A | 0 | 6 | 9.4 | 1000 | 10 | 500 | 11.6 | 200 | 13.5 | 100 | 16.8 | 50 | 26.3 | 20 | 30 | 10 | 30 | 5 | 30 | 2 | 30 | 1 | 30 | 0.5 | 30 | 0.2 | 30 | 0.1 | 36.3 | 0.05 | 120 | 0.02 | 3000 | 0.01
B-10 aut IEC 898 | Baut 10 A | 0 | 10 | 15.6 | 1000 | 16.7 | 500 | 19.3 | 200 | 22.5 | 100 | 28 | 50 | 43.8 | 20 | 50 | 10 | 50 | 5 | 50 | 2 | 50 | 1 | 50 | 0.5 | 50 | 0.2 | 50 | 0.1 | 60.5 | 0.05 | 200 | 0.02 | 5000 | 0.01
B-16 aut IEC 898 | Baut 16 A | 0 | 16 | 25 | 1000 | 26.7 | 500 | 30.9 | 200 | 36 | 100 | 44.8 | 50 | 70 | 20 | 80 | 10 | 80 | 5 | 80 | 2 | 80 | 1 | 80 | 0.5 | 80 | 0.2 | 80 | 0.1 | 97 | 0.05 | 320 | 0.02 | 8000 | 0.01
B-20 aut IEC 898 | Baut 20 A | 0 | 20 | 31.2 | 1000 | 33.4 | 500 | 38.6 | 200 | 45 | 100 | 56 | 50 | 88 | 20 | 100 | 10 | 100 | 5 | 100 | 2 | 100 | 1 | 100 | 0.5 | 100 | 0.2 | 100 | 0.1 | 121 | 0.05 | 400 | 0.02 | 10000 | 0.01
B-25 aut IEC 898 | Baut 25 A | 0 | 25 | 39 | 1000 | 42 | 500 | 48 | 200 | 56 | 100 | 70 | 50 | 110 | 20 | 125 | 10 | 125 | 5 | 125 | 2 | 125 | 1 | 125 | 0.5 | 125 | 0.2 | 125 | 0.1 | 151 | 0.05 | 500 | 0.02 | 12500 | 0.01
B-32 aut IEC 898 | Baut 32 A | 0 | 32 | 50 | 1000 | 53 | 500 | 62 | 200 | 72 | 100 | 90 | 50 | 140 | 20 | 160 | 10 | 160 | 5 | 160 | 2 | 160 | 1 | 160 | 0.5 | 160 | 0.2 | 160 | 0.1 | 193 | 0.05 | 640 | 0.02 | 16000 | 0.01
B-40 aut IEC 898 | Baut 40 A | 0 | 40 | 62 | 1000 | 67 | 500 | 77 | 200 | 90 | 100 | 112 | 50 | 175 | 20 | 200 | 10 | 200 | 5 | 200 | 2 | 200 | 1 | 200 | 0.5 | 200 | 0.2 | 200 | 0.1 | 242 | 0.05 | 800 | 0.02 | 20000 | 0.01
B-50 aut IEC 947 | Baut 50 A | 0 | 50 | 71 | 1000 | 76 | 500 | 86 | 200 | 102 | 100 | 123 | 50 | 192 | 20 | 250 | 10 | 250 | 5 | 250 | 2 | 250 | 1 | 250 | 0.5 | 250 | 0.2 | 250 | 0.1 | 302 | 0.05 | 1000 | 0.02 | 25000 | 0.01
B-63 aut IEC 947 | Baut 63 A | 0 | 63 | 89 | 1000 | 95 | 500 | 108 | 200 | 128 | 100 | 154 | 50 | 242 | 20 | 315 | 10 | 315 | 5 | 315 | 2 | 315 | 1 | 315 | 0.5 | 315 | 0.2 | 315 | 0.1 | 381 | 0.05 | 1260 | 0.02 | 31500 | 0.01
B-80 aut IEC 947 | Baut 80 A | 0 | 80 | 113 | 1000 | 121 | 500 | 138 | 200 | 162 | 100 | 196 | 50 | 307 | 20 | 400 | 10 | 400 | 5 | 400 | 2 | 400 | 1 | 400 | 0.5 | 400 | 0.2 | 400 | 0.1 | 484 | 0.05 | 1600 | 0.02 | 40000 | 0.01
C-16 aut IEC 898 | Caut 16 A | 0 | 16 | 25 | 1000 | 26.7 | 500 | 30.9 | 200 | 36 | 100 | 44.8 | 50 | 70 | 20 | 123 | 10 | 160 | 5 | 160 | 2 | 160 | 1 | 160 | 0.5 | 160 | 0.2 | 160 | 0.1 | 170 | 0.05 | 406 | 0.02 | 8000 | 0.01
C-20 aut IEC 898 | Caut 20 A | 0 | 20 | 31.2 | 1000 | 33.4 | 500 | 38.6 | 200 | 45 | 100 | 56 | 50 | 88 | 20 | 154 | 10 | 200 | 5 | 200 | 2 | 200 | 1 | 200 | 0.5 | 200 | 0.2 | 200 | 0.1 | 212 | 0.05 | 508 | 0.02 | 10000 | 0.01
C-25 aut IEC 898 | Caut 25 A | 0 | 25 | 39 | 1000 | 42 | 500 | 48 | 200 | 56 | 100 | 70 | 50 | 110 | 20 | 193 | 10 | 250 | 5 | 250 | 2 | 250 | 1 | 250 | 0.5 | 250 | 0.2 | 250 | 0.1 | 265 | 0.05 | 635 | 0.02 | 12500 | 0.01
C-32 aut IEC 898 | Caut 32 A | 0 | 32 | 50 | 1000 | 53 | 500 | 62 | 200 | 72 | 100 | 90 | 50 | 140 | 20 | 246 | 10 | 320 | 5 | 320 | 2 | 320 | 1 | 320 | 0.5 | 320 | 0.2 | 320 | 0.1 | 339 | 0.05 | 813 | 0.02 | 16000 | 0.01
C-40 aut IEC 898 | Caut 40 A | 0 | 40 | 62 | 1000 | 67 | 500 | 77 | 200 | 90 | 100 | 112 | 50 | 175 | 20 | 308 | 10 | 400 | 5 | 400 | 2 | 400 | 1 | 400 | 0.5 | 400 | 0.2 | 400 | 0.1 | 423 | 0.05 | 1016 | 0.02 | 20000 | 0.01
C-50 aut IEC 947 | Caut 50 A | 0 | 50 | 71 | 1000 | 76 | 500 | 86 | 200 | 102 | 100 | 123 | 50 | 192 | 20 | 372 | 10 | 500 | 5 | 500 | 2 | 500 | 1 | 500 | 0.5 | 500 | 0.2 | 500 | 0.1 | 529 | 0.05 | 1270 | 0.02 | 25000 | 0.01
C-63 aut IEC 947 | Caut 63 A | 0 | 63 | 89 | 1000 | 95 | 500 | 108 | 200 | 128 | 100 | 154 | 50 | 242 | 20 | 469 | 10 | 630 | 5 | 630 | 2 | 630 | 1 | 630 | 0.5 | 630 | 0.2 | 630 | 0.1 | 667 | 0.05 | 1600 | 0.02 | 31500 | 0.01
C-80 aut IEC 947 | Caut 80 A | 0 | 80 | 113 | 1000 | 121 | 500 | 138 | 200 | 162 | 100 | 196 | 50 | 307 | 20 | 595 | 10 | 800 | 5 | 800 | 2 | 800 | 1 | 800 | 0.5 | 800 | 0.2 | 800 | 0.1 | 847 | 0.05 | 2030 | 0.02 | 40000 | 0.01
D-16 aut IEC 898 | Daut 16 A | 0 | 16 | 25 | 1000 | 26.7 | 500 | 30.9 | 200 | 36 | 100 | 44.8 | 50 | 70 | 20 | 123 | 10 | 320 | 5 | 320 | 2 | 320 | 1 | 320 | 0.5 | 320 | 0.2 | 320 | 0.1 | 370 | 0.05 | 1248 | 0.02 | 8000 | 0.01
D-20 aut IEC 898 | Daut 20 A | 0 | 20 | 31.2 | 1000 | 33.4 | 500 | 38.6 | 200 | 45 | 100 | 56 | 50 | 88 | 20 | 154 | 10 | 400 | 5 | 400 | 2 | 400 | 1 | 400 | 0.5 | 400 | 0.2 | 400 | 0.1 | 463 | 0.05 | 1560 | 0.02 | 10000 | 0.01
D-25 aut IEC 898 | Daut 25 A | 0 | 25 | 39 | 1000 | 42 | 500 | 48 | 200 | 56 | 100 | 70 | 50 | 110 | 20 | 193 | 10 | 500 | 5 | 500 | 2 | 500 | 1 | 500 | 0.5 | 500 | 0.2 | 500 | 0.1 | 579 | 0.05 | 1950 | 0.02 | 12500 | 0.01
D-32 aut IEC 898 | Daut 32 A | 0 | 32 | 50 | 1000 | 53 | 500 | 62 | 200 | 72 | 100 | 90 | 50 | 140 | 20 | 246 | 10 | 640 | 5 | 640 | 2 | 640 | 1 | 640 | 0.5 | 640 | 0.2 | 640 | 0.1 | 742 | 0.05 | 2496 | 0.02 | 16000 | 0.01
D-40 aut IEC 898 | Daut 40 A | 0 | 40 | 62 | 1000 | 67 | 500 | 77 | 200 | 90 | 100 | 112 | 50 | 175 | 20 | 308 | 10 | 800 | 5 | 800 | 2 | 800 | 1 | 800 | 0.5 | 800 | 0.2 | 800 | 0.1 | 927 | 0.05 | 3120 | 0.02 | 20000 | 0.01
D-50 aut IEC 947 | Daut 50 A | 0 | 50 | 71 | 1000 | 76 | 500 | 86 | 200 | 102 | 100 | 123 | 50 | 192 | 20 | 372 | 10 | 1000 | 5 | 1000 | 2 | 1000 | 1 | 1000 | 0.5 | 1000 | 0.2 | 1000 | 0.1 | 1115 | 0.05 | 12500 | 0.02 | 25000 | 0.01
D-63 aut IEC 947 | Daut 63 A | 0 | 63 | 89 | 1000 | 95 | 500 | 108 | 200 | 128 | 100 | 154 | 50 | 242 | 20 | 469 | 10 | 1260 | 5 | 1260 | 2 | 1260 | 1 | 1260 | 0.5 | 1260 | 0.2 | 1260 | 0.1 | 1405 | 0.05 | 3150 | 0.02 | 31500 | 0.01
D-80 aut IEC 947 | Daut 80 A | 0 | 80 | 113 | 1000 | 121 | 500 | 138 | 200 | 162 | 100 | 196 | 50 | 307 | 20 | 595 | 10 | 1600 | 5 | 1600 | 2 | 1600 | 1 | 1600 | 0.5 | 1600 | 0.2 | 1600 | 0.1 | 1780 | 0.05 | 4000 | 0.02 | 40000 | 0.01
NC100B 25 A Okasel | Oksaut 25 A | 0 | 25 | 45 | 1000 | 46 | 500 | 48 | 200 | 50 | 100 | 55 | 50 | 76 | 20 | 80 | 10 | 110 | 5 | 171 | 2 | 250 | 1 | 385 | 0.5 | 720 | 0.2 | 1200 | 0.1 | 1200 | 0.05 | 1500 | 0.02 | 5000 | 0.01
NC100B 35 A Okasel | Oksaut 35 A | 0 | 35 | 58 | 1000 | 59 | 500 | 62 | 200 | 67 | 100 | 75 | 50 | 93 | 20 | 120 | 10 | 160 | 5 | 252 | 2 | 380 | 1 | 610 | 0.5 | 1200 | 0.2 | 1200 | 0.1 | 1200 | 0.05 | 1500 | 0.02 | 5000 | 0.01
NC100B 50 A Okasel | Oksaut 50 A | 0 | 50 | 85 | 1000 | 89 | 500 | 100 | 200 | 112 | 100 | 131 | 50 | 172 | 20 | 230 | 10 | 310 | 5 | 480 | 2 | 700 | 1 | 1050 | 0.5 | 1200 | 0.2 | 1200 | 0.1 | 1200 | 0.05 | 1500 | 0.02 | 5000 | 0.01
NC100B 63 A Okasel | Oksaut 63 A | 0 | 63 | 107 | 1000 | 113 | 500 | 126 | 200 | 143 | 100 | 171 | 50 | 229 | 20 | 300 | 10 | 420 | 5 | 670 | 2 | 1000 | 1 | 1200 | 0.5 | 1200 | 0.2 | 1200 | 0.1 | 1200 | 0.05 | 1500 | 0.02 | 5000 | 0.01
NC100B 80 A Okasel | Oksaut 80 A | 0 | 80 | 143 | 1000 | 157 | 500 | 184 | 200 | 219 | 100 | 273 | 50 | 390 | 20 | 520 | 10 | 730 | 5 | 1200 | 2 | 1200 | 1 | 1200 | 0.5 | 1200 | 0.2 | 1200 | 0.1 | 1200 | 0.05 | 1500 | 0.02 | 5000 | 0.01
Name | Shortname | Setting | Inom | I> | t> | I>> | t>> | I>>> | t>>> | dropout | treset | tinput | toutput
|  |  | A | A | s | A | s | A | s |  | s | s | s
Voorbeeld vaste tijd 200 A | Voorbeeld | 1 | 200 | 400 | 1 | 1000 | 0.1 | 10000 | 0.01 | 1 | 0 | 0 | 0
Name | Shortname | Setting | Inom | I> | Id | m | I>> | t>> | I>>> | t>>> | dropout | treset | resetmethod | Uprop
|  |  | A | A |  |  | A | s | A | s |  | s
Voorbeeld normal inverse 200 A | Voorbeeld | 11 | 200 | 250 | 20 | 1 | 1000 | 0.1 | 0 | 0 | 1 | 0 | 0 | FALSE
Voorbeeld very inverse 200 A | Voorbeeld | 12 | 200 | 250 | 20 | 1 | 1000 | 0.1 | 0 | 0 | 1 | 0 | 0 | FALSE
Voorbeeld extremely inverse 200 A | Voorbeeld | 13 | 200 | 250 | 20 | 1 | 1000 | 0.1 | 0 | 0 | 1 | 0 | 1 | FALSE
Voorbeeld long time inverse 200 A | Voorbeeld | 14 | 200 | 250 | 20 | 1 | 1000 | 0.1 | 0 | 0 | 1 | 0 | 1 | TRUE
Voorbeeld RI-inverse 200 A | Voorbeeld | 15 | 200 | 250 | 20 | 1 | 1000 | 0.1 | 0 | 0 | 1 | 0 | 1 | TRUE
Name | Shortname | Setting | Inom | I> | Id | m | alfa | beta | c | d | e | I>> | t>> | I>>> | t>>> | dropout | treset
|  |  | A | A | [6 empty] | s | A | s | A | s |  | s
Voorbeeld speciaal 200 A | Voorbeeld | 21 | 200 | 250 | 20 | 1 | 1 | 3 | 1 | 1 | 0 | 1000 | 0.1 |  |  | 1 | 0
Name | Shortname | Setting | Inom | I> | m
|  |  | A | A
Voorbeeld HV-fuse 200 A | Voorbeeld | 31 | 200 | 250 | 1
Voorbeeld FR-fuse 200 A | Voorbeeld | 32 | 200 | 250 | 1
Name | Shortname | Setting | Inom | I> | t> | I>> | t>> | I>>> | t>>> | Ilt | alfa | Ist | dropout
|  |  | A | A | s | A | s | A | s | A |  | A
Voorbeeld LSI | Voorbeeld | 41 | 1250 | 625 | 3 | 3750 | 0.25 | 15000 | 0.015 | 3750 | 2 | 10000 | 1

## Voltage
Name | Shortname | Unom | tinput | toutput | U< | t< | U<< | t<< | U> | t> | U>> | t>> | Ue> | te>
|  | kV | s | s | kV | s | kV | s | kV | s | kV | s | kV | s
Voorbeeld 10 kV | Voorbeeld | 10 | 0 | 0 | 9.6 | 1 | 9.2 | 0.2 | 10.8 | 2 | 11.5 | 0.5 | 0 | 0
Voorbeeld 0,4 kV | Voorbeeld | 0.4 | 0 | 0 | 0.38 | 1.5 | 0.36 | 0.3 | 0.42 | 2.5 | 0.44 | 0.4 | 0 | 0

## Distance
Name | Shortname | tinput | toutput | Ie> | I> | U< | Z< | Kn | Kn_angle | t1 | t2 | t3 | tdir | tback | tnodir
|  | s | s | A | A | kV | Ohm |  | ° | s | s | s | s | s | s
Voorbeeld 200 A | Voorbeeld | 0 | 0 | 0 | 200 | 0 | 0 | 3 | 0 | 0.05 | 0.9 | 3 | 5 | 0 | 8

## Vt
Name | Ratio | Class | Capacity
VA
Voorbeeld 200 VA | Overzetverhouding | Klasse | 200

## Ct
Name | Ratio | Class | Capacity | Inom | Ik_dynamic | Ik_thermic | T_thermic
|  |  | VA | A | kA | kA | s
Voorbeeld 300 A | Overzetverhouding | Klasse | 100 | 300 | 30 | 20 | 1

## Load
Name | Cos1 | YearUse1 | Alfa1*1000 | Beta1 | Cos2 | YearUse2 | Alfa2*1000 | Beta2
|  | kWh |  |  |  | kWh
vrijstaande woningen | 0.9 | 4400 | 0.2319 | 0.0234 | 0 | 0 | 0 | 0
eengezinswoningen | 0.9 | 3300 | 0.2332 | 0.0159 | 0 | 0 | 0 | 0
etagewoningen | 0.9 | 2400 | 0.189 | 0.0325 | 0 | 0 | 0 | 0
huishoudelijk | 0.9 | 2400 | 0.1847 | 0.0437 | 0 | 0 | 0 | 0
gemengd | 0.9 | 6400 | 0.1524 | 0.0533 | 0 | 0 | 0 | 0
gemiddeld | 0.9 | 3300 | 0.3 | 0.03 | 0 | 0 | 0 | 0
eengezinswoningen plus opwek | 0.9 | 3300 | 0.2332 | 0.0159 | 1 | -400 | 1.25 | 0

## GM
Name | Cos | Indicator | Correlation | Average[1] | Average[2] | Average[3] | Average[4] | Deviation[1] | Deviation[2] | Deviation[3] | Deviation[4] | Workday[1,1] | Workday[1,2] | Workday[1,3] | Workday[1,4] | Workday[1,5] | Workday[1,6] | Workday[1,7] | Workday[1,8] | Workday[1,9] | Workday[1,10] | Workday[1,11] | Workday[1,12] | Workday[1,13] | Workday[1,14] | Workday[1,15] | Workday[1,16] | Workday[1,17] | Workday[1,18] | Workday[1,19] | Workday[1,20] | Workday[1,21] | Workday[1,22] | Workday[1,23] | Workday[1,24] | Workday[1,25] | Workday[1,26] | Workday[1,27] | Workday[1,28] | Workday[1,29] | Workday[1,30] | Workday[1,31] | Workday[1,32] | Workday[1,33] | Workday[1,34] | Workday[1,35] | Workday[1,36] | Workday[1,37] | Workday[1,38] | Workday[1,39] | Workday[1,40] | Workday[1,41] | Workday[1,42] | Workday[1,43] | Workday[1,44] | Workday[1,45] | Workday[1,46] | Workday[1,47] | Workday[1,48] | Workday[1,49] | Workday[1,50] | Workday[1,51] | Workday[1,52] | Workday[1,53] | Workday[1,54] | Workday[1,55] | Workday[1,56] | Workday[1,57] | Workday[1,58] | Workday[1,59] | Workday[1,60] | Workday[1,61] | Workday[1,62] | Workday[1,63] | Workday[1,64] | Workday[1,65] | Workday[1,66] | Workday[1,67] | Workday[1,68] | Workday[1,69] | Workday[1,70] | Workday[1,71] | Workday[1,72] | Workday[1,73] | Workday[1,74] | Workday[1,75] | Workday[1,76] | Workday[1,77] | Workday[1,78] | Workday[1,79] | Workday[1,80] | Workday[1,81] | Workday[1,82] | Workday[1,83] | Workday[1,84] | Workday[1,85] | Workday[1,86] | Workday[1,87] | Workday[1,88] | Workday[1,89] | Workday[1,90] | Workday[1,91] | Workday[1,92] | Workday[1,93] | Workday[1,94] | Workday[1,95] | Workday[1,96] | Workday[2,1] | Workday[2,2] | Workday[2,3] | Workday[2,4] | Workday[2,5] | Workday[2,6] | Workday[2,7] | Workday[2,8] | Workday[2,9] | Workday[2,10] | Workday[2,11] | Workday[2,12] | Workday[2,13] | Workday[2,14] | Workday[2,15] | Workday[2,16] | Workday[2,17] | Workday[2,18] | Workday[2,19] | Workday[2,20] | Workday[2,21] | Workday[2,22] | Workday[2,23] | Workday[2,24] | Workday[2,25] | Workday[2,26] | Workday[2,27] | Workday[2,28] | Workday[2,29] | Workday[2,30] | Workday[2,31] | Workday[2,32] | Workday[2,33] | Workday[2,34] | Workday[2,35] | Workday[2,36] | Workday[2,37] | Workday[2,38] | Workday[2,39] | Workday[2,40] | Workday[2,41] | Workday[2,42] | Workday[2,43] | Workday[2,44] | Workday[2,45] | Workday[2,46] | Workday[2,47] | Workday[2,48] | Workday[2,49] | Workday[2,50] | Workday[2,51] | Workday[2,52] | Workday[2,53] | Workday[2,54] | Workday[2,55] | Workday[2,56] | Workday[2,57] | Workday[2,58] | Workday[2,59] | Workday[2,60] | Workday[2,61] | Workday[2,62] | Workday[2,63] | Workday[2,64] | Workday[2,65] | Workday[2,66] | Workday[2,67] | Workday[2,68] | Workday[2,69] | Workday[2,70] | Workday[2,71] | Workday[2,72] | Workday[2,73] | Workday[2,74] | Workday[2,75] | Workday[2,76] | Workday[2,77] | Workday[2,78] | Workday[2,79] | Workday[2,80] | Workday[2,81] | Workday[2,82] | Workday[2,83] | Workday[2,84] | Workday[2,85] | Workday[2,86] | Workday[2,87] | Workday[2,88] | Workday[2,89] | Workday[2,90] | Workday[2,91] | Workday[2,92] | Workday[2,93] | Workday[2,94] | Workday[2,95] | Workday[2,96] | Workday[3,1] | Workday[3,2] | Workday[3,3] | Workday[3,4] | Workday[3,5] | Workday[3,6] | Workday[3,7] | Workday[3,8] | Workday[3,9] | Workday[3,10] | Workday[3,11] | Workday[3,12] | Workday[3,13] | Workday[3,14] | Workday[3,15] | Workday[3,16] | Workday[3,17] | Workday[3,18] | Workday[3,19] | Workday[3,20] | Workday[3,21] | Workday[3,22] | Workday[3,23] | Workday[3,24] | Workday[3,25] | Workday[3,26] | Workday[3,27] | Workday[3,28] | Workday[3,29] | Workday[3,30] | Workday[3,31] | Workday[3,32] | Workday[3,33] | Workday[3,34] | Workday[3,35] | Workday[3,36] | Workday[3,37] | Workday[3,38] | Workday[3,39] | Workday[3,40] | Workday[3,41] | Workday[3,42] | Workday[3,43] | Workday[3,44] | Workday[3,45] | Workday[3,46] | Workday[3,47] | Workday[3,48] | Workday[3,49] | Workday[3,50] | Workday[3,51] | Workday[3,52] | Workday[3,53] | Workday[3,54] | Workday[3,55] | Workday[3,56] | Workday[3,57] | Workday[3,58] | Workday[3,59] | Workday[3,60] | Workday[3,61] | Workday[3,62] | Workday[3,63] | Workday[3,64] | Workday[3,65] | Workday[3,66] | Workday[3,67] | Workday[3,68] | Workday[3,69] | Workday[3,70] | Workday[3,71] | Workday[3,72] | Workday[3,73] | Workday[3,74] | Workday[3,75] | Workday[3,76] | Workday[3,77] | Workday[3,78] | Workday[3,79] | Workday[3,80] | Workday[3,81] | Workday[3,82] | Workday[3,83] | Workday[3,84] | Workday[3,85] | Workday[3,86] | Workday[3,87] | Workday[3,88] | Workday[3,89] | Workday[3,90] | Workday[3,91] | Workday[3,92] | Workday[3,93] | Workday[3,94] | Workday[3,95] | Workday[3,96] | Workday[4,1] | Workday[4,2] | Workday[4,3] | Workday[4,4] | Workday[4,5] | Workday[4,6] | Workday[4,7] | Workday[4,8] | Workday[4,9] | Workday[4,10] | Workday[4,11] | Workday[4,12] | Workday[4,13] | Workday[4,14] | Workday[4,15] | Workday[4,16] | Workday[4,17] | Workday[4,18] | Workday[4,19] | Workday[4,20] | Workday[4,21] | Workday[4,22] | Workday[4,23] | Workday[4,24] | Workday[4,25] | Workday[4,26] | Workday[4,27] | Workday[4,28] | Workday[4,29] | Workday[4,30] | Workday[4,31] | Workday[4,32] | Workday[4,33] | Workday[4,34] | Workday[4,35] | Workday[4,36] | Workday[4,37] | Workday[4,38] | Workday[4,39] | Workday[4,40] | Workday[4,41] | Workday[4,42] | Workday[4,43] | Workday[4,44] | Workday[4,45] | Workday[4,46] | Workday[4,47] | Workday[4,48] | Workday[4,49] | Workday[4,50] | Workday[4,51] | Workday[4,52] | Workday[4,53] | Workday[4,54] | Workday[4,55] | Workday[4,56] | Workday[4,57] | Workday[4,58] | Workday[4,59] | Workday[4,60] | Workday[4,61] | Workday[4,62] | Workday[4,63] | Workday[4,64] | Workday[4,65] | Workday[4,66] | Workday[4,67] | Workday[4,68] | Workday[4,69] | Workday[4,70] | Workday[4,71] | Workday[4,72] | Workday[4,73] | Workday[4,74] | Workday[4,75] | Workday[4,76] | Workday[4,77] | Workday[4,78] | Workday[4,79] | Workday[4,80] | Workday[4,81] | Workday[4,82] | Workday[4,83] | Workday[4,84] | Workday[4,85] | Workday[4,86] | Workday[4,87] | Workday[4,88] | Workday[4,89] | Workday[4,90] | Workday[4,91] | Workday[4,92] | Workday[4,93] | Workday[4,94] | Workday[4,95] | Workday[4,96] | Weekend[1,1] | Weekend[1,2] | Weekend[1,3] | Weekend[1,4] | Weekend[1,5] | Weekend[1,6] | Weekend[1,7] | Weekend[1,8] | Weekend[1,9] | Weekend[1,10] | Weekend[1,11] | Weekend[1,12] | Weekend[1,13] | Weekend[1,14] | Weekend[1,15] | Weekend[1,16] | Weekend[1,17] | Weekend[1,18] | Weekend[1,19] | Weekend[1,20] | Weekend[1,21] | Weekend[1,22] | Weekend[1,23] | Weekend[1,24] | Weekend[1,25] | Weekend[1,26] | Weekend[1,27] | Weekend[1,28] | Weekend[1,29] | Weekend[1,30] | Weekend[1,31] | Weekend[1,32] | Weekend[1,33] | Weekend[1,34] | Weekend[1,35] | Weekend[1,36] | Weekend[1,37] | Weekend[1,38] | Weekend[1,39] | Weekend[1,40] | Weekend[1,41] | Weekend[1,42] | Weekend[1,43] | Weekend[1,44] | Weekend[1,45] | Weekend[1,46] | Weekend[1,47] | Weekend[1,48] | Weekend[1,49] | Weekend[1,50] | Weekend[1,51] | Weekend[1,52] | Weekend[1,53] | Weekend[1,54] | Weekend[1,55] | Weekend[1,56] | Weekend[1,57] | Weekend[1,58] | Weekend[1,59] | Weekend[1,60] | Weekend[1,61] | Weekend[1,62] | Weekend[1,63] | Weekend[1,64] | Weekend[1,65] | Weekend[1,66] | Weekend[1,67] | Weekend[1,68] | Weekend[1,69] | Weekend[1,70] | Weekend[1,71] | Weekend[1,72] | Weekend[1,73] | Weekend[1,74] | Weekend[1,75] | Weekend[1,76] | Weekend[1,77] | Weekend[1,78] | Weekend[1,79] | Weekend[1,80] | Weekend[1,81] | Weekend[1,82] | Weekend[1,83] | Weekend[1,84] | Weekend[1,85] | Weekend[1,86] | Weekend[1,87] | Weekend[1,88] | Weekend[1,89] | Weekend[1,90] | Weekend[1,91] | Weekend[1,92] | Weekend[1,93] | Weekend[1,94] | Weekend[1,95] | Weekend[1,96] | Weekend[2,1] | Weekend[2,2] | Weekend[2,3] | Weekend[2,4] | Weekend[2,5] | Weekend[2,6] | Weekend[2,7] | Weekend[2,8] | Weekend[2,9] | Weekend[2,10] | Weekend[2,11] | Weekend[2,12] | Weekend[2,13] | Weekend[2,14] | Weekend[2,15] | Weekend[2,16] | Weekend[2,17] | Weekend[2,18] | Weekend[2,19] | Weekend[2,20] | Weekend[2,21] | Weekend[2,22] | Weekend[2,23] | Weekend[2,24] | Weekend[2,25] | Weekend[2,26] | Weekend[2,27] | Weekend[2,28] | Weekend[2,29] | Weekend[2,30] | Weekend[2,31] | Weekend[2,32] | Weekend[2,33] | Weekend[2,34] | Weekend[2,35] | Weekend[2,36] | Weekend[2,37] | Weekend[2,38] | Weekend[2,39] | Weekend[2,40] | Weekend[2,41] | Weekend[2,42] | Weekend[2,43] | Weekend[2,44] | Weekend[2,45] | Weekend[2,46] | Weekend[2,47] | Weekend[2,48] | Weekend[2,49] | Weekend[2,50] | Weekend[2,51] | Weekend[2,52] | Weekend[2,53] | Weekend[2,54] | Weekend[2,55] | Weekend[2,56] | Weekend[2,57] | Weekend[2,58] | Weekend[2,59] | Weekend[2,60] | Weekend[2,61] | Weekend[2,62] | Weekend[2,63] | Weekend[2,64] | Weekend[2,65] | Weekend[2,66] | Weekend[2,67] | Weekend[2,68] | Weekend[2,69] | Weekend[2,70] | Weekend[2,71] | Weekend[2,72] | Weekend[2,73] | Weekend[2,74] | Weekend[2,75] | Weekend[2,76] | Weekend[2,77] | Weekend[2,78] | Weekend[2,79] | Weekend[2,80] | Weekend[2,81] | Weekend[2,82] | Weekend[2,83] | Weekend[2,84] | Weekend[2,85] | Weekend[2,86] | Weekend[2,87] | Weekend[2,88] | Weekend[2,89] | Weekend[2,90] | Weekend[2,91] | Weekend[2,92] | Weekend[2,93] | Weekend[2,94] | Weekend[2,95] | Weekend[2,96] | Weekend[3,1] | Weekend[3,2] | Weekend[3,3] | Weekend[3,4] | Weekend[3,5] | Weekend[3,6] | Weekend[3,7] | Weekend[3,8] | Weekend[3,9] | Weekend[3,10] | Weekend[3,11] | Weekend[3,12] | Weekend[3,13] | Weekend[3,14] | Weekend[3,15] | Weekend[3,16] | Weekend[3,17] | Weekend[3,18] | Weekend[3,19] | Weekend[3,20] | Weekend[3,21] | Weekend[3,22] | Weekend[3,23] | Weekend[3,24] | Weekend[3,25] | Weekend[3,26] | Weekend[3,27] | Weekend[3,28] | Weekend[3,29] | Weekend[3,30] | Weekend[3,31] | Weekend[3,32] | Weekend[3,33] | Weekend[3,34] | Weekend[3,35] | Weekend[3,36] | Weekend[3,37] | Weekend[3,38] | Weekend[3,39] | Weekend[3,40] | Weekend[3,41] | Weekend[3,42] | Weekend[3,43] | Weekend[3,44] | Weekend[3,45] | Weekend[3,46] | Weekend[3,47] | Weekend[3,48] | Weekend[3,49] | Weekend[3,50] | Weekend[3,51] | Weekend[3,52] | Weekend[3,53] | Weekend[3,54] | Weekend[3,55] | Weekend[3,56] | Weekend[3,57] | Weekend[3,58] | Weekend[3,59] | Weekend[3,60] | Weekend[3,61] | Weekend[3,62] | Weekend[3,63] | Weekend[3,64] | Weekend[3,65] | Weekend[3,66] | Weekend[3,67] | Weekend[3,68] | Weekend[3,69] | Weekend[3,70] | Weekend[3,71] | Weekend[3,72] | Weekend[3,73] | Weekend[3,74] | Weekend[3,75] | Weekend[3,76] | Weekend[3,77] | Weekend[3,78] | Weekend[3,79] | Weekend[3,80] | Weekend[3,81] | Weekend[3,82] | Weekend[3,83] | Weekend[3,84] | Weekend[3,85] | Weekend[3,86] | Weekend[3,87] | Weekend[3,88] | Weekend[3,89] | Weekend[3,90] | Weekend[3,91] | Weekend[3,92] | Weekend[3,93] | Weekend[3,94] | Weekend[3,95] | Weekend[3,96] | Weekend[4,1] | Weekend[4,2] | Weekend[4,3] | Weekend[4,4] | Weekend[4,5] | Weekend[4,6] | Weekend[4,7] | Weekend[4,8] | Weekend[4,9] | Weekend[4,10] | Weekend[4,11] | Weekend[4,12] | Weekend[4,13] | Weekend[4,14] | Weekend[4,15] | Weekend[4,16] | Weekend[4,17] | Weekend[4,18] | Weekend[4,19] | Weekend[4,20] | Weekend[4,21] | Weekend[4,22] | Weekend[4,23] | Weekend[4,24] | Weekend[4,25] | Weekend[4,26] | Weekend[4,27] | Weekend[4,28] | Weekend[4,29] | Weekend[4,30] | Weekend[4,31] | Weekend[4,32] | Weekend[4,33] | Weekend[4,34] | Weekend[4,35] | Weekend[4,36] | Weekend[4,37] | Weekend[4,38] | Weekend[4,39] | Weekend[4,40] | Weekend[4,41] | Weekend[4,42] | Weekend[4,43] | Weekend[4,44] | Weekend[4,45] | Weekend[4,46] | Weekend[4,47] | Weekend[4,48] | Weekend[4,49] | Weekend[4,50] | Weekend[4,51] | Weekend[4,52] | Weekend[4,53] | Weekend[4,54] | Weekend[4,55] | Weekend[4,56] | Weekend[4,57] | Weekend[4,58] | Weekend[4,59] | Weekend[4,60] | Weekend[4,61] | Weekend[4,62] | Weekend[4,63] | Weekend[4,64] | Weekend[4,65] | Weekend[4,66] | Weekend[4,67] | Weekend[4,68] | Weekend[4,69] | Weekend[4,70] | Weekend[4,71] | Weekend[4,72] | Weekend[4,73] | Weekend[4,74] | Weekend[4,75] | Weekend[4,76] | Weekend[4,77] | Weekend[4,78] | Weekend[4,79] | Weekend[4,80] | Weekend[4,81] | Weekend[4,82] | Weekend[4,83] | Weekend[4,84] | Weekend[4,85] | Weekend[4,86] | Weekend[4,87] | Weekend[4,88] | Weekend[4,89] | Weekend[4,90] | Weekend[4,91] | Weekend[4,92] | Weekend[4,93] | Weekend[4,94] | Weekend[4,95] | Weekend[4,96] | Month[1,1] | Month[1,2] | Month[1,3] | Month[1,4] | Month[1,5] | Month[1,6] | Month[1,7] | Month[1,8] | Month[1,9] | Month[1,10] | Month[1,11] | Month[1,12] | Month[2,1] | Month[2,2] | Month[2,3] | Month[2,4] | Month[2,5] | Month[2,6] | Month[2,7] | Month[2,8] | Month[2,9] | Month[2,10] | Month[2,11] | Month[2,12] | Month[3,1] | Month[3,2] | Month[3,3] | Month[3,4] | Month[3,5] | Month[3,6] | Month[3,7] | Month[3,8] | Month[3,9] | Month[3,10] | Month[3,11] | Month[3,12] | Month[4,1] | Month[4,2] | Month[4,3] | Month[4,4] | Month[4,5] | Month[4,6] | Month[4,7] | Month[4,8] | Month[4,9] | Month[4,10] | Month[4,11] | Month[4,12] | TrendWorkday[1] | TrendWorkday[2] | TrendWorkday[3] | TrendWorkday[4] | TrendWorkday[5] | TrendWorkday[6] | TrendWorkday[7] | TrendWorkday[8] | TrendWorkday[9] | TrendWorkday[10] | TrendWorkday[11] | TrendWorkday[12] | TrendWorkday[13] | TrendWorkday[14] | TrendWorkday[15] | TrendWorkday[16] | TrendWorkday[17] | TrendWorkday[18] | TrendWorkday[19] | TrendWorkday[20] | TrendWorkday[21] | TrendWorkday[22] | TrendWorkday[23] | TrendWorkday[24] | TrendWorkday[25] | TrendWorkday[26] | TrendWorkday[27] | TrendWorkday[28] | TrendWorkday[29] | TrendWorkday[30] | TrendWorkday[31] | TrendWorkday[32] | TrendWorkday[33] | TrendWorkday[34] | TrendWorkday[35] | TrendWorkday[36] | TrendWorkday[37] | TrendWorkday[38] | TrendWorkday[39] | TrendWorkday[40] | TrendWorkday[41] | TrendWorkday[42] | TrendWorkday[43] | TrendWorkday[44] | TrendWorkday[45] | TrendWorkday[46] | TrendWorkday[47] | TrendWorkday[48] | TrendWorkday[49] | TrendWorkday[50] | TrendWorkday[51] | TrendWorkday[52] | TrendWorkday[53] | TrendWorkday[54] | TrendWorkday[55] | TrendWorkday[56] | TrendWorkday[57] | TrendWorkday[58] | TrendWorkday[59] | TrendWorkday[60] | TrendWorkday[61] | TrendWorkday[62] | TrendWorkday[63] | TrendWorkday[64] | TrendWorkday[65] | TrendWorkday[66] | TrendWorkday[67] | TrendWorkday[68] | TrendWorkday[69] | TrendWorkday[70] | TrendWorkday[71] | TrendWorkday[72] | TrendWorkday[73] | TrendWorkday[74] | TrendWorkday[75] | TrendWorkday[76] | TrendWorkday[77] | TrendWorkday[78] | TrendWorkday[79] | TrendWorkday[80] | TrendWorkday[81] | TrendWorkday[82] | TrendWorkday[83] | TrendWorkday[84] | TrendWorkday[85] | TrendWorkday[86] | TrendWorkday[87] | TrendWorkday[88] | TrendWorkday[89] | TrendWorkday[90] | TrendWorkday[91] | TrendWorkday[92] | TrendWorkday[93] | TrendWorkday[94] | TrendWorkday[95] | TrendWorkday[96] | TrendWeekend[1] | TrendWeekend[2] | TrendWeekend[3] | TrendWeekend[4] | TrendWeekend[5] | TrendWeekend[6] | TrendWeekend[7] | TrendWeekend[8] | TrendWeekend[9] | TrendWeekend[10] | TrendWeekend[11] | TrendWeekend[12] | TrendWeekend[13] | TrendWeekend[14] | TrendWeekend[15] | TrendWeekend[16] | TrendWeekend[17] | TrendWeekend[18] | TrendWeekend[19] | TrendWeekend[20] | TrendWeekend[21] | TrendWeekend[22] | TrendWeekend[23] | TrendWeekend[24] | TrendWeekend[25] | TrendWeekend[26] | TrendWeekend[27] | TrendWeekend[28] | TrendWeekend[29] | TrendWeekend[30] | TrendWeekend[31] | TrendWeekend[32] | TrendWeekend[33] | TrendWeekend[34] | TrendWeekend[35] | TrendWeekend[36] | TrendWeekend[37] | TrendWeekend[38] | TrendWeekend[39] | TrendWeekend[40] | TrendWeekend[41] | TrendWeekend[42] | TrendWeekend[43] | TrendWeekend[44] | TrendWeekend[45] | TrendWeekend[46] | TrendWeekend[47] | TrendWeekend[48] | TrendWeekend[49] | TrendWeekend[50] | TrendWeekend[51] | TrendWeekend[52] | TrendWeekend[53] | TrendWeekend[54] | TrendWeekend[55] | TrendWeekend[56] | TrendWeekend[57] | TrendWeekend[58] | TrendWeekend[59] | TrendWeekend[60] | TrendWeekend[61] | TrendWeekend[62] | TrendWeekend[63] | TrendWeekend[64] | TrendWeekend[65] | TrendWeekend[66] | TrendWeekend[67] | TrendWeekend[68] | TrendWeekend[69] | TrendWeekend[70] | TrendWeekend[71] | TrendWeekend[72] | TrendWeekend[73] | TrendWeekend[74] | TrendWeekend[75] | TrendWeekend[76] | TrendWeekend[77] | TrendWeekend[78] | TrendWeekend[79] | TrendWeekend[80] | TrendWeekend[81] | TrendWeekend[82] | TrendWeekend[83] | TrendWeekend[84] | TrendWeekend[85] | TrendWeekend[86] | TrendWeekend[87] | TrendWeekend[88] | TrendWeekend[89] | TrendWeekend[90] | TrendWeekend[91] | TrendWeekend[92] | TrendWeekend[93] | TrendWeekend[94] | TrendWeekend[95] | TrendWeekend[96] | TrendMonth[1] | TrendMonth[2] | TrendMonth[3] | TrendMonth[4] | TrendMonth[5] | TrendMonth[6] | TrendMonth[7] | TrendMonth[8] | TrendMonth[9] | TrendMonth[10] | TrendMonth[11] | TrendMonth[12]
|  |  |  | kW of % | kW of % | kW of % | kW of % | kW of % | kW of % | kW of % | kW of %
Warmtepomp | 0.9 | WP | 0 | 100 |  |  |  | 0.1 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [288 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [288 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
PV | 1 | PV | 1 | -8.756 |  |  |  | 15.009 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 0.848 | 0.893 | 0.922 | 0.942 | 0.957 | 0.967 | 0.973 | 0.977 | 0.98 | 0.982 | 0.983 | 0.983 | 0.983 | 0.983 | 0.982 | 0.981 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.979 | 0.979 | 0.979 | 0.979 | 0.979 | 0.979 | 0.979 | 0.98 | 0.98 | 0.981 | 0.982 | 0.981 | 0.982 | 0.982 | 0.982 | 0.983 | 0.981 | 0.978 | 0.974 | 0.969 | 0.963 | 0.956 | 0.945 | 0.934 | 0.928 | 0.861 | 0.741 | 0.597 | 0.424 | 0.296 | 0.217 | 0.156 | 0.115 | 0.088 | 0.07 | 0.057 | 0.049 | 0.043 | 0.039 | 0.036 | 0.035 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [288 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 0.848 | 0.893 | 0.922 | 0.942 | 0.957 | 0.967 | 0.973 | 0.977 | 0.98 | 0.982 | 0.983 | 0.983 | 0.983 | 0.983 | 0.982 | 0.981 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.979 | 0.979 | 0.979 | 0.979 | 0.979 | 0.979 | 0.979 | 0.98 | 0.98 | 0.981 | 0.982 | 0.981 | 0.982 | 0.982 | 0.982 | 0.983 | 0.981 | 0.978 | 0.974 | 0.969 | 0.963 | 0.956 | 0.945 | 0.934 | 0.928 | 0.861 | 0.741 | 0.597 | 0.424 | 0.296 | 0.217 | 0.156 | 0.115 | 0.088 | 0.07 | 0.057 | 0.049 | 0.043 | 0.039 | 0.036 | 0.035 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [288 empty] | 1 | 1.007 | 1.004 | 1.007 | 1.035 | 1.042 | 1.047 | 1.053 | 1.033 | 1.011 | 0.999 | 0.993 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.005 | -0.079 | -0.287 | -0.701 | -1.766 | -3.209 | -5.077 | -7.037 | -8.985 | -12.374 | -15.97 | -19.487 | -24.058 | -28.86 | -33.051 | -37.845 | -41.176 | -45.278 | -48.468 | -52.685 | -53.991 | -53.93 | -56.356 | -58.678 | -59.682 | -63.037 | -63.12 | -65.745 | -65.35 | -70.078 | -68.571 | -69.108 | -69.043 | -69.464 | -70.423 | -68.194 | -68.778 | -64.324 | -59.094 | -58.957 | -53.913 | -51.056 | -49.331 | -43.199 | -41.197 | -37.194 | -36.424 | -31.343 | -26.049 | -21.757 | -19.079 | -16.474 | -15.577 | -12.494 | -9.299 | -7.421 | -5.6 | -3.295 | -1.792 | -0.807 | -0.453 | -0.236 | -0.099 | -0.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.005 | -0.079 | -0.287 | -0.701 | -1.766 | -3.209 | -5.077 | -7.037 | -8.985 | -12.374 | -15.97 | -19.487 | -24.058 | -28.86 | -33.051 | -37.845 | -41.176 | -45.278 | -48.468 | -52.685 | -53.991 | -53.93 | -56.356 | -58.678 | -59.682 | -63.037 | -63.12 | -65.745 | -65.35 | -70.078 | -68.571 | -69.108 | -69.043 | -69.464 | -70.423 | -68.194 | -68.778 | -64.324 | -59.094 | -58.957 | -53.913 | -51.056 | -49.331 | -43.199 | -41.197 | -37.194 | -36.424 | -31.343 | -26.049 | -21.757 | -19.079 | -16.474 | -15.577 | -12.494 | -9.299 | -7.421 | -5.6 | -3.295 | -1.792 | -0.807 | -0.453 | -0.236 | -0.099 | -0.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.254 | 0.399 | 0.302 | 0.391 | 0.805 | 0.947 | 0.939 | 1 | 0.752 | 0.44 | 0.308 | 0.172
EV | 1 | EV | 0 | 19.039 |  |  |  | 14.235 |  |  |  | 0.116 | 0.105 | 0.1 | 0.095 | 0.091 | 0.088 | 0.086 | 0.084 | 0.088 | 0.084 | 0.086 | 0.084 | 0.088 | 0.089 | 0.09 | 0.091 | 0.101 | 0.098 | 0.096 | 0.087 | 0.083 | 0.076 | 0.069 | 0.052 | 0.038 | 0.04 | 0.041 | 0.045 | 0.052 | 0.056 | 0.05 | 0.051 | 0.05 | 0.049 | 0.047 | 0.046 | 0.047 | 0.047 | 0.047 | 0.047 | 0.049 | 0.05 | 0.048 | 0.05 | 0.05 | 0.053 | 0.056 | 0.058 | 0.061 | 0.064 | 0.067 | 0.068 | 0.071 | 0.07 | 0.071 | 0.073 | 0.072 | 0.073 | 0.073 | 0.076 | 0.082 | 0.086 | 0.088 | 0.093 | 0.1 | 0.104 | 0.112 | 0.119 | 0.128 | 0.136 | 0.144 | 0.152 | 0.159 | 0.162 | 0.167 | 0.172 | 0.179 | 0.183 | 0.184 | 0.181 | 0.177 | 0.171 | 0.165 | 0.161 | 0.166 | 0.161 | 0.153 | 0.149 | 0.161 | 0.154 | 0.149 | 0.145 | 0.137 | 0.129 | 0.121 | 0.115 | [288 empty] | 0.116 | 0.105 | 0.1 | 0.095 | 0.091 | 0.088 | 0.086 | 0.084 | 0.088 | 0.084 | 0.086 | 0.084 | 0.088 | 0.089 | 0.09 | 0.091 | 0.101 | 0.098 | 0.096 | 0.087 | 0.083 | 0.076 | 0.069 | 0.052 | 0.038 | 0.04 | 0.041 | 0.045 | 0.052 | 0.056 | 0.05 | 0.051 | 0.05 | 0.049 | 0.047 | 0.046 | 0.047 | 0.047 | 0.047 | 0.047 | 0.049 | 0.05 | 0.048 | 0.05 | 0.05 | 0.053 | 0.056 | 0.058 | 0.061 | 0.064 | 0.067 | 0.068 | 0.071 | 0.07 | 0.071 | 0.073 | 0.072 | 0.073 | 0.073 | 0.076 | 0.082 | 0.086 | 0.088 | 0.093 | 0.1 | 0.104 | 0.112 | 0.119 | 0.128 | 0.136 | 0.144 | 0.152 | 0.159 | 0.162 | 0.167 | 0.172 | 0.179 | 0.183 | 0.184 | 0.181 | 0.177 | 0.171 | 0.165 | 0.161 | 0.166 | 0.161 | 0.153 | 0.149 | 0.161 | 0.154 | 0.149 | 0.145 | 0.137 | 0.129 | 0.121 | 0.115 | [288 empty] | 1 | 1 | 1 | 1 | 0.956 | 0.948 | 0.907 | 0.916 | 0.965 | 0.973 | 1 | 1
Huislaadpunt | 1 | EV | 0 | 3.49 |  |  |  | 58.255 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [288 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [288 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Kantoorlaadpunt | 1 | EV | 0 | 8.143 |  |  |  | 55.929 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [288 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [288 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Openbaar laadpunt | 1 | EV | 0 | 8.143 |  |  |  | 55.929 |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [288 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | [288 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Laadpunt met vermogen | 1 | EV | 0 | 100 |  |  |  | 0.1 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [288 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [288 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | -75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Koken | 1 | Koken | 0 | 20 |  |  |  | 0.1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [288 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [288 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Airco | 0.95 | Apparaat | 0 | 36.122 |  |  |  | 9.749 |  |  |  | 0.871 | 0.871 | 0.871 | 0.872 | 0.872 | 0.873 | 0.873 | 0.874 | 0.875 | 0.876 | 0.878 | 0.879 | 0.881 | 0.883 | 0.884 | 0.886 | 0.889 | 0.892 | 0.896 | 0.9 | 0.9 | 0.901 | 0.9 | 0.902 | 0.902 | 0.901 | 0.904 | 0.907 | 0.91 | 0.911 | 0.911 | 0.911 | 0.909 | 0.908 | 0.908 | 0.909 | 0.909 | 0.908 | 0.906 | 0.906 | 0.907 | 0.91 | 0.912 | 0.914 | 0.92 | 0.918 | 0.925 | 0.928 | 0.927 | 0.922 | 0.927 | 0.929 | 0.924 | 0.92 | 0.927 | 0.931 | 0.928 | 0.921 | 0.924 | 0.927 | 0.935 | 0.934 | 0.934 | 0.937 | 0.943 | 0.948 | 0.95 | 0.953 | 0.954 | 0.954 | 0.953 | 0.955 | 0.957 | 0.956 | 0.954 | 0.958 | 0.953 | 0.954 | 0.955 | 0.955 | 0.954 | 0.953 | 0.952 | 0.951 | 0.948 | 0.939 | 0.941 | 0.94 | 0.921 | 0.906 | 0.915 | 0.894 | 0.878 | 0.875 | 0.871 | 0.883 | [288 empty] | 0.871 | 0.871 | 0.871 | 0.872 | 0.872 | 0.873 | 0.873 | 0.874 | 0.875 | 0.876 | 0.878 | 0.879 | 0.881 | 0.883 | 0.884 | 0.886 | 0.889 | 0.892 | 0.896 | 0.9 | 0.9 | 0.901 | 0.9 | 0.902 | 0.902 | 0.901 | 0.904 | 0.907 | 0.91 | 0.911 | 0.911 | 0.911 | 0.909 | 0.908 | 0.908 | 0.909 | 0.909 | 0.908 | 0.906 | 0.906 | 0.907 | 0.91 | 0.912 | 0.914 | 0.92 | 0.918 | 0.925 | 0.928 | 0.927 | 0.922 | 0.927 | 0.929 | 0.924 | 0.92 | 0.927 | 0.931 | 0.928 | 0.921 | 0.924 | 0.927 | 0.935 | 0.934 | 0.934 | 0.937 | 0.943 | 0.948 | 0.95 | 0.953 | 0.954 | 0.954 | 0.953 | 0.955 | 0.957 | 0.956 | 0.954 | 0.958 | 0.953 | 0.954 | 0.955 | 0.955 | 0.954 | 0.953 | 0.952 | 0.951 | 0.948 | 0.939 | 0.941 | 0.94 | 0.921 | 0.906 | 0.915 | 0.894 | 0.878 | 0.875 | 0.871 | 0.883 | [288 empty] | 0.01 | 0.01 | 0.19 | 0.24 | 0.51 | 0.87 | 1 | 0.81 | 0.38 | 0.19 | 0.01 | 0.01
sjv500 | 0.98 | Belasting | 0 | 0.117 | 0.029 |  |  | 0.178 | 0.044 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv1000 | 0.98 | Belasting | 0 | 0.23 | 0.058 |  |  | 0.295 | 0.074 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv1500 | 0.98 | Belasting | 0 | 0.35 | 0.087 |  |  | 0.308 | 0.077 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv2000 | 0.98 | Belasting | 0 | 0.47 | 0.118 |  |  | 0.429 | 0.107 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv2500 | 0.98 | Belasting | 0 | 0.583 | 0.146 |  |  | 0.398 | 0.099 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv3000 | 0.98 | Belasting | 0 | 0.7 | 0.175 |  |  | 0.526 | 0.132 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv3500 | 0.98 | Belasting | 0 | 0.816 | 0.204 |  |  | 0.47 | 0.118 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv4000 | 0.98 | Belasting | 0 | 0.93 | 0.233 |  |  | 0.617 | 0.154 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv4500 | 0.98 | Belasting | 0 | 1.049 | 0.262 |  |  | 0.533 | 0.133 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv5000 | 0.98 | Belasting | 0 | 1.17 | 0.293 |  |  | 0.695 | 0.174 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv6000 | 0.98 | Belasting | 0 | 1.4 | 0.35 |  |  | 0.777 | 0.194 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv7000 | 0.98 | Belasting | 0 | 1.63 | 0.408 |  |  | 0.835 | 0.209 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv8000 | 0.98 | Belasting | 0 | 1.87 | 0.468 |  |  | 0.92 | 0.23 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv9000 | 0.98 | Belasting | 0 | 2.099 | 0.525 |  |  | 0.754 | 0.189 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv10000 | 0.98 | Belasting | 0 | 2.332 | 0.583 |  |  | 0.795 | 0.199 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv15000 | 0.98 | Belasting | 0 | 3.498 | 0.875 |  |  | 0.974 | 0.243 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv20000 | 0.98 | Belasting | 0 | 4.664 | 1.166 |  |  | 1.124 | 0.281 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv25000 | 0.98 | Belasting | 0 | 5.83 | 1.458 |  |  | 1.257 | 0.314 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv30000 | 0.98 | Belasting | 0 | 6.996 | 1.749 |  |  | 1.377 | 0.344 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv35000 | 0.98 | Belasting | 0 | 8.162 | 2.041 |  |  | 1.487 | 0.372 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv40000 | 0.98 | Belasting | 0 | 9.328 | 2.332 |  |  | 1.59 | 0.398 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv45000 | 0.98 | Belasting | 0 | 10.494 | 2.624 |  |  | 1.686 | 0.422 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv50000 | 0.98 | Belasting | 0 | 11.66 | 2.915 |  |  | 1.778 | 0.444 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv60000 | 0.98 | Belasting | 0 | 13.992 | 3.498 |  |  | 1.947 | 0.487 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv70000 | 0.98 | Belasting | 0 | 16.324 | 4.081 |  |  | 2.103 | 0.526 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv80000 | 0.98 | Belasting | 0 | 18.656 | 4.664 |  |  | 2.249 | 0.562 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv90000 | 0.98 | Belasting | 0 | 20.988 | 5.247 |  |  | 2.385 | 0.596 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
sjv100000 | 0.98 | Belasting | 0 | 23.32 | 5.83 |  |  | 2.514 | 0.629 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv500 | 0.98 | Belasting | 0 | 0.127 | 0.032 |  |  | 0.236 | 0.055 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv1000 | 0.98 | Belasting | 0 | 0.253 | 0.063 |  |  | 0.341 | 0.09 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv1500 | 0.98 | Belasting | 0 | 0.38 | 0.095 |  |  | 0.43 | 0.144 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv2000 | 0.98 | Belasting | 0 | 0.506 | 0.127 |  |  | 0.488 | 0.166 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv2500 | 0.98 | Belasting | 0 | 0.633 | 0.158 |  |  | 0.618 | 0.186 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv3000 | 0.98 | Belasting | 0 | 0.76 | 0.19 |  |  | 0.645 | 0.203 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv3500 | 0.98 | Belasting | 0 | 0.886 | 0.222 |  |  | 0.671 | 0.22 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv4000 | 0.98 | Belasting | 0 | 1.013 | 0.253 |  |  | 0.716 | 0.235 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv4500 | 0.98 | Belasting | 0 | 1.139 | 0.285 |  |  | 0.773 | 0.249 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv5000 | 0.98 | Belasting | 0 | 1.266 | 0.317 |  |  | 0.912 | 0.263 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv6000 | 0.98 | Belasting | 0 | 1.519 | 0.38 |  |  | 1.031 | 0.288 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv7000 | 0.98 | Belasting | 0 | 1.772 | 0.443 |  |  | 1.244 | 0.311 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv8000 | 0.98 | Belasting | 0 | 2.026 | 0.506 |  |  | 1.33 | 0.333 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv9000 | 0.98 | Belasting | 0 | 2.279 | 0.57 |  |  | 1.41 | 0.352 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv10000 | 0.98 | Belasting | 0 | 2.532 | 0.633 |  |  | 1.487 | 0.372 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv15000 | 0.98 | Belasting | 0 | 3.798 | 0.95 |  |  | 1.821 | 0.455 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv20000 | 0.98 | Belasting | 0 | 5.064 | 1.266 |  |  | 2.103 | 0.525 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv25000 | 0.98 | Belasting | 0 | 6.33 | 1.583 |  |  | 2.35 | 0.588 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv30000 | 0.98 | Belasting | 0 | 7.596 | 1.899 |  |  | 2.575 | 0.644 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv35000 | 0.98 | Belasting | 0 | 8.862 | 2.216 |  |  | 2.782 | 0.695 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv40000 | 0.98 | Belasting | 0 | 10.128 | 2.532 |  |  | 2.974 | 0.744 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv45000 | 0.98 | Belasting | 0 | 11.394 | 2.849 |  |  | 3.154 | 0.788 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv50000 | 0.98 | Belasting | 0 | 12.66 | 3.165 |  |  | 3.745 | 0.936 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv60000 | 0.98 | Belasting | 0 | 15.192 | 3.798 |  |  | 3.642 | 0.911 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv70000 | 0.98 | Belasting | 0 | 17.724 | 4.431 |  |  | 3.934 | 0.983 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv80000 | 0.98 | Belasting | 0 | 20.256 | 5.064 |  |  | 4.206 | 1.051 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv90000 | 0.98 | Belasting | 0 | 22.788 | 5.697 |  |  | 4.46 | 1.115 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1
Verhoogd sjv100000 | 0.98 | Belasting | 0 | 25.32 | 6.33 |  |  | 4.702 | 1.175 |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [192 empty] | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 1 | 1 | 1 | 1 | 1

## GM (echt)
Name | Cos | Indicator | Correlation | Average[1] | Average[2] | Average[3] | Average[4] | Deviation[1] | Deviation[2] | Deviation[3] | Deviation[4] | Workday[1,1] | Workday[1,2] | Workday[1,3] | Workday[1,4] | Workday[1,5] | Workday[1,6] | Workday[1,7] | Workday[1,8] | Workday[1,9] | Workday[1,10] | Workday[1,11] | Workday[1,12] | Workday[1,13] | Workday[1,14] | Workday[1,15] | Workday[1,16] | Workday[1,17] | Workday[1,18] | Workday[1,19] | Workday[1,20] | Workday[1,21] | Workday[1,22] | Workday[1,23] | Workday[1,24] | Workday[1,25] | Workday[1,26] | Workday[1,27] | Workday[1,28] | Workday[1,29] | Workday[1,30] | Workday[1,31] | Workday[1,32] | Workday[1,33] | Workday[1,34] | Workday[1,35] | Workday[1,36] | Workday[1,37] | Workday[1,38] | Workday[1,39] | Workday[1,40] | Workday[1,41] | Workday[1,42] | Workday[1,43] | Workday[1,44] | Workday[1,45] | Workday[1,46] | Workday[1,47] | Workday[1,48] | Workday[1,49] | Workday[1,50] | Workday[1,51] | Workday[1,52] | Workday[1,53] | Workday[1,54] | Workday[1,55] | Workday[1,56] | Workday[1,57] | Workday[1,58] | Workday[1,59] | Workday[1,60] | Workday[1,61] | Workday[1,62] | Workday[1,63] | Workday[1,64] | Workday[1,65] | Workday[1,66] | Workday[1,67] | Workday[1,68] | Workday[1,69] | Workday[1,70] | Workday[1,71] | Workday[1,72] | Workday[1,73] | Workday[1,74] | Workday[1,75] | Workday[1,76] | Workday[1,77] | Workday[1,78] | Workday[1,79] | Workday[1,80] | Workday[1,81] | Workday[1,82] | Workday[1,83] | Workday[1,84] | Workday[1,85] | Workday[1,86] | Workday[1,87] | Workday[1,88] | Workday[1,89] | Workday[1,90] | Workday[1,91] | Workday[1,92] | Workday[1,93] | Workday[1,94] | Workday[1,95] | Workday[1,96] | Workday[2,1] | Workday[2,2] | Workday[2,3] | Workday[2,4] | Workday[2,5] | Workday[2,6] | Workday[2,7] | Workday[2,8] | Workday[2,9] | Workday[2,10] | Workday[2,11] | Workday[2,12] | Workday[2,13] | Workday[2,14] | Workday[2,15] | Workday[2,16] | Workday[2,17] | Workday[2,18] | Workday[2,19] | Workday[2,20] | Workday[2,21] | Workday[2,22] | Workday[2,23] | Workday[2,24] | Workday[2,25] | Workday[2,26] | Workday[2,27] | Workday[2,28] | Workday[2,29] | Workday[2,30] | Workday[2,31] | Workday[2,32] | Workday[2,33] | Workday[2,34] | Workday[2,35] | Workday[2,36] | Workday[2,37] | Workday[2,38] | Workday[2,39] | Workday[2,40] | Workday[2,41] | Workday[2,42] | Workday[2,43] | Workday[2,44] | Workday[2,45] | Workday[2,46] | Workday[2,47] | Workday[2,48] | Workday[2,49] | Workday[2,50] | Workday[2,51] | Workday[2,52] | Workday[2,53] | Workday[2,54] | Workday[2,55] | Workday[2,56] | Workday[2,57] | Workday[2,58] | Workday[2,59] | Workday[2,60] | Workday[2,61] | Workday[2,62] | Workday[2,63] | Workday[2,64] | Workday[2,65] | Workday[2,66] | Workday[2,67] | Workday[2,68] | Workday[2,69] | Workday[2,70] | Workday[2,71] | Workday[2,72] | Workday[2,73] | Workday[2,74] | Workday[2,75] | Workday[2,76] | Workday[2,77] | Workday[2,78] | Workday[2,79] | Workday[2,80] | Workday[2,81] | Workday[2,82] | Workday[2,83] | Workday[2,84] | Workday[2,85] | Workday[2,86] | Workday[2,87] | Workday[2,88] | Workday[2,89] | Workday[2,90] | Workday[2,91] | Workday[2,92] | Workday[2,93] | Workday[2,94] | Workday[2,95] | Workday[2,96] | Workday[3,1] | Workday[3,2] | Workday[3,3] | Workday[3,4] | Workday[3,5] | Workday[3,6] | Workday[3,7] | Workday[3,8] | Workday[3,9] | Workday[3,10] | Workday[3,11] | Workday[3,12] | Workday[3,13] | Workday[3,14] | Workday[3,15] | Workday[3,16] | Workday[3,17] | Workday[3,18] | Workday[3,19] | Workday[3,20] | Workday[3,21] | Workday[3,22] | Workday[3,23] | Workday[3,24] | Workday[3,25] | Workday[3,26] | Workday[3,27] | Workday[3,28] | Workday[3,29] | Workday[3,30] | Workday[3,31] | Workday[3,32] | Workday[3,33] | Workday[3,34] | Workday[3,35] | Workday[3,36] | Workday[3,37] | Workday[3,38] | Workday[3,39] | Workday[3,40] | Workday[3,41] | Workday[3,42] | Workday[3,43] | Workday[3,44] | Workday[3,45] | Workday[3,46] | Workday[3,47] | Workday[3,48] | Workday[3,49] | Workday[3,50] | Workday[3,51] | Workday[3,52] | Workday[3,53] | Workday[3,54] | Workday[3,55] | Workday[3,56] | Workday[3,57] | Workday[3,58] | Workday[3,59] | Workday[3,60] | Workday[3,61] | Workday[3,62] | Workday[3,63] | Workday[3,64] | Workday[3,65] | Workday[3,66] | Workday[3,67] | Workday[3,68] | Workday[3,69] | Workday[3,70] | Workday[3,71] | Workday[3,72] | Workday[3,73] | Workday[3,74] | Workday[3,75] | Workday[3,76] | Workday[3,77] | Workday[3,78] | Workday[3,79] | Workday[3,80] | Workday[3,81] | Workday[3,82] | Workday[3,83] | Workday[3,84] | Workday[3,85] | Workday[3,86] | Workday[3,87] | Workday[3,88] | Workday[3,89] | Workday[3,90] | Workday[3,91] | Workday[3,92] | Workday[3,93] | Workday[3,94] | Workday[3,95] | Workday[3,96] | Workday[4,1] | Workday[4,2] | Workday[4,3] | Workday[4,4] | Workday[4,5] | Workday[4,6] | Workday[4,7] | Workday[4,8] | Workday[4,9] | Workday[4,10] | Workday[4,11] | Workday[4,12] | Workday[4,13] | Workday[4,14] | Workday[4,15] | Workday[4,16] | Workday[4,17] | Workday[4,18] | Workday[4,19] | Workday[4,20] | Workday[4,21] | Workday[4,22] | Workday[4,23] | Workday[4,24] | Workday[4,25] | Workday[4,26] | Workday[4,27] | Workday[4,28] | Workday[4,29] | Workday[4,30] | Workday[4,31] | Workday[4,32] | Workday[4,33] | Workday[4,34] | Workday[4,35] | Workday[4,36] | Workday[4,37] | Workday[4,38] | Workday[4,39] | Workday[4,40] | Workday[4,41] | Workday[4,42] | Workday[4,43] | Workday[4,44] | Workday[4,45] | Workday[4,46] | Workday[4,47] | Workday[4,48] | Workday[4,49] | Workday[4,50] | Workday[4,51] | Workday[4,52] | Workday[4,53] | Workday[4,54] | Workday[4,55] | Workday[4,56] | Workday[4,57] | Workday[4,58] | Workday[4,59] | Workday[4,60] | Workday[4,61] | Workday[4,62] | Workday[4,63] | Workday[4,64] | Workday[4,65] | Workday[4,66] | Workday[4,67] | Workday[4,68] | Workday[4,69] | Workday[4,70] | Workday[4,71] | Workday[4,72] | Workday[4,73] | Workday[4,74] | Workday[4,75] | Workday[4,76] | Workday[4,77] | Workday[4,78] | Workday[4,79] | Workday[4,80] | Workday[4,81] | Workday[4,82] | Workday[4,83] | Workday[4,84] | Workday[4,85] | Workday[4,86] | Workday[4,87] | Workday[4,88] | Workday[4,89] | Workday[4,90] | Workday[4,91] | Workday[4,92] | Workday[4,93] | Workday[4,94] | Workday[4,95] | Workday[4,96] | Weekend[1,1] | Weekend[1,2] | Weekend[1,3] | Weekend[1,4] | Weekend[1,5] | Weekend[1,6] | Weekend[1,7] | Weekend[1,8] | Weekend[1,9] | Weekend[1,10] | Weekend[1,11] | Weekend[1,12] | Weekend[1,13] | Weekend[1,14] | Weekend[1,15] | Weekend[1,16] | Weekend[1,17] | Weekend[1,18] | Weekend[1,19] | Weekend[1,20] | Weekend[1,21] | Weekend[1,22] | Weekend[1,23] | Weekend[1,24] | Weekend[1,25] | Weekend[1,26] | Weekend[1,27] | Weekend[1,28] | Weekend[1,29] | Weekend[1,30] | Weekend[1,31] | Weekend[1,32] | Weekend[1,33] | Weekend[1,34] | Weekend[1,35] | Weekend[1,36] | Weekend[1,37] | Weekend[1,38] | Weekend[1,39] | Weekend[1,40] | Weekend[1,41] | Weekend[1,42] | Weekend[1,43] | Weekend[1,44] | Weekend[1,45] | Weekend[1,46] | Weekend[1,47] | Weekend[1,48] | Weekend[1,49] | Weekend[1,50] | Weekend[1,51] | Weekend[1,52] | Weekend[1,53] | Weekend[1,54] | Weekend[1,55] | Weekend[1,56] | Weekend[1,57] | Weekend[1,58] | Weekend[1,59] | Weekend[1,60] | Weekend[1,61] | Weekend[1,62] | Weekend[1,63] | Weekend[1,64] | Weekend[1,65] | Weekend[1,66] | Weekend[1,67] | Weekend[1,68] | Weekend[1,69] | Weekend[1,70] | Weekend[1,71] | Weekend[1,72] | Weekend[1,73] | Weekend[1,74] | Weekend[1,75] | Weekend[1,76] | Weekend[1,77] | Weekend[1,78] | Weekend[1,79] | Weekend[1,80] | Weekend[1,81] | Weekend[1,82] | Weekend[1,83] | Weekend[1,84] | Weekend[1,85] | Weekend[1,86] | Weekend[1,87] | Weekend[1,88] | Weekend[1,89] | Weekend[1,90] | Weekend[1,91] | Weekend[1,92] | Weekend[1,93] | Weekend[1,94] | Weekend[1,95] | Weekend[1,96] | Weekend[2,1] | Weekend[2,2] | Weekend[2,3] | Weekend[2,4] | Weekend[2,5] | Weekend[2,6] | Weekend[2,7] | Weekend[2,8] | Weekend[2,9] | Weekend[2,10] | Weekend[2,11] | Weekend[2,12] | Weekend[2,13] | Weekend[2,14] | Weekend[2,15] | Weekend[2,16] | Weekend[2,17] | Weekend[2,18] | Weekend[2,19] | Weekend[2,20] | Weekend[2,21] | Weekend[2,22] | Weekend[2,23] | Weekend[2,24] | Weekend[2,25] | Weekend[2,26] | Weekend[2,27] | Weekend[2,28] | Weekend[2,29] | Weekend[2,30] | Weekend[2,31] | Weekend[2,32] | Weekend[2,33] | Weekend[2,34] | Weekend[2,35] | Weekend[2,36] | Weekend[2,37] | Weekend[2,38] | Weekend[2,39] | Weekend[2,40] | Weekend[2,41] | Weekend[2,42] | Weekend[2,43] | Weekend[2,44] | Weekend[2,45] | Weekend[2,46] | Weekend[2,47] | Weekend[2,48] | Weekend[2,49] | Weekend[2,50] | Weekend[2,51] | Weekend[2,52] | Weekend[2,53] | Weekend[2,54] | Weekend[2,55] | Weekend[2,56] | Weekend[2,57] | Weekend[2,58] | Weekend[2,59] | Weekend[2,60] | Weekend[2,61] | Weekend[2,62] | Weekend[2,63] | Weekend[2,64] | Weekend[2,65] | Weekend[2,66] | Weekend[2,67] | Weekend[2,68] | Weekend[2,69] | Weekend[2,70] | Weekend[2,71] | Weekend[2,72] | Weekend[2,73] | Weekend[2,74] | Weekend[2,75] | Weekend[2,76] | Weekend[2,77] | Weekend[2,78] | Weekend[2,79] | Weekend[2,80] | Weekend[2,81] | Weekend[2,82] | Weekend[2,83] | Weekend[2,84] | Weekend[2,85] | Weekend[2,86] | Weekend[2,87] | Weekend[2,88] | Weekend[2,89] | Weekend[2,90] | Weekend[2,91] | Weekend[2,92] | Weekend[2,93] | Weekend[2,94] | Weekend[2,95] | Weekend[2,96] | Weekend[3,1] | Weekend[3,2] | Weekend[3,3] | Weekend[3,4] | Weekend[3,5] | Weekend[3,6] | Weekend[3,7] | Weekend[3,8] | Weekend[3,9] | Weekend[3,10] | Weekend[3,11] | Weekend[3,12] | Weekend[3,13] | Weekend[3,14] | Weekend[3,15] | Weekend[3,16] | Weekend[3,17] | Weekend[3,18] | Weekend[3,19] | Weekend[3,20] | Weekend[3,21] | Weekend[3,22] | Weekend[3,23] | Weekend[3,24] | Weekend[3,25] | Weekend[3,26] | Weekend[3,27] | Weekend[3,28] | Weekend[3,29] | Weekend[3,30] | Weekend[3,31] | Weekend[3,32] | Weekend[3,33] | Weekend[3,34] | Weekend[3,35] | Weekend[3,36] | Weekend[3,37] | Weekend[3,38] | Weekend[3,39] | Weekend[3,40] | Weekend[3,41] | Weekend[3,42] | Weekend[3,43] | Weekend[3,44] | Weekend[3,45] | Weekend[3,46] | Weekend[3,47] | Weekend[3,48] | Weekend[3,49] | Weekend[3,50] | Weekend[3,51] | Weekend[3,52] | Weekend[3,53] | Weekend[3,54] | Weekend[3,55] | Weekend[3,56] | Weekend[3,57] | Weekend[3,58] | Weekend[3,59] | Weekend[3,60] | Weekend[3,61] | Weekend[3,62] | Weekend[3,63] | Weekend[3,64] | Weekend[3,65] | Weekend[3,66] | Weekend[3,67] | Weekend[3,68] | Weekend[3,69] | Weekend[3,70] | Weekend[3,71] | Weekend[3,72] | Weekend[3,73] | Weekend[3,74] | Weekend[3,75] | Weekend[3,76] | Weekend[3,77] | Weekend[3,78] | Weekend[3,79] | Weekend[3,80] | Weekend[3,81] | Weekend[3,82] | Weekend[3,83] | Weekend[3,84] | Weekend[3,85] | Weekend[3,86] | Weekend[3,87] | Weekend[3,88] | Weekend[3,89] | Weekend[3,90] | Weekend[3,91] | Weekend[3,92] | Weekend[3,93] | Weekend[3,94] | Weekend[3,95] | Weekend[3,96] | Weekend[4,1] | Weekend[4,2] | Weekend[4,3] | Weekend[4,4] | Weekend[4,5] | Weekend[4,6] | Weekend[4,7] | Weekend[4,8] | Weekend[4,9] | Weekend[4,10] | Weekend[4,11] | Weekend[4,12] | Weekend[4,13] | Weekend[4,14] | Weekend[4,15] | Weekend[4,16] | Weekend[4,17] | Weekend[4,18] | Weekend[4,19] | Weekend[4,20] | Weekend[4,21] | Weekend[4,22] | Weekend[4,23] | Weekend[4,24] | Weekend[4,25] | Weekend[4,26] | Weekend[4,27] | Weekend[4,28] | Weekend[4,29] | Weekend[4,30] | Weekend[4,31] | Weekend[4,32] | Weekend[4,33] | Weekend[4,34] | Weekend[4,35] | Weekend[4,36] | Weekend[4,37] | Weekend[4,38] | Weekend[4,39] | Weekend[4,40] | Weekend[4,41] | Weekend[4,42] | Weekend[4,43] | Weekend[4,44] | Weekend[4,45] | Weekend[4,46] | Weekend[4,47] | Weekend[4,48] | Weekend[4,49] | Weekend[4,50] | Weekend[4,51] | Weekend[4,52] | Weekend[4,53] | Weekend[4,54] | Weekend[4,55] | Weekend[4,56] | Weekend[4,57] | Weekend[4,58] | Weekend[4,59] | Weekend[4,60] | Weekend[4,61] | Weekend[4,62] | Weekend[4,63] | Weekend[4,64] | Weekend[4,65] | Weekend[4,66] | Weekend[4,67] | Weekend[4,68] | Weekend[4,69] | Weekend[4,70] | Weekend[4,71] | Weekend[4,72] | Weekend[4,73] | Weekend[4,74] | Weekend[4,75] | Weekend[4,76] | Weekend[4,77] | Weekend[4,78] | Weekend[4,79] | Weekend[4,80] | Weekend[4,81] | Weekend[4,82] | Weekend[4,83] | Weekend[4,84] | Weekend[4,85] | Weekend[4,86] | Weekend[4,87] | Weekend[4,88] | Weekend[4,89] | Weekend[4,90] | Weekend[4,91] | Weekend[4,92] | Weekend[4,93] | Weekend[4,94] | Weekend[4,95] | Weekend[4,96] | Month[1,1] | Month[1,2] | Month[1,3] | Month[1,4] | Month[1,5] | Month[1,6] | Month[1,7] | Month[1,8] | Month[1,9] | Month[1,10] | Month[1,11] | Month[1,12] | Month[2,1] | Month[2,2] | Month[2,3] | Month[2,4] | Month[2,5] | Month[2,6] | Month[2,7] | Month[2,8] | Month[2,9] | Month[2,10] | Month[2,11] | Month[2,12] | Month[3,1] | Month[3,2] | Month[3,3] | Month[3,4] | Month[3,5] | Month[3,6] | Month[3,7] | Month[3,8] | Month[3,9] | Month[3,10] | Month[3,11] | Month[3,12] | Month[4,1] | Month[4,2] | Month[4,3] | Month[4,4] | Month[4,5] | Month[4,6] | Month[4,7] | Month[4,8] | Month[4,9] | Month[4,10] | Month[4,11] | Month[4,12] | TrendWorkday[1] | TrendWorkday[2] | TrendWorkday[3] | TrendWorkday[4] | TrendWorkday[5] | TrendWorkday[6] | TrendWorkday[7] | TrendWorkday[8] | TrendWorkday[9] | TrendWorkday[10] | TrendWorkday[11] | TrendWorkday[12] | TrendWorkday[13] | TrendWorkday[14] | TrendWorkday[15] | TrendWorkday[16] | TrendWorkday[17] | TrendWorkday[18] | TrendWorkday[19] | TrendWorkday[20] | TrendWorkday[21] | TrendWorkday[22] | TrendWorkday[23] | TrendWorkday[24] | TrendWorkday[25] | TrendWorkday[26] | TrendWorkday[27] | TrendWorkday[28] | TrendWorkday[29] | TrendWorkday[30] | TrendWorkday[31] | TrendWorkday[32] | TrendWorkday[33] | TrendWorkday[34] | TrendWorkday[35] | TrendWorkday[36] | TrendWorkday[37] | TrendWorkday[38] | TrendWorkday[39] | TrendWorkday[40] | TrendWorkday[41] | TrendWorkday[42] | TrendWorkday[43] | TrendWorkday[44] | TrendWorkday[45] | TrendWorkday[46] | TrendWorkday[47] | TrendWorkday[48] | TrendWorkday[49] | TrendWorkday[50] | TrendWorkday[51] | TrendWorkday[52] | TrendWorkday[53] | TrendWorkday[54] | TrendWorkday[55] | TrendWorkday[56] | TrendWorkday[57] | TrendWorkday[58] | TrendWorkday[59] | TrendWorkday[60] | TrendWorkday[61] | TrendWorkday[62] | TrendWorkday[63] | TrendWorkday[64] | TrendWorkday[65] | TrendWorkday[66] | TrendWorkday[67] | TrendWorkday[68] | TrendWorkday[69] | TrendWorkday[70] | TrendWorkday[71] | TrendWorkday[72] | TrendWorkday[73] | TrendWorkday[74] | TrendWorkday[75] | TrendWorkday[76] | TrendWorkday[77] | TrendWorkday[78] | TrendWorkday[79] | TrendWorkday[80] | TrendWorkday[81] | TrendWorkday[82] | TrendWorkday[83] | TrendWorkday[84] | TrendWorkday[85] | TrendWorkday[86] | TrendWorkday[87] | TrendWorkday[88] | TrendWorkday[89] | TrendWorkday[90] | TrendWorkday[91] | TrendWorkday[92] | TrendWorkday[93] | TrendWorkday[94] | TrendWorkday[95] | TrendWorkday[96] | TrendWeekend[1] | TrendWeekend[2] | TrendWeekend[3] | TrendWeekend[4] | TrendWeekend[5] | TrendWeekend[6] | TrendWeekend[7] | TrendWeekend[8] | TrendWeekend[9] | TrendWeekend[10] | TrendWeekend[11] | TrendWeekend[12] | TrendWeekend[13] | TrendWeekend[14] | TrendWeekend[15] | TrendWeekend[16] | TrendWeekend[17] | TrendWeekend[18] | TrendWeekend[19] | TrendWeekend[20] | TrendWeekend[21] | TrendWeekend[22] | TrendWeekend[23] | TrendWeekend[24] | TrendWeekend[25] | TrendWeekend[26] | TrendWeekend[27] | TrendWeekend[28] | TrendWeekend[29] | TrendWeekend[30] | TrendWeekend[31] | TrendWeekend[32] | TrendWeekend[33] | TrendWeekend[34] | TrendWeekend[35] | TrendWeekend[36] | TrendWeekend[37] | TrendWeekend[38] | TrendWeekend[39] | TrendWeekend[40] | TrendWeekend[41] | TrendWeekend[42] | TrendWeekend[43] | TrendWeekend[44] | TrendWeekend[45] | TrendWeekend[46] | TrendWeekend[47] | TrendWeekend[48] | TrendWeekend[49] | TrendWeekend[50] | TrendWeekend[51] | TrendWeekend[52] | TrendWeekend[53] | TrendWeekend[54] | TrendWeekend[55] | TrendWeekend[56] | TrendWeekend[57] | TrendWeekend[58] | TrendWeekend[59] | TrendWeekend[60] | TrendWeekend[61] | TrendWeekend[62] | TrendWeekend[63] | TrendWeekend[64] | TrendWeekend[65] | TrendWeekend[66] | TrendWeekend[67] | TrendWeekend[68] | TrendWeekend[69] | TrendWeekend[70] | TrendWeekend[71] | TrendWeekend[72] | TrendWeekend[73] | TrendWeekend[74] | TrendWeekend[75] | TrendWeekend[76] | TrendWeekend[77] | TrendWeekend[78] | TrendWeekend[79] | TrendWeekend[80] | TrendWeekend[81] | TrendWeekend[82] | TrendWeekend[83] | TrendWeekend[84] | TrendWeekend[85] | TrendWeekend[86] | TrendWeekend[87] | TrendWeekend[88] | TrendWeekend[89] | TrendWeekend[90] | TrendWeekend[91] | TrendWeekend[92] | TrendWeekend[93] | TrendWeekend[94] | TrendWeekend[95] | TrendWeekend[96] | TrendMonth[1] | TrendMonth[2] | TrendMonth[3] | TrendMonth[4] | TrendMonth[5] | TrendMonth[6] | TrendMonth[7] | TrendMonth[8] | TrendMonth[9] | TrendMonth[10] | TrendMonth[11] | TrendMonth[12]
|  |  |  | kW of % | kW of % | kW of % | kW of % | kW of % | kW of % | kW of % | kW of %
Vrijstaand | 0.95 | Belasting | 0 | 0.527 | 2.176 | 0.112 | 0.286 | 0.55 | 1.28 | 0.24 | 0.363 | 0.348 | 0.34 | 0.329 | 0.323 | 0.315 | 0.309 | 0.304 | 0.299 | 0.295 | 0.291 | 0.287 | 0.284 | 0.281 | 0.279 | 0.277 | 0.276 | 0.275 | 0.275 | 0.275 | 0.275 | 0.276 | 0.282 | 0.286 | 0.29 | 0.297 | 0.306 | 0.316 | 0.325 | 0.332 | 0.341 | 0.348 | 0.352 | 0.355 | 0.355 | 0.359 | 0.359 | 0.357 | 0.357 | 0.356 | 0.357 | 0.358 | 0.36 | 0.358 | 0.356 | 0.356 | 0.357 | 0.358 | 0.358 | 0.358 | 0.358 | 0.36 | 0.36 | 0.363 | 0.362 | 0.365 | 0.366 | 0.367 | 0.367 | 0.37 | 0.372 | 0.375 | 0.377 | 0.379 | 0.384 | 0.386 | 0.391 | 0.398 | 0.403 | 0.407 | 0.412 | 0.416 | 0.423 | 0.429 | 0.435 | 0.439 | 0.446 | 0.45 | 0.452 | 0.455 | 0.46 | 0.462 | 0.465 | 0.466 | 0.467 | 0.467 | 0.465 | 0.459 | 0.452 | 0.445 | 0.436 | 0.425 | 0.412 | 0.398 | 0.387 | 0.374 | 0.362 | 0.082 | 0.077 | 0.072 | 0.068 | 0.065 | 0.062 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.055 | 0.054 | 0.054 | 0.054 | 0.054 | 0.055 | 0.055 | 0.055 | 0.056 | 0.058 | 0.063 | 0.068 | 0.07 | 0.079 | 0.09 | 0.098 | 0.105 | 0.116 | 0.127 | 0.137 | 0.141 | 0.145 | 0.15 | 0.154 | 0.156 | 0.161 | 0.163 | 0.168 | 0.17 | 0.172 | 0.173 | 0.177 | 0.178 | 0.184 | 0.184 | 0.185 | 0.184 | 0.187 | 0.188 | 0.186 | 0.186 | 0.185 | 0.181 | 0.18 | 0.179 | 0.179 | 0.181 | 0.183 | 0.185 | 0.19 | 0.195 | 0.2 | 0.203 | 0.21 | 0.22 | 0.222 | 0.228 | 0.232 | 0.234 | 0.236 | 0.234 | 0.231 | 0.227 | 0.224 | 0.218 | 0.212 | 0.208 | 0.204 | 0.197 | 0.193 | 0.19 | 0.183 | 0.176 | 0.172 | 0.169 | 0.158 | 0.149 | 0.141 | 0.136 | 0.128 | 0.119 | 0.111 | 0.104 | 0.095 | 0.088 | 0.228 | 0.239 | 0.252 | 0.26 | 0.269 | 0.275 | 0.281 | 0.287 | 0.292 | 0.297 | 0.3 | 0.303 | 0.307 | 0.309 | 0.31 | 0.311 | 0.313 | 0.312 | 0.312 | 0.313 | 0.311 | 0.302 | 0.295 | 0.289 | 0.278 | 0.262 | 0.247 | 0.234 | 0.222 | 0.208 | 0.195 | 0.187 | 0.183 | 0.179 | 0.174 | 0.172 | 0.173 | 0.171 | 0.169 | 0.166 | 0.164 | 0.163 | 0.163 | 0.164 | 0.162 | 0.16 | 0.16 | 0.16 | 0.159 | 0.158 | 0.157 | 0.157 | 0.155 | 0.157 | 0.156 | 0.154 | 0.154 | 0.153 | 0.15 | 0.147 | 0.142 | 0.138 | 0.133 | 0.129 | 0.123 | 0.116 | 0.11 | 0.104 | 0.099 | 0.094 | 0.09 | 0.087 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.078 | 0.078 | 0.076 | 0.076 | 0.075 | 0.077 | 0.078 | 0.08 | 0.083 | 0.092 | 0.102 | 0.111 | 0.123 | 0.138 | 0.152 | 0.169 | 0.183 | 0.199 | 0.213 | 0.344 | 0.346 | 0.348 | 0.35 | 0.352 | 0.354 | 0.356 | 0.357 | 0.357 | 0.358 | 0.359 | 0.359 | 0.359 | 0.36 | 0.36 | 0.36 | 0.358 | 0.359 | 0.358 | 0.358 | 0.356 | 0.354 | 0.353 | 0.352 | 0.348 | 0.343 | 0.34 | 0.337 | 0.331 | 0.326 | 0.322 | 0.321 | 0.318 | 0.317 | 0.314 | 0.314 | 0.311 | 0.311 | 0.309 | 0.308 | 0.307 | 0.305 | 0.304 | 0.303 | 0.3 | 0.299 | 0.298 | 0.299 | 0.297 | 0.297 | 0.298 | 0.298 | 0.298 | 0.301 | 0.301 | 0.302 | 0.301 | 0.301 | 0.299 | 0.297 | 0.294 | 0.291 | 0.288 | 0.286 | 0.282 | 0.274 | 0.271 | 0.267 | 0.264 | 0.261 | 0.259 | 0.257 | 0.257 | 0.255 | 0.256 | 0.258 | 0.261 | 0.264 | 0.265 | 0.269 | 0.271 | 0.271 | 0.276 | 0.28 | 0.282 | 0.284 | 0.292 | 0.298 | 0.303 | 0.306 | 0.311 | 0.318 | 0.323 | 0.327 | 0.334 | 0.339 | 0.343 | 0.332 | 0.324 | 0.317 | 0.311 | 0.307 | 0.301 | 0.297 | 0.294 | 0.289 | 0.286 | 0.284 | 0.281 | 0.278 | 0.278 | 0.276 | 0.275 | 0.275 | 0.276 | 0.275 | 0.277 | 0.282 | 0.286 | 0.292 | 0.298 | 0.308 | 0.322 | 0.331 | 0.336 | 0.348 | 0.356 | 0.359 | 0.361 | 0.362 | 0.368 | 0.366 | 0.358 | 0.356 | 0.357 | 0.358 | 0.356 | 0.356 | 0.356 | 0.351 | 0.354 | 0.353 | 0.354 | 0.354 | 0.354 | 0.355 | 0.359 | 0.358 | 0.362 | 0.363 | 0.366 | 0.365 | 0.364 | 0.368 | 0.368 | 0.372 | 0.375 | 0.375 | 0.379 | 0.382 | 0.386 | 0.389 | 0.396 | 0.406 | 0.413 | 0.419 | 0.423 | 0.427 | 0.435 | 0.439 | 0.445 | 0.454 | 0.456 | 0.458 | 0.458 | 0.466 | 0.47 | 0.473 | 0.471 | 0.471 | 0.471 | 0.467 | 0.46 | 0.456 | 0.451 | 0.44 | 0.425 | 0.413 | 0.399 | 0.384 | 0.369 | 0.355 | 0.08 | 0.076 | 0.071 | 0.069 | 0.065 | 0.062 | 0.06 | 0.058 | 0.057 | 0.056 | 0.055 | 0.054 | 0.053 | 0.053 | 0.053 | 0.053 | 0.054 | 0.055 | 0.055 | 0.056 | 0.058 | 0.063 | 0.068 | 0.072 | 0.082 | 0.092 | 0.101 | 0.111 | 0.13 | 0.14 | 0.151 | 0.15 | 0.16 | 0.158 | 0.157 | 0.152 | 0.157 | 0.161 | 0.16 | 0.16 | 0.16 | 0.157 | 0.157 | 0.162 | 0.161 | 0.167 | 0.168 | 0.174 | 0.174 | 0.174 | 0.169 | 0.168 | 0.169 | 0.163 | 0.162 | 0.163 | 0.162 | 0.165 | 0.169 | 0.171 | 0.174 | 0.186 | 0.191 | 0.201 | 0.214 | 0.224 | 0.23 | 0.228 | 0.232 | 0.236 | 0.234 | 0.234 | 0.23 | 0.226 | 0.224 | 0.215 | 0.211 | 0.211 | 0.207 | 0.199 | 0.192 | 0.191 | 0.184 | 0.178 | 0.172 | 0.17 | 0.164 | 0.151 | 0.14 | 0.134 | 0.124 | 0.115 | 0.108 | 0.101 | 0.095 | 0.089 | 0.239 | 0.249 | 0.26 | 0.268 | 0.276 | 0.28 | 0.288 | 0.293 | 0.297 | 0.302 | 0.304 | 0.308 | 0.31 | 0.313 | 0.313 | 0.316 | 0.316 | 0.315 | 0.314 | 0.315 | 0.312 | 0.305 | 0.298 | 0.289 | 0.277 | 0.261 | 0.243 | 0.228 | 0.214 | 0.198 | 0.183 | 0.178 | 0.173 | 0.17 | 0.164 | 0.168 | 0.176 | 0.175 | 0.174 | 0.175 | 0.176 | 0.176 | 0.176 | 0.177 | 0.178 | 0.175 | 0.174 | 0.17 | 0.17 | 0.169 | 0.169 | 0.17 | 0.166 | 0.167 | 0.166 | 0.166 | 0.166 | 0.162 | 0.16 | 0.154 | 0.15 | 0.146 | 0.139 | 0.131 | 0.123 | 0.119 | 0.111 | 0.104 | 0.098 | 0.091 | 0.089 | 0.087 | 0.082 | 0.082 | 0.081 | 0.078 | 0.076 | 0.074 | 0.074 | 0.075 | 0.074 | 0.073 | 0.075 | 0.077 | 0.08 | 0.084 | 0.092 | 0.103 | 0.113 | 0.124 | 0.141 | 0.158 | 0.173 | 0.19 | 0.205 | 0.221 | 0.348 | 0.35 | 0.351 | 0.353 | 0.355 | 0.357 | 0.357 | 0.357 | 0.358 | 0.36 | 0.361 | 0.361 | 0.362 | 0.362 | 0.362 | 0.361 | 0.361 | 0.361 | 0.361 | 0.361 | 0.359 | 0.356 | 0.354 | 0.353 | 0.348 | 0.345 | 0.341 | 0.337 | 0.326 | 0.32 | 0.317 | 0.319 | 0.312 | 0.316 | 0.317 | 0.32 | 0.315 | 0.315 | 0.314 | 0.314 | 0.315 | 0.317 | 0.317 | 0.317 | 0.314 | 0.311 | 0.309 | 0.308 | 0.308 | 0.307 | 0.309 | 0.311 | 0.31 | 0.313 | 0.313 | 0.312 | 0.314 | 0.312 | 0.31 | 0.309 | 0.307 | 0.3 | 0.298 | 0.292 | 0.283 | 0.275 | 0.27 | 0.269 | 0.264 | 0.26 | 0.26 | 0.258 | 0.259 | 0.26 | 0.257 | 0.259 | 0.263 | 0.264 | 0.267 | 0.267 | 0.27 | 0.27 | 0.277 | 0.28 | 0.284 | 0.285 | 0.29 | 0.296 | 0.303 | 0.309 | 0.316 | 0.321 | 0.327 | 0.331 | 0.337 | 0.341 | 1.03 | 1.005 | 0.988 | 0.966 | 0.94 | 0.937 | 0.956 | 0.964 | 0.969 | 0.987 | 1.021 | 1 | 1.003 | 0.985 | 0.972 | 0.898 | 0.837 | 0.784 | 0.744 | 0.813 | 0.879 | 0.953 | 1.028 | 1 | 0.958 | 1.006 | 1.03 | 1.094 | 1.172 | 1.189 | 1.161 | 1.128 | 1.103 | 1.05 | 0.963 | 1 | 0.985 | 0.999 | 1.013 | 1.044 | 1.065 | 1.086 | 1.1 | 1.072 | 1.044 | 1.013 | 0.981 | 1
Rijtjes en 2/1 kap | 0.95 | Belasting | 0 | 1.826 | 0.485 | 0.116 | 0.351 | 1.034 | 0.511 | 0.237 | 0.429 | 0.1 | 0.095 | 0.088 | 0.082 | 0.077 | 0.075 | 0.074 | 0.072 | 0.07 | 0.07 | 0.067 | 0.066 | 0.064 | 0.063 | 0.061 | 0.061 | 0.06 | 0.06 | 0.059 | 0.059 | 0.058 | 0.058 | 0.059 | 0.061 | 0.065 | 0.067 | 0.072 | 0.08 | 0.09 | 0.105 | 0.11 | 0.116 | 0.124 | 0.138 | 0.147 | 0.152 | 0.158 | 0.163 | 0.155 | 0.16 | 0.162 | 0.16 | 0.155 | 0.153 | 0.153 | 0.153 | 0.154 | 0.162 | 0.168 | 0.168 | 0.162 | 0.163 | 0.161 | 0.161 | 0.157 | 0.154 | 0.155 | 0.152 | 0.146 | 0.146 | 0.145 | 0.143 | 0.144 | 0.144 | 0.146 | 0.154 | 0.166 | 0.196 | 0.223 | 0.249 | 0.258 | 0.255 | 0.25 | 0.246 | 0.241 | 0.241 | 0.239 | 0.239 | 0.234 | 0.23 | 0.218 | 0.205 | 0.197 | 0.188 | 0.183 | 0.181 | 0.174 | 0.169 | 0.162 | 0.16 | 0.15 | 0.15 | 0.142 | 0.131 | 0.118 | 0.11 | 0.304 | 0.302 | 0.288 | 0.287 | 0.278 | 0.284 | 0.273 | 0.278 | 0.272 | 0.278 | 0.271 | 0.277 | 0.27 | 0.277 | 0.269 | 0.274 | 0.269 | 0.277 | 0.27 | 0.277 | 0.273 | 0.282 | 0.277 | 0.289 | 0.292 | 0.303 | 0.299 | 0.314 | 0.313 | 0.319 | 0.314 | 0.321 | 0.315 | 0.321 | 0.314 | 0.319 | 0.312 | 0.317 | 0.314 | 0.313 | 0.305 | 0.309 | 0.305 | 0.309 | 0.304 | 0.31 | 0.304 | 0.309 | 0.305 | 0.313 | 0.307 | 0.31 | 0.304 | 0.307 | 0.3 | 0.306 | 0.301 | 0.31 | 0.307 | 0.313 | 0.311 | 0.319 | 0.313 | 0.319 | 0.317 | 0.328 | 0.324 | 0.323 | 0.316 | 0.318 | 0.316 | 0.329 | 0.332 | 0.34 | 0.338 | 0.348 | 0.348 | 0.354 | 0.36 | 0.367 | 0.372 | 0.382 | 0.38 | 0.387 | 0.384 | 0.389 | 0.385 | 0.389 | 0.385 | 0.384 | 0.374 | 0.363 | 0.345 | 0.341 | 0.325 | 0.317 | 0.259 | 0.261 | 0.286 | 0.288 | 0.305 | 0.297 | 0.313 | 0.306 | 0.318 | 0.306 | 0.321 | 0.311 | 0.323 | 0.311 | 0.327 | 0.317 | 0.327 | 0.312 | 0.326 | 0.314 | 0.322 | 0.307 | 0.316 | 0.298 | 0.297 | 0.275 | 0.279 | 0.254 | 0.251 | 0.233 | 0.237 | 0.222 | 0.227 | 0.208 | 0.215 | 0.204 | 0.209 | 0.198 | 0.209 | 0.206 | 0.217 | 0.21 | 0.222 | 0.218 | 0.226 | 0.216 | 0.225 | 0.213 | 0.215 | 0.201 | 0.215 | 0.21 | 0.221 | 0.214 | 0.227 | 0.222 | 0.229 | 0.218 | 0.227 | 0.217 | 0.221 | 0.21 | 0.219 | 0.21 | 0.211 | 0.192 | 0.191 | 0.172 | 0.165 | 0.146 | 0.144 | 0.13 | 0.132 | 0.121 | 0.128 | 0.116 | 0.116 | 0.105 | 0.107 | 0.098 | 0.1 | 0.094 | 0.1 | 0.096 | 0.101 | 0.094 | 0.103 | 0.101 | 0.112 | 0.115 | 0.137 | 0.151 | 0.18 | 0.19 | 0.221 | 0.234 | 0.337 | 0.342 | 0.338 | 0.343 | 0.339 | 0.344 | 0.339 | 0.343 | 0.34 | 0.345 | 0.341 | 0.346 | 0.342 | 0.348 | 0.343 | 0.348 | 0.344 | 0.35 | 0.345 | 0.35 | 0.347 | 0.353 | 0.348 | 0.352 | 0.347 | 0.356 | 0.349 | 0.352 | 0.345 | 0.342 | 0.338 | 0.34 | 0.334 | 0.332 | 0.324 | 0.325 | 0.322 | 0.321 | 0.321 | 0.321 | 0.317 | 0.32 | 0.318 | 0.321 | 0.318 | 0.321 | 0.317 | 0.316 | 0.312 | 0.317 | 0.316 | 0.318 | 0.314 | 0.318 | 0.315 | 0.318 | 0.315 | 0.321 | 0.321 | 0.324 | 0.323 | 0.328 | 0.324 | 0.327 | 0.325 | 0.327 | 0.319 | 0.308 | 0.296 | 0.287 | 0.281 | 0.285 | 0.287 | 0.293 | 0.293 | 0.295 | 0.297 | 0.301 | 0.299 | 0.305 | 0.31 | 0.319 | 0.323 | 0.33 | 0.333 | 0.336 | 0.338 | 0.342 | 0.341 | 0.341 | 0.34 | 0.337 | 0.332 | 0.337 | 0.336 | 0.339 | 0.102 | 0.092 | 0.089 | 0.081 | 0.076 | 0.074 | 0.075 | 0.071 | 0.073 | 0.068 | 0.065 | 0.064 | 0.063 | 0.062 | 0.061 | 0.06 | 0.06 | 0.06 | 0.058 | 0.058 | 0.057 | 0.059 | 0.059 | 0.064 | 0.067 | 0.068 | 0.075 | 0.09 | 0.1 | 0.122 | 0.131 | 0.13 | 0.138 | 0.14 | 0.15 | 0.142 | 0.147 | 0.143 | 0.144 | 0.138 | 0.133 | 0.126 | 0.13 | 0.13 | 0.128 | 0.128 | 0.133 | 0.133 | 0.137 | 0.134 | 0.125 | 0.132 | 0.133 | 0.133 | 0.13 | 0.124 | 0.125 | 0.129 | 0.125 | 0.129 | 0.125 | 0.116 | 0.119 | 0.124 | 0.131 | 0.135 | 0.147 | 0.194 | 0.231 | 0.26 | 0.261 | 0.25 | 0.242 | 0.251 | 0.245 | 0.232 | 0.233 | 0.239 | 0.235 | 0.222 | 0.209 | 0.201 | 0.19 | 0.184 | 0.178 | 0.175 | 0.175 | 0.174 | 0.164 | 0.16 | 0.15 | 0.148 | 0.137 | 0.131 | 0.114 | 0.104 | 0.295 | 0.294 | 0.281 | 0.282 | 0.276 | 0.28 | 0.273 | 0.276 | 0.269 | 0.277 | 0.27 | 0.276 | 0.271 | 0.276 | 0.267 | 0.274 | 0.269 | 0.277 | 0.271 | 0.278 | 0.274 | 0.281 | 0.279 | 0.292 | 0.297 | 0.31 | 0.311 | 0.328 | 0.328 | 0.33 | 0.323 | 0.325 | 0.314 | 0.321 | 0.307 | 0.31 | 0.305 | 0.315 | 0.303 | 0.309 | 0.302 | 0.307 | 0.298 | 0.303 | 0.298 | 0.303 | 0.295 | 0.31 | 0.302 | 0.316 | 0.306 | 0.305 | 0.298 | 0.303 | 0.297 | 0.305 | 0.3 | 0.304 | 0.302 | 0.309 | 0.31 | 0.322 | 0.314 | 0.321 | 0.317 | 0.329 | 0.327 | 0.324 | 0.312 | 0.318 | 0.324 | 0.339 | 0.342 | 0.342 | 0.34 | 0.358 | 0.355 | 0.363 | 0.365 | 0.377 | 0.381 | 0.388 | 0.387 | 0.394 | 0.391 | 0.397 | 0.391 | 0.39 | 0.387 | 0.386 | 0.374 | 0.363 | 0.346 | 0.338 | 0.323 | 0.312 | 0.269 | 0.273 | 0.293 | 0.294 | 0.307 | 0.301 | 0.313 | 0.309 | 0.319 | 0.309 | 0.322 | 0.314 | 0.321 | 0.312 | 0.328 | 0.318 | 0.326 | 0.312 | 0.325 | 0.313 | 0.319 | 0.307 | 0.313 | 0.29 | 0.289 | 0.264 | 0.264 | 0.231 | 0.23 | 0.21 | 0.212 | 0.208 | 0.219 | 0.206 | 0.22 | 0.22 | 0.226 | 0.217 | 0.23 | 0.227 | 0.241 | 0.235 | 0.248 | 0.24 | 0.249 | 0.24 | 0.248 | 0.231 | 0.239 | 0.218 | 0.239 | 0.234 | 0.245 | 0.238 | 0.249 | 0.242 | 0.25 | 0.239 | 0.244 | 0.232 | 0.234 | 0.223 | 0.234 | 0.222 | 0.221 | 0.202 | 0.199 | 0.175 | 0.166 | 0.142 | 0.136 | 0.124 | 0.127 | 0.118 | 0.122 | 0.111 | 0.111 | 0.1 | 0.101 | 0.094 | 0.096 | 0.088 | 0.095 | 0.089 | 0.093 | 0.086 | 0.095 | 0.095 | 0.108 | 0.114 | 0.138 | 0.156 | 0.187 | 0.197 | 0.229 | 0.246 | 0.334 | 0.341 | 0.337 | 0.343 | 0.341 | 0.345 | 0.339 | 0.344 | 0.339 | 0.347 | 0.343 | 0.347 | 0.345 | 0.35 | 0.343 | 0.348 | 0.345 | 0.351 | 0.346 | 0.351 | 0.35 | 0.353 | 0.35 | 0.354 | 0.347 | 0.358 | 0.35 | 0.351 | 0.342 | 0.338 | 0.334 | 0.337 | 0.329 | 0.332 | 0.323 | 0.328 | 0.322 | 0.326 | 0.323 | 0.326 | 0.324 | 0.332 | 0.324 | 0.327 | 0.325 | 0.329 | 0.324 | 0.326 | 0.322 | 0.331 | 0.33 | 0.329 | 0.324 | 0.327 | 0.324 | 0.329 | 0.326 | 0.329 | 0.329 | 0.33 | 0.331 | 0.339 | 0.333 | 0.333 | 0.33 | 0.334 | 0.327 | 0.308 | 0.291 | 0.28 | 0.279 | 0.287 | 0.289 | 0.29 | 0.293 | 0.299 | 0.302 | 0.298 | 0.3 | 0.307 | 0.314 | 0.322 | 0.328 | 0.333 | 0.338 | 0.342 | 0.339 | 0.341 | 0.341 | 0.34 | 0.338 | 0.333 | 0.329 | 0.334 | 0.334 | 0.338 | 1 | 0.917 | 0.912 | 0.8 | 0.755 | 0.688 | 0.703 | 0.71 | 0.728 | 0.808 | 0.892 | 0.972 | 1 | 0.995 | 0.98 | 0.952 | 0.936 | 0.917 | 0.921 | 0.928 | 0.96 | 0.975 | 0.99 | 1.003 | 1 | 1.06 | 1.102 | 1.235 | 1.293 | 1.371 | 1.342 | 1.325 | 1.251 | 1.171 | 1.088 | 1.019 | 1 | 1.014 | 1.008 | 1.021 | 1.028 | 1.037 | 1.042 | 1.041 | 1.041 | 1.028 | 1.016 | 1
Hoogbouw | 0.95 | Belasting | 0 | 0.221 | 0.919 | 0.069 | 0.303 | 0.37 | 0.773 | 0.211 | 0.504 | 0.312 | 0.312 | 0.312 | 0.313 | 0.313 | 0.313 | 0.313 | 0.313 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.313 | 0.313 | 0.313 | 0.313 | 0.312 | 0.312 | 0.312 | 0.311 | 0.31 | 0.31 | 0.309 | 0.308 | 0.308 | 0.307 | 0.306 | 0.306 | 0.305 | 0.305 | 0.304 | 0.304 | 0.304 | 0.304 | 0.303 | 0.303 | 0.303 | 0.303 | 0.303 | 0.303 | 0.303 | 0.303 | 0.303 | 0.303 | 0.304 | 0.304 | 0.304 | 0.304 | 0.304 | 0.305 | 0.305 | 0.304 | 0.304 | 0.303 | 0.303 | 0.301 | 0.3 | 0.298 | 0.297 | 0.295 | 0.293 | 0.293 | 0.292 | 0.291 | 0.291 | 0.291 | 0.292 | 0.293 | 0.294 | 0.296 | 0.298 | 0.3 | 0.301 | 0.303 | 0.305 | 0.306 | 0.308 | 0.309 | 0.31 | 0.311 | 0.312 | 0.313 | 0.313 | 0.314 | 0.314 | 0.313 | 0.312 | 0.312 | 0.13 | 0.126 | 0.122 | 0.119 | 0.115 | 0.113 | 0.111 | 0.11 | 0.108 | 0.107 | 0.106 | 0.105 | 0.105 | 0.105 | 0.105 | 0.106 | 0.107 | 0.108 | 0.109 | 0.112 | 0.115 | 0.119 | 0.122 | 0.128 | 0.133 | 0.137 | 0.141 | 0.146 | 0.151 | 0.154 | 0.157 | 0.159 | 0.162 | 0.163 | 0.164 | 0.164 | 0.165 | 0.165 | 0.165 | 0.166 | 0.166 | 0.166 | 0.166 | 0.167 | 0.168 | 0.168 | 0.169 | 0.169 | 0.169 | 0.169 | 0.169 | 0.168 | 0.168 | 0.167 | 0.166 | 0.166 | 0.166 | 0.167 | 0.168 | 0.17 | 0.173 | 0.177 | 0.18 | 0.186 | 0.192 | 0.198 | 0.203 | 0.209 | 0.215 | 0.218 | 0.222 | 0.225 | 0.227 | 0.227 | 0.227 | 0.225 | 0.224 | 0.221 | 0.219 | 0.216 | 0.213 | 0.209 | 0.205 | 0.2 | 0.196 | 0.19 | 0.184 | 0.177 | 0.171 | 0.163 | 0.156 | 0.15 | 0.143 | 0.141 | 0.139 | 0.139 | 0.241 | 0.246 | 0.251 | 0.255 | 0.259 | 0.262 | 0.264 | 0.266 | 0.268 | 0.269 | 0.271 | 0.271 | 0.272 | 0.272 | 0.272 | 0.27 | 0.269 | 0.267 | 0.265 | 0.261 | 0.257 | 0.252 | 0.247 | 0.24 | 0.233 | 0.227 | 0.221 | 0.216 | 0.211 | 0.208 | 0.204 | 0.203 | 0.201 | 0.201 | 0.201 | 0.201 | 0.201 | 0.202 | 0.202 | 0.203 | 0.203 | 0.203 | 0.204 | 0.203 | 0.203 | 0.202 | 0.202 | 0.202 | 0.201 | 0.201 | 0.201 | 0.202 | 0.202 | 0.202 | 0.202 | 0.202 | 0.201 | 0.2 | 0.198 | 0.196 | 0.193 | 0.189 | 0.185 | 0.18 | 0.175 | 0.17 | 0.165 | 0.16 | 0.155 | 0.152 | 0.149 | 0.146 | 0.144 | 0.142 | 0.141 | 0.14 | 0.14 | 0.139 | 0.139 | 0.14 | 0.14 | 0.142 | 0.143 | 0.146 | 0.149 | 0.155 | 0.161 | 0.169 | 0.176 | 0.186 | 0.195 | 0.204 | 0.213 | 0.22 | 0.228 | 0.228 | 0.32 | 0.319 | 0.317 | 0.316 | 0.315 | 0.315 | 0.314 | 0.314 | 0.313 | 0.313 | 0.313 | 0.313 | 0.313 | 0.313 | 0.313 | 0.313 | 0.313 | 0.314 | 0.315 | 0.316 | 0.317 | 0.319 | 0.321 | 0.323 | 0.325 | 0.326 | 0.328 | 0.33 | 0.331 | 0.332 | 0.332 | 0.332 | 0.333 | 0.332 | 0.332 | 0.332 | 0.331 | 0.331 | 0.33 | 0.33 | 0.33 | 0.33 | 0.329 | 0.329 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.331 | 0.331 | 0.332 | 0.332 | 0.333 | 0.334 | 0.335 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.339 | 0.34 | 0.34 | 0.341 | 0.341 | 0.342 | 0.343 | 0.344 | 0.345 | 0.346 | 0.347 | 0.348 | 0.349 | 0.35 | 0.35 | 0.35 | 0.35 | 0.349 | 0.347 | 0.346 | 0.344 | 0.341 | 0.338 | 0.335 | 0.332 | 0.329 | 0.325 | 0.325 | 0.313 | 0.313 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.315 | 0.314 | 0.314 | 0.314 | 0.315 | 0.315 | 0.314 | 0.314 | 0.314 | 0.314 | 0.314 | 0.313 | 0.313 | 0.312 | 0.312 | 0.311 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.309 | 0.309 | 0.309 | 0.309 | 0.309 | 0.309 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308 | 0.309 | 0.309 | 0.309 | 0.309 | 0.309 | 0.309 | 0.309 | 0.308 | 0.308 | 0.307 | 0.306 | 0.305 | 0.303 | 0.301 | 0.3 | 0.298 | 0.296 | 0.296 | 0.295 | 0.294 | 0.293 | 0.293 | 0.294 | 0.295 | 0.296 | 0.297 | 0.299 | 0.301 | 0.303 | 0.304 | 0.306 | 0.307 | 0.309 | 0.31 | 0.312 | 0.313 | 0.314 | 0.314 | 0.315 | 0.316 | 0.316 | 0.315 | 0.313 | 0.313 | 0.13 | 0.126 | 0.122 | 0.119 | 0.116 | 0.115 | 0.113 | 0.111 | 0.11 | 0.109 | 0.108 | 0.108 | 0.107 | 0.108 | 0.108 | 0.109 | 0.11 | 0.111 | 0.113 | 0.117 | 0.12 | 0.125 | 0.13 | 0.137 | 0.143 | 0.148 | 0.152 | 0.157 | 0.161 | 0.163 | 0.164 | 0.164 | 0.164 | 0.163 | 0.162 | 0.161 | 0.16 | 0.16 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.16 | 0.16 | 0.16 | 0.16 | 0.161 | 0.161 | 0.16 | 0.16 | 0.159 | 0.159 | 0.159 | 0.159 | 0.159 | 0.16 | 0.162 | 0.164 | 0.167 | 0.172 | 0.177 | 0.183 | 0.19 | 0.197 | 0.204 | 0.211 | 0.218 | 0.222 | 0.225 | 0.229 | 0.232 | 0.233 | 0.233 | 0.232 | 0.231 | 0.229 | 0.226 | 0.223 | 0.22 | 0.217 | 0.213 | 0.208 | 0.203 | 0.196 | 0.189 | 0.182 | 0.175 | 0.167 | 0.159 | 0.151 | 0.144 | 0.142 | 0.139 | 0.139 | 0.248 | 0.253 | 0.258 | 0.262 | 0.265 | 0.268 | 0.27 | 0.272 | 0.273 | 0.274 | 0.275 | 0.276 | 0.276 | 0.276 | 0.276 | 0.274 | 0.273 | 0.27 | 0.267 | 0.262 | 0.257 | 0.251 | 0.244 | 0.236 | 0.227 | 0.222 | 0.216 | 0.211 | 0.207 | 0.205 | 0.203 | 0.204 | 0.204 | 0.207 | 0.209 | 0.21 | 0.212 | 0.213 | 0.214 | 0.215 | 0.216 | 0.216 | 0.216 | 0.216 | 0.215 | 0.215 | 0.215 | 0.214 | 0.213 | 0.213 | 0.213 | 0.214 | 0.214 | 0.214 | 0.214 | 0.214 | 0.214 | 0.212 | 0.21 | 0.206 | 0.203 | 0.198 | 0.193 | 0.187 | 0.18 | 0.175 | 0.169 | 0.163 | 0.158 | 0.154 | 0.15 | 0.147 | 0.144 | 0.142 | 0.14 | 0.139 | 0.138 | 0.138 | 0.137 | 0.137 | 0.137 | 0.139 | 0.141 | 0.144 | 0.147 | 0.154 | 0.161 | 0.169 | 0.178 | 0.188 | 0.199 | 0.209 | 0.219 | 0.227 | 0.234 | 0.234 | 0.323 | 0.321 | 0.32 | 0.319 | 0.318 | 0.318 | 0.317 | 0.317 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.317 | 0.317 | 0.318 | 0.319 | 0.321 | 0.322 | 0.324 | 0.326 | 0.329 | 0.331 | 0.333 | 0.334 | 0.335 | 0.336 | 0.336 | 0.336 | 0.336 | 0.336 | 0.335 | 0.334 | 0.334 | 0.333 | 0.333 | 0.332 | 0.332 | 0.331 | 0.331 | 0.331 | 0.331 | 0.331 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.332 | 0.333 | 0.333 | 0.334 | 0.335 | 0.336 | 0.337 | 0.338 | 0.339 | 0.34 | 0.341 | 0.342 | 0.342 | 0.342 | 0.343 | 0.344 | 0.345 | 0.345 | 0.346 | 0.347 | 0.348 | 0.349 | 0.35 | 0.351 | 0.353 | 0.354 | 0.354 | 0.355 | 0.355 | 0.355 | 0.353 | 0.352 | 0.35 | 0.348 | 0.345 | 0.342 | 0.338 | 0.335 | 0.331 | 0.327 | 0.327 | 0.999 | 0.995 | 0.996 | 1.036 | 1.044 | 1.052 | 1.064 | 1.061 | 1.043 | 1.03 | 1.009 | 1 | 1.004 | 1.014 | 1.004 | 0.816 | 0.773 | 0.735 | 0.7 | 0.7 | 0.785 | 0.86 | 0.958 | 1 | 1.004 | 1.005 | 1.014 | 1.122 | 1.152 | 1.176 | 1.18 | 1.195 | 1.138 | 1.08 | 1.025 | 1 | 0.997 | 0.994 | 0.993 | 0.998 | 0.997 | 0.996 | 1.002 | 0.997 | 0.999 | 1.003 | 1 | 1
Hoog | 0.95 | Belasting | 0 | 1.43 | 2.98 | 0.89 | 0.61 | 0.894 | 1.158 | 0.656 | 0.346 | 0.224 | 0.218 | 0.209 | 0.202 | 0.196 | 0.192 | 0.189 | 0.186 | 0.183 | 0.181 | 0.177 | 0.175 | 0.173 | 0.171 | 0.169 | 0.169 | 0.168 | 0.168 | 0.167 | 0.167 | 0.167 | 0.17 | 0.173 | 0.176 | 0.181 | 0.187 | 0.194 | 0.202 | 0.211 | 0.223 | 0.229 | 0.234 | 0.24 | 0.247 | 0.253 | 0.255 | 0.257 | 0.26 | 0.256 | 0.259 | 0.26 | 0.26 | 0.256 | 0.255 | 0.254 | 0.255 | 0.256 | 0.26 | 0.263 | 0.263 | 0.261 | 0.261 | 0.262 | 0.262 | 0.261 | 0.26 | 0.261 | 0.259 | 0.258 | 0.259 | 0.26 | 0.26 | 0.262 | 0.264 | 0.266 | 0.272 | 0.282 | 0.3 | 0.315 | 0.331 | 0.337 | 0.339 | 0.339 | 0.341 | 0.34 | 0.344 | 0.345 | 0.346 | 0.344 | 0.345 | 0.34 | 0.335 | 0.331 | 0.328 | 0.325 | 0.323 | 0.317 | 0.31 | 0.304 | 0.298 | 0.287 | 0.281 | 0.27 | 0.259 | 0.246 | 0.236 | 0.193 | 0.189 | 0.18 | 0.178 | 0.172 | 0.173 | 0.167 | 0.168 | 0.165 | 0.167 | 0.163 | 0.166 | 0.162 | 0.165 | 0.161 | 0.164 | 0.162 | 0.166 | 0.163 | 0.167 | 0.166 | 0.172 | 0.172 | 0.18 | 0.186 | 0.196 | 0.199 | 0.21 | 0.215 | 0.223 | 0.226 | 0.231 | 0.23 | 0.236 | 0.234 | 0.238 | 0.236 | 0.24 | 0.241 | 0.242 | 0.238 | 0.241 | 0.241 | 0.243 | 0.244 | 0.247 | 0.245 | 0.246 | 0.246 | 0.251 | 0.246 | 0.248 | 0.244 | 0.244 | 0.24 | 0.242 | 0.24 | 0.245 | 0.245 | 0.249 | 0.25 | 0.257 | 0.256 | 0.261 | 0.263 | 0.274 | 0.273 | 0.276 | 0.274 | 0.276 | 0.276 | 0.282 | 0.281 | 0.284 | 0.281 | 0.283 | 0.28 | 0.281 | 0.282 | 0.282 | 0.282 | 0.286 | 0.281 | 0.281 | 0.278 | 0.279 | 0.272 | 0.269 | 0.263 | 0.26 | 0.251 | 0.241 | 0.228 | 0.223 | 0.21 | 0.202 | 0.243 | 0.25 | 0.269 | 0.274 | 0.287 | 0.286 | 0.297 | 0.297 | 0.305 | 0.302 | 0.31 | 0.307 | 0.315 | 0.31 | 0.318 | 0.314 | 0.32 | 0.312 | 0.319 | 0.313 | 0.316 | 0.305 | 0.305 | 0.293 | 0.287 | 0.268 | 0.263 | 0.244 | 0.237 | 0.221 | 0.216 | 0.205 | 0.205 | 0.194 | 0.194 | 0.188 | 0.191 | 0.185 | 0.189 | 0.186 | 0.19 | 0.187 | 0.192 | 0.191 | 0.194 | 0.188 | 0.193 | 0.186 | 0.187 | 0.18 | 0.186 | 0.183 | 0.188 | 0.186 | 0.192 | 0.188 | 0.192 | 0.185 | 0.188 | 0.182 | 0.182 | 0.174 | 0.176 | 0.169 | 0.167 | 0.154 | 0.151 | 0.138 | 0.132 | 0.12 | 0.117 | 0.109 | 0.108 | 0.102 | 0.104 | 0.097 | 0.097 | 0.091 | 0.092 | 0.087 | 0.088 | 0.084 | 0.088 | 0.087 | 0.09 | 0.088 | 0.097 | 0.102 | 0.112 | 0.119 | 0.137 | 0.152 | 0.175 | 0.187 | 0.21 | 0.224 | 0.341 | 0.344 | 0.343 | 0.347 | 0.346 | 0.349 | 0.347 | 0.35 | 0.349 | 0.352 | 0.35 | 0.353 | 0.351 | 0.354 | 0.352 | 0.354 | 0.351 | 0.355 | 0.352 | 0.354 | 0.352 | 0.354 | 0.35 | 0.352 | 0.347 | 0.349 | 0.344 | 0.344 | 0.338 | 0.334 | 0.33 | 0.331 | 0.326 | 0.325 | 0.319 | 0.32 | 0.316 | 0.316 | 0.315 | 0.314 | 0.312 | 0.312 | 0.311 | 0.312 | 0.309 | 0.31 | 0.308 | 0.308 | 0.305 | 0.307 | 0.307 | 0.308 | 0.306 | 0.309 | 0.308 | 0.31 | 0.308 | 0.311 | 0.31 | 0.31 | 0.309 | 0.31 | 0.306 | 0.307 | 0.304 | 0.3 | 0.295 | 0.287 | 0.28 | 0.274 | 0.27 | 0.271 | 0.272 | 0.274 | 0.275 | 0.276 | 0.279 | 0.282 | 0.282 | 0.287 | 0.29 | 0.295 | 0.3 | 0.305 | 0.307 | 0.31 | 0.315 | 0.32 | 0.322 | 0.324 | 0.325 | 0.327 | 0.328 | 0.332 | 0.335 | 0.339 | 0.222 | 0.212 | 0.206 | 0.199 | 0.194 | 0.191 | 0.188 | 0.184 | 0.184 | 0.179 | 0.176 | 0.174 | 0.172 | 0.17 | 0.17 | 0.168 | 0.168 | 0.168 | 0.167 | 0.166 | 0.167 | 0.171 | 0.172 | 0.178 | 0.183 | 0.188 | 0.199 | 0.211 | 0.218 | 0.235 | 0.243 | 0.244 | 0.25 | 0.251 | 0.259 | 0.254 | 0.252 | 0.249 | 0.251 | 0.248 | 0.244 | 0.241 | 0.243 | 0.241 | 0.241 | 0.241 | 0.244 | 0.244 | 0.246 | 0.245 | 0.242 | 0.245 | 0.247 | 0.248 | 0.248 | 0.245 | 0.245 | 0.248 | 0.246 | 0.251 | 0.25 | 0.245 | 0.249 | 0.253 | 0.258 | 0.262 | 0.271 | 0.3 | 0.322 | 0.339 | 0.342 | 0.339 | 0.338 | 0.345 | 0.345 | 0.343 | 0.344 | 0.348 | 0.346 | 0.344 | 0.339 | 0.337 | 0.331 | 0.327 | 0.324 | 0.321 | 0.317 | 0.315 | 0.307 | 0.3 | 0.287 | 0.281 | 0.268 | 0.258 | 0.242 | 0.23 | 0.187 | 0.185 | 0.176 | 0.176 | 0.17 | 0.171 | 0.167 | 0.167 | 0.163 | 0.166 | 0.163 | 0.165 | 0.162 | 0.165 | 0.16 | 0.164 | 0.162 | 0.166 | 0.163 | 0.167 | 0.166 | 0.172 | 0.173 | 0.182 | 0.19 | 0.201 | 0.206 | 0.219 | 0.229 | 0.235 | 0.237 | 0.237 | 0.237 | 0.24 | 0.232 | 0.231 | 0.231 | 0.238 | 0.232 | 0.235 | 0.231 | 0.232 | 0.228 | 0.232 | 0.23 | 0.235 | 0.232 | 0.242 | 0.238 | 0.245 | 0.238 | 0.236 | 0.234 | 0.233 | 0.23 | 0.234 | 0.231 | 0.234 | 0.235 | 0.24 | 0.242 | 0.254 | 0.252 | 0.261 | 0.266 | 0.276 | 0.278 | 0.276 | 0.272 | 0.277 | 0.279 | 0.287 | 0.286 | 0.284 | 0.282 | 0.287 | 0.283 | 0.287 | 0.286 | 0.288 | 0.287 | 0.29 | 0.285 | 0.286 | 0.282 | 0.284 | 0.278 | 0.271 | 0.264 | 0.26 | 0.249 | 0.239 | 0.227 | 0.22 | 0.209 | 0.201 | 0.254 | 0.261 | 0.276 | 0.281 | 0.291 | 0.291 | 0.301 | 0.301 | 0.308 | 0.305 | 0.313 | 0.311 | 0.316 | 0.313 | 0.321 | 0.317 | 0.321 | 0.313 | 0.32 | 0.314 | 0.316 | 0.306 | 0.306 | 0.29 | 0.283 | 0.263 | 0.253 | 0.229 | 0.222 | 0.204 | 0.197 | 0.193 | 0.196 | 0.188 | 0.192 | 0.194 | 0.201 | 0.196 | 0.202 | 0.201 | 0.209 | 0.205 | 0.212 | 0.209 | 0.213 | 0.208 | 0.211 | 0.201 | 0.205 | 0.194 | 0.204 | 0.202 | 0.205 | 0.202 | 0.207 | 0.204 | 0.208 | 0.2 | 0.202 | 0.193 | 0.192 | 0.184 | 0.186 | 0.176 | 0.172 | 0.161 | 0.155 | 0.139 | 0.132 | 0.117 | 0.113 | 0.105 | 0.105 | 0.1 | 0.101 | 0.095 | 0.093 | 0.087 | 0.087 | 0.084 | 0.085 | 0.08 | 0.085 | 0.083 | 0.086 | 0.085 | 0.094 | 0.099 | 0.111 | 0.119 | 0.14 | 0.157 | 0.18 | 0.194 | 0.217 | 0.233 | 0.341 | 0.345 | 0.344 | 0.348 | 0.348 | 0.351 | 0.348 | 0.351 | 0.349 | 0.353 | 0.352 | 0.354 | 0.353 | 0.356 | 0.353 | 0.354 | 0.353 | 0.356 | 0.353 | 0.356 | 0.354 | 0.355 | 0.352 | 0.353 | 0.348 | 0.351 | 0.346 | 0.344 | 0.334 | 0.329 | 0.326 | 0.328 | 0.32 | 0.324 | 0.32 | 0.324 | 0.319 | 0.32 | 0.319 | 0.32 | 0.319 | 0.324 | 0.321 | 0.322 | 0.32 | 0.32 | 0.317 | 0.317 | 0.315 | 0.319 | 0.319 | 0.32 | 0.317 | 0.32 | 0.318 | 0.32 | 0.32 | 0.32 | 0.319 | 0.319 | 0.319 | 0.319 | 0.315 | 0.313 | 0.307 | 0.304 | 0.299 | 0.288 | 0.278 | 0.27 | 0.269 | 0.273 | 0.274 | 0.275 | 0.275 | 0.279 | 0.282 | 0.281 | 0.284 | 0.287 | 0.292 | 0.296 | 0.302 | 0.306 | 0.311 | 0.314 | 0.314 | 0.318 | 0.322 | 0.325 | 0.327 | 0.327 | 0.328 | 0.332 | 0.336 | 0.339 | 1.015 | 0.961 | 0.95 | 0.883 | 0.847 | 0.812 | 0.829 | 0.837 | 0.849 | 0.898 | 0.956 | 0.986 | 1.001 | 0.99 | 0.976 | 0.925 | 0.886 | 0.851 | 0.833 | 0.87 | 0.92 | 0.964 | 1.009 | 1.001 | 0.979 | 1.033 | 1.066 | 1.164 | 1.232 | 1.28 | 1.252 | 1.227 | 1.177 | 1.111 | 1.026 | 1.009 | 0.992 | 1.007 | 1.011 | 1.032 | 1.046 | 1.062 | 1.071 | 1.056 | 1.042 | 1.021 | 0.999 | 1
Laag | 0.95 | Belasting | 0 | 0.42 | 0.3 | 0.08 | 0.04 | 0.548 | 0.447 | 0.224 | 0.141 | 0.206 | 0.204 | 0.2 | 0.197 | 0.195 | 0.194 | 0.194 | 0.193 | 0.192 | 0.192 | 0.19 | 0.19 | 0.189 | 0.188 | 0.188 | 0.187 | 0.187 | 0.187 | 0.187 | 0.186 | 0.186 | 0.186 | 0.186 | 0.187 | 0.188 | 0.19 | 0.192 | 0.195 | 0.2 | 0.208 | 0.21 | 0.212 | 0.216 | 0.223 | 0.227 | 0.229 | 0.232 | 0.234 | 0.23 | 0.232 | 0.233 | 0.232 | 0.229 | 0.228 | 0.228 | 0.228 | 0.228 | 0.233 | 0.235 | 0.235 | 0.232 | 0.233 | 0.232 | 0.233 | 0.231 | 0.229 | 0.23 | 0.228 | 0.225 | 0.225 | 0.225 | 0.223 | 0.223 | 0.222 | 0.223 | 0.226 | 0.231 | 0.246 | 0.258 | 0.271 | 0.275 | 0.273 | 0.27 | 0.269 | 0.266 | 0.267 | 0.267 | 0.268 | 0.266 | 0.265 | 0.259 | 0.254 | 0.251 | 0.247 | 0.245 | 0.245 | 0.242 | 0.24 | 0.237 | 0.236 | 0.232 | 0.232 | 0.228 | 0.222 | 0.215 | 0.211 | 0.217 | 0.214 | 0.205 | 0.203 | 0.197 | 0.198 | 0.192 | 0.194 | 0.19 | 0.193 | 0.189 | 0.191 | 0.188 | 0.191 | 0.187 | 0.19 | 0.188 | 0.193 | 0.189 | 0.195 | 0.194 | 0.2 | 0.2 | 0.208 | 0.213 | 0.22 | 0.22 | 0.23 | 0.232 | 0.236 | 0.236 | 0.24 | 0.238 | 0.242 | 0.239 | 0.242 | 0.238 | 0.241 | 0.24 | 0.239 | 0.235 | 0.238 | 0.236 | 0.238 | 0.236 | 0.239 | 0.236 | 0.239 | 0.237 | 0.241 | 0.238 | 0.239 | 0.236 | 0.237 | 0.233 | 0.236 | 0.234 | 0.238 | 0.237 | 0.242 | 0.242 | 0.248 | 0.246 | 0.253 | 0.254 | 0.263 | 0.264 | 0.266 | 0.265 | 0.268 | 0.269 | 0.277 | 0.28 | 0.284 | 0.283 | 0.286 | 0.286 | 0.288 | 0.289 | 0.291 | 0.292 | 0.295 | 0.293 | 0.294 | 0.29 | 0.29 | 0.285 | 0.283 | 0.278 | 0.274 | 0.265 | 0.256 | 0.244 | 0.241 | 0.232 | 0.228 | 0.25 | 0.253 | 0.268 | 0.272 | 0.282 | 0.279 | 0.289 | 0.286 | 0.293 | 0.288 | 0.296 | 0.291 | 0.297 | 0.291 | 0.299 | 0.294 | 0.298 | 0.29 | 0.296 | 0.287 | 0.29 | 0.279 | 0.282 | 0.269 | 0.265 | 0.251 | 0.25 | 0.235 | 0.231 | 0.22 | 0.221 | 0.212 | 0.214 | 0.204 | 0.208 | 0.203 | 0.205 | 0.2 | 0.206 | 0.204 | 0.21 | 0.207 | 0.213 | 0.211 | 0.214 | 0.209 | 0.214 | 0.207 | 0.208 | 0.201 | 0.208 | 0.206 | 0.211 | 0.208 | 0.215 | 0.212 | 0.215 | 0.209 | 0.212 | 0.206 | 0.207 | 0.199 | 0.202 | 0.195 | 0.193 | 0.181 | 0.178 | 0.166 | 0.16 | 0.149 | 0.146 | 0.138 | 0.138 | 0.132 | 0.134 | 0.128 | 0.128 | 0.122 | 0.123 | 0.119 | 0.12 | 0.118 | 0.122 | 0.121 | 0.125 | 0.125 | 0.132 | 0.135 | 0.144 | 0.151 | 0.166 | 0.178 | 0.197 | 0.205 | 0.225 | 0.231 | 0.329 | 0.33 | 0.328 | 0.33 | 0.327 | 0.33 | 0.327 | 0.328 | 0.326 | 0.329 | 0.327 | 0.329 | 0.327 | 0.331 | 0.328 | 0.33 | 0.329 | 0.332 | 0.33 | 0.333 | 0.332 | 0.336 | 0.334 | 0.337 | 0.336 | 0.341 | 0.339 | 0.341 | 0.338 | 0.337 | 0.335 | 0.336 | 0.333 | 0.332 | 0.328 | 0.329 | 0.326 | 0.326 | 0.326 | 0.325 | 0.323 | 0.325 | 0.324 | 0.325 | 0.324 | 0.325 | 0.323 | 0.323 | 0.321 | 0.324 | 0.323 | 0.324 | 0.322 | 0.324 | 0.322 | 0.324 | 0.323 | 0.326 | 0.326 | 0.328 | 0.328 | 0.331 | 0.33 | 0.332 | 0.331 | 0.332 | 0.328 | 0.323 | 0.317 | 0.313 | 0.311 | 0.313 | 0.314 | 0.317 | 0.318 | 0.319 | 0.321 | 0.324 | 0.323 | 0.327 | 0.33 | 0.334 | 0.337 | 0.34 | 0.341 | 0.342 | 0.343 | 0.344 | 0.342 | 0.341 | 0.339 | 0.336 | 0.332 | 0.333 | 0.33 | 0.332 | 0.207 | 0.203 | 0.201 | 0.197 | 0.195 | 0.194 | 0.195 | 0.192 | 0.194 | 0.191 | 0.19 | 0.189 | 0.189 | 0.188 | 0.188 | 0.187 | 0.187 | 0.187 | 0.186 | 0.186 | 0.186 | 0.187 | 0.186 | 0.189 | 0.19 | 0.19 | 0.194 | 0.201 | 0.205 | 0.216 | 0.221 | 0.22 | 0.224 | 0.225 | 0.23 | 0.225 | 0.228 | 0.226 | 0.226 | 0.223 | 0.22 | 0.217 | 0.219 | 0.219 | 0.218 | 0.218 | 0.221 | 0.221 | 0.223 | 0.221 | 0.217 | 0.22 | 0.221 | 0.221 | 0.219 | 0.217 | 0.217 | 0.219 | 0.217 | 0.219 | 0.216 | 0.211 | 0.213 | 0.215 | 0.217 | 0.218 | 0.223 | 0.246 | 0.264 | 0.278 | 0.278 | 0.272 | 0.267 | 0.272 | 0.27 | 0.264 | 0.264 | 0.268 | 0.267 | 0.262 | 0.256 | 0.253 | 0.248 | 0.246 | 0.243 | 0.243 | 0.244 | 0.244 | 0.239 | 0.237 | 0.232 | 0.232 | 0.227 | 0.223 | 0.214 | 0.209 | 0.213 | 0.21 | 0.202 | 0.201 | 0.196 | 0.197 | 0.193 | 0.194 | 0.189 | 0.193 | 0.189 | 0.192 | 0.189 | 0.192 | 0.188 | 0.192 | 0.189 | 0.194 | 0.192 | 0.197 | 0.197 | 0.203 | 0.204 | 0.215 | 0.22 | 0.229 | 0.232 | 0.242 | 0.245 | 0.246 | 0.243 | 0.245 | 0.239 | 0.242 | 0.234 | 0.235 | 0.233 | 0.237 | 0.231 | 0.234 | 0.23 | 0.233 | 0.228 | 0.231 | 0.229 | 0.231 | 0.227 | 0.235 | 0.231 | 0.238 | 0.233 | 0.232 | 0.229 | 0.231 | 0.228 | 0.232 | 0.229 | 0.232 | 0.232 | 0.237 | 0.238 | 0.247 | 0.245 | 0.252 | 0.254 | 0.263 | 0.265 | 0.267 | 0.265 | 0.27 | 0.275 | 0.284 | 0.287 | 0.287 | 0.287 | 0.295 | 0.293 | 0.296 | 0.295 | 0.3 | 0.301 | 0.303 | 0.3 | 0.301 | 0.297 | 0.297 | 0.29 | 0.286 | 0.281 | 0.276 | 0.267 | 0.257 | 0.245 | 0.24 | 0.231 | 0.226 | 0.259 | 0.263 | 0.275 | 0.278 | 0.286 | 0.284 | 0.291 | 0.29 | 0.296 | 0.291 | 0.299 | 0.295 | 0.299 | 0.294 | 0.302 | 0.296 | 0.299 | 0.291 | 0.296 | 0.287 | 0.288 | 0.279 | 0.279 | 0.263 | 0.258 | 0.243 | 0.24 | 0.221 | 0.218 | 0.208 | 0.208 | 0.206 | 0.212 | 0.207 | 0.215 | 0.215 | 0.219 | 0.215 | 0.222 | 0.221 | 0.229 | 0.225 | 0.232 | 0.228 | 0.232 | 0.227 | 0.231 | 0.223 | 0.226 | 0.216 | 0.226 | 0.224 | 0.23 | 0.226 | 0.232 | 0.228 | 0.232 | 0.225 | 0.227 | 0.219 | 0.219 | 0.21 | 0.213 | 0.204 | 0.201 | 0.189 | 0.184 | 0.169 | 0.162 | 0.148 | 0.143 | 0.135 | 0.135 | 0.13 | 0.131 | 0.125 | 0.124 | 0.119 | 0.119 | 0.116 | 0.116 | 0.114 | 0.118 | 0.117 | 0.12 | 0.12 | 0.128 | 0.132 | 0.143 | 0.151 | 0.169 | 0.182 | 0.203 | 0.212 | 0.232 | 0.24 | 0.328 | 0.331 | 0.329 | 0.331 | 0.33 | 0.331 | 0.328 | 0.331 | 0.328 | 0.331 | 0.329 | 0.332 | 0.33 | 0.333 | 0.33 | 0.332 | 0.331 | 0.334 | 0.332 | 0.336 | 0.336 | 0.339 | 0.338 | 0.341 | 0.339 | 0.345 | 0.342 | 0.343 | 0.339 | 0.337 | 0.335 | 0.337 | 0.332 | 0.334 | 0.329 | 0.331 | 0.327 | 0.329 | 0.327 | 0.329 | 0.328 | 0.332 | 0.328 | 0.329 | 0.328 | 0.33 | 0.328 | 0.329 | 0.327 | 0.332 | 0.331 | 0.331 | 0.328 | 0.329 | 0.328 | 0.331 | 0.329 | 0.331 | 0.331 | 0.332 | 0.334 | 0.338 | 0.335 | 0.336 | 0.335 | 0.337 | 0.334 | 0.325 | 0.317 | 0.312 | 0.311 | 0.316 | 0.317 | 0.318 | 0.32 | 0.323 | 0.325 | 0.324 | 0.326 | 0.33 | 0.334 | 0.338 | 0.341 | 0.344 | 0.347 | 0.348 | 0.346 | 0.346 | 0.344 | 0.343 | 0.34 | 0.336 | 0.332 | 0.333 | 0.331 | 0.332 | 0.999 | 0.956 | 0.954 | 0.918 | 0.899 | 0.87 | 0.883 | 0.885 | 0.885 | 0.919 | 0.951 | 0.986 | 1.002 | 1.004 | 0.992 | 0.884 | 0.854 | 0.826 | 0.811 | 0.814 | 0.873 | 0.918 | 0.974 | 1.001 | 1.002 | 1.033 | 1.058 | 1.178 | 1.222 | 1.273 | 1.261 | 1.26 | 1.194 | 1.126 | 1.056 | 1.009 | 0.998 | 1.004 | 1.001 | 1.009 | 1.013 | 1.017 | 1.022 | 1.019 | 1.02 | 1.016 | 1.008 | 1
Warmtepomp | 0.9 | WP | 0 | 36.122 |  |  |  | 9.749 |  |  |  | 0.871 | 0.879 | 0.874 | 0.882 | 0.871 | 0.88 | 0.884 | 0.901 | 0.881 | 0.89 | 0.887 | 0.908 | 0.905 | 0.916 | 0.911 | 0.92 | 0.909 | 0.922 | 0.932 | 0.925 | 0.931 | 0.928 | 0.932 | 0.933 | 0.942 | 0.936 | 0.946 | 0.947 | 0.95 | 0.954 | 0.957 | 0.958 | 0.957 | 0.948 | 0.949 | 0.951 | 0.949 | 0.935 | 0.941 | 0.942 | 0.929 | 0.923 | 0.932 | 0.936 | 0.92 | 0.918 | 0.925 | 0.928 | 0.927 | 0.922 | 0.927 | 0.929 | 0.924 | 0.92 | 0.927 | 0.931 | 0.928 | 0.921 | 0.924 | 0.927 | 0.935 | 0.934 | 0.934 | 0.937 | 0.943 | 0.948 | 0.95 | 0.953 | 0.954 | 0.954 | 0.953 | 0.955 | 0.957 | 0.956 | 0.954 | 0.958 | 0.953 | 0.954 | 0.955 | 0.955 | 0.954 | 0.953 | 0.952 | 0.951 | 0.948 | 0.939 | 0.941 | 0.94 | 0.921 | 0.906 | 0.915 | 0.894 | 0.878 | 0.875 | 0.871 | 0.883 | [288 empty] | 0.871 | 0.879 | 0.874 | 0.882 | 0.871 | 0.88 | 0.884 | 0.901 | 0.881 | 0.89 | 0.887 | 0.908 | 0.905 | 0.916 | 0.911 | 0.92 | 0.909 | 0.922 | 0.932 | 0.925 | 0.931 | 0.928 | 0.932 | 0.933 | 0.942 | 0.936 | 0.946 | 0.947 | 0.95 | 0.954 | 0.957 | 0.958 | 0.957 | 0.948 | 0.949 | 0.951 | 0.949 | 0.935 | 0.941 | 0.942 | 0.929 | 0.923 | 0.932 | 0.936 | 0.92 | 0.918 | 0.925 | 0.928 | 0.927 | 0.922 | 0.927 | 0.929 | 0.924 | 0.92 | 0.927 | 0.931 | 0.928 | 0.921 | 0.924 | 0.927 | 0.935 | 0.934 | 0.934 | 0.937 | 0.943 | 0.948 | 0.95 | 0.953 | 0.954 | 0.954 | 0.953 | 0.955 | 0.957 | 0.956 | 0.954 | 0.958 | 0.953 | 0.954 | 0.955 | 0.955 | 0.954 | 0.953 | 0.952 | 0.951 | 0.948 | 0.939 | 0.941 | 0.94 | 0.921 | 0.906 | 0.915 | 0.894 | 0.878 | 0.875 | 0.871 | 0.883 | [288 empty] | 0.936 | 1 | 0.96 | 0.853 | 0.689 | 0.555 | 0.489 | 0.469 | 0.481 | 0.543 | 0.673 | 0.82
Warmtepomp 2-onder-1-kapwoning | 0.95 | WP | 0 | 35.333 |  |  |  | 15.726 |  |  |  | 0.622 | 0.614 | 0.608 | 0.608 | 0.61 | 0.611 | 0.613 | 0.613 | 0.611 | 0.611 | 0.612 | 0.611 | 0.612 | 0.613 | 0.614 | 0.615 | 0.616 | 0.617 | 0.617 | 0.618 | 0.617 | 0.617 | 0.615 | 0.611 | 0.609 | 0.609 | 0.611 | 0.615 | 0.617 | 0.612 | 0.602 | 0.584 | 0.557 | 0.523 | 0.483 | 0.443 | 0.407 | 0.377 | 0.355 | 0.338 | 0.325 | 0.316 | 0.309 | 0.305 | 0.304 | 0.304 | 0.307 | 0.312 | 0.318 | 0.323 | 0.332 | 0.344 | 0.356 | 0.368 | 0.373 | 0.374 | 0.374 | 0.379 | 0.406 | 0.443 | 0.474 | 0.489 | 0.505 | 0.521 | 0.534 | 0.549 | 0.563 | 0.57 | 0.573 | 0.584 | 0.6 | 0.549 | 0.568 | 0.58 | 0.583 | 0.582 | 0.582 | 0.581 | 0.582 | 0.583 | 0.586 | 0.591 | 0.595 | 0.6 | 0.602 | 0.602 | 0.606 | 0.615 | 0.627 | 0.64 | 0.647 | 0.65 | 0.646 | 0.644 | 0.64 | 0.635 | [288 empty] | 0.634 | 0.628 | 0.625 | 0.624 | 0.626 | 0.628 | 0.629 | 0.629 | 0.628 | 0.628 | 0.628 | 0.627 | 0.628 | 0.629 | 0.629 | 0.631 | 0.631 | 0.631 | 0.632 | 0.632 | 0.631 | 0.63 | 0.627 | 0.621 | 0.617 | 0.614 | 0.614 | 0.616 | 0.615 | 0.61 | 0.6 | 0.585 | 0.56 | 0.526 | 0.484 | 0.439 | 0.401 | 0.37 | 0.347 | 0.331 | 0.318 | 0.31 | 0.305 | 0.304 | 0.305 | 0.308 | 0.313 | 0.32 | 0.326 | 0.333 | 0.341 | 0.354 | 0.368 | 0.38 | 0.386 | 0.387 | 0.387 | 0.393 | 0.421 | 0.476 | 0.504 | 0.518 | 0.541 | 0.555 | 0.56 | 0.572 | 0.583 | 0.594 | 0.598 | 0.605 | 0.62 | 0.549 | 0.567 | 0.577 | 0.58 | 0.578 | 0.577 | 0.576 | 0.575 | 0.574 | 0.576 | 0.58 | 0.584 | 0.587 | 0.589 | 0.589 | 0.594 | 0.603 | 0.615 | 0.629 | 0.637 | 0.638 | 0.638 | 0.635 | 0.631 | 0.627 | [288 empty] | 1 | 0.843 | 0.593 | 0.212 | 0.133 | 0.098 | 0.095 | 0.092 | 0.12 | 0.509 | 0.715 | 1.046
Warmtepomp appartement | 0.95 | WP | 0 | 24.566 |  |  |  | 11.812 |  |  |  | 0.544 | 0.532 | 0.523 | 0.52 | 0.519 | 0.519 | 0.518 | 0.516 | 0.513 | 0.511 | 0.509 | 0.508 | 0.508 | 0.508 | 0.508 | 0.509 | 0.509 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.509 | 0.51 | 0.515 | 0.528 | 0.548 | 0.568 | 0.588 | 0.6 | 0.602 | 0.594 | 0.572 | 0.537 | 0.493 | 0.446 | 0.401 | 0.362 | 0.331 | 0.308 | 0.289 | 0.275 | 0.266 | 0.259 | 0.256 | 0.256 | 0.257 | 0.26 | 0.264 | 0.267 | 0.275 | 0.289 | 0.304 | 0.316 | 0.321 | 0.317 | 0.31 | 0.306 | 0.308 | 0.315 | 0.338 | 0.368 | 0.397 | 0.419 | 0.436 | 0.446 | 0.457 | 0.467 | 0.48 | 0.501 | 0.532 | 0.486 | 0.512 | 0.523 | 0.522 | 0.517 | 0.511 | 0.506 | 0.501 | 0.5 | 0.503 | 0.508 | 0.514 | 0.519 | 0.52 | 0.522 | 0.531 | 0.545 | 0.564 | 0.58 | 0.589 | 0.591 | 0.586 | 0.579 | 0.572 | 0.561 | [288 empty] | 0.553 | 0.541 | 0.534 | 0.531 | 0.53 | 0.531 | 0.53 | 0.529 | 0.525 | 0.523 | 0.521 | 0.519 | 0.519 | 0.519 | 0.519 | 0.519 | 0.52 | 0.52 | 0.519 | 0.52 | 0.518 | 0.517 | 0.515 | 0.514 | 0.518 | 0.53 | 0.547 | 0.569 | 0.586 | 0.597 | 0.602 | 0.593 | 0.573 | 0.539 | 0.492 | 0.441 | 0.393 | 0.352 | 0.321 | 0.297 | 0.279 | 0.266 | 0.258 | 0.253 | 0.252 | 0.253 | 0.255 | 0.259 | 0.263 | 0.266 | 0.274 | 0.288 | 0.303 | 0.317 | 0.322 | 0.318 | 0.312 | 0.307 | 0.307 | 0.315 | 0.339 | 0.369 | 0.407 | 0.429 | 0.444 | 0.461 | 0.473 | 0.483 | 0.494 | 0.515 | 0.545 | 0.486 | 0.512 | 0.522 | 0.522 | 0.517 | 0.511 | 0.504 | 0.498 | 0.495 | 0.496 | 0.5 | 0.505 | 0.508 | 0.509 | 0.511 | 0.52 | 0.535 | 0.554 | 0.571 | 0.579 | 0.581 | 0.578 | 0.571 | 0.564 | 0.553 | [288 empty] | 1 | 0.839 | 0.588 | 0.25 | 0.192 | 0.16 | 0.157 | 0.153 | 0.181 | 0.534 | 0.741 | 1.058
Warmtepomp hoekwoning | 0.95 | WP | 0 | 31.719 |  |  |  | 13.459 |  |  |  | 0.637 | 0.628 | 0.623 | 0.623 | 0.624 | 0.625 | 0.627 | 0.627 | 0.625 | 0.625 | 0.625 | 0.624 | 0.626 | 0.626 | 0.627 | 0.628 | 0.628 | 0.629 | 0.629 | 0.629 | 0.629 | 0.628 | 0.625 | 0.621 | 0.618 | 0.618 | 0.621 | 0.626 | 0.629 | 0.626 | 0.617 | 0.601 | 0.575 | 0.542 | 0.502 | 0.461 | 0.424 | 0.393 | 0.369 | 0.352 | 0.339 | 0.33 | 0.323 | 0.32 | 0.318 | 0.319 | 0.323 | 0.328 | 0.335 | 0.34 | 0.349 | 0.362 | 0.375 | 0.387 | 0.392 | 0.392 | 0.39 | 0.393 | 0.405 | 0.442 | 0.476 | 0.504 | 0.52 | 0.536 | 0.551 | 0.558 | 0.572 | 0.583 | 0.581 | 0.584 | 0.603 | 0.565 | 0.585 | 0.598 | 0.602 | 0.601 | 0.6 | 0.599 | 0.598 | 0.598 | 0.6 | 0.604 | 0.609 | 0.613 | 0.615 | 0.616 | 0.62 | 0.63 | 0.642 | 0.655 | 0.663 | 0.666 | 0.662 | 0.66 | 0.655 | 0.65 | [288 empty] | 0.649 | 0.643 | 0.639 | 0.638 | 0.639 | 0.641 | 0.642 | 0.641 | 0.64 | 0.639 | 0.639 | 0.639 | 0.64 | 0.64 | 0.641 | 0.642 | 0.642 | 0.643 | 0.643 | 0.643 | 0.642 | 0.64 | 0.635 | 0.628 | 0.624 | 0.621 | 0.623 | 0.626 | 0.626 | 0.623 | 0.615 | 0.601 | 0.577 | 0.543 | 0.501 | 0.457 | 0.418 | 0.386 | 0.363 | 0.345 | 0.333 | 0.324 | 0.319 | 0.318 | 0.32 | 0.324 | 0.33 | 0.337 | 0.344 | 0.35 | 0.359 | 0.373 | 0.387 | 0.399 | 0.406 | 0.406 | 0.403 | 0.404 | 0.415 | 0.45 | 0.503 | 0.523 | 0.544 | 0.558 | 0.575 | 0.585 | 0.596 | 0.588 | 0.586 | 0.588 | 0.604 | 0.562 | 0.582 | 0.592 | 0.595 | 0.593 | 0.591 | 0.589 | 0.588 | 0.587 | 0.588 | 0.592 | 0.597 | 0.6 | 0.603 | 0.603 | 0.607 | 0.618 | 0.63 | 0.644 | 0.652 | 0.654 | 0.654 | 0.651 | 0.647 | 0.642 | [288 empty] | 1 | 0.856 | 0.622 | 0.239 | 0.151 | 0.108 | 0.104 | 0.099 | 0.135 | 0.527 | 0.727 | 1.046
Warmtepomp maisonette | 0.95 | WP | 0 | 27.257 |  |  |  | 12.595 |  |  |  | 0.586 | 0.575 | 0.568 | 0.566 | 0.566 | 0.566 | 0.566 | 0.565 | 0.562 | 0.561 | 0.56 | 0.559 | 0.559 | 0.559 | 0.56 | 0.561 | 0.561 | 0.562 | 0.562 | 0.562 | 0.561 | 0.561 | 0.559 | 0.559 | 0.561 | 0.57 | 0.583 | 0.598 | 0.611 | 0.615 | 0.613 | 0.6 | 0.576 | 0.541 | 0.498 | 0.453 | 0.412 | 0.376 | 0.348 | 0.327 | 0.312 | 0.3 | 0.291 | 0.287 | 0.284 | 0.284 | 0.287 | 0.292 | 0.297 | 0.302 | 0.31 | 0.324 | 0.338 | 0.349 | 0.354 | 0.351 | 0.346 | 0.345 | 0.35 | 0.368 | 0.404 | 0.433 | 0.455 | 0.472 | 0.487 | 0.5 | 0.507 | 0.516 | 0.526 | 0.541 | 0.566 | 0.524 | 0.548 | 0.559 | 0.56 | 0.556 | 0.552 | 0.547 | 0.544 | 0.543 | 0.545 | 0.55 | 0.555 | 0.559 | 0.561 | 0.563 | 0.57 | 0.582 | 0.599 | 0.614 | 0.622 | 0.624 | 0.62 | 0.615 | 0.609 | 0.601 | [288 empty] | 0.596 | 0.586 | 0.581 | 0.579 | 0.579 | 0.581 | 0.581 | 0.579 | 0.577 | 0.575 | 0.574 | 0.574 | 0.574 | 0.574 | 0.574 | 0.575 | 0.575 | 0.575 | 0.576 | 0.575 | 0.574 | 0.573 | 0.57 | 0.566 | 0.567 | 0.573 | 0.584 | 0.598 | 0.609 | 0.613 | 0.612 | 0.6 | 0.578 | 0.543 | 0.497 | 0.449 | 0.404 | 0.367 | 0.339 | 0.318 | 0.302 | 0.291 | 0.285 | 0.282 | 0.282 | 0.285 | 0.289 | 0.295 | 0.302 | 0.307 | 0.315 | 0.328 | 0.342 | 0.354 | 0.359 | 0.356 | 0.351 | 0.347 | 0.352 | 0.373 | 0.408 | 0.452 | 0.477 | 0.487 | 0.503 | 0.514 | 0.525 | 0.535 | 0.537 | 0.541 | 0.561 | 0.521 | 0.544 | 0.555 | 0.555 | 0.551 | 0.548 | 0.543 | 0.539 | 0.537 | 0.538 | 0.541 | 0.546 | 0.548 | 0.549 | 0.55 | 0.557 | 0.571 | 0.587 | 0.604 | 0.612 | 0.614 | 0.612 | 0.608 | 0.601 | 0.594 | [288 empty] | 1 | 0.844 | 0.601 | 0.24 | 0.173 | 0.135 | 0.131 | 0.128 | 0.158 | 0.525 | 0.734 | 1.056
Warmtepomp overige woning | 0.95 | WP | 0 | 24.935 |  |  |  | 12.248 |  |  |  | 0.57 | 0.557 | 0.549 | 0.545 | 0.544 | 0.544 | 0.544 | 0.541 | 0.538 | 0.536 | 0.535 | 0.534 | 0.533 | 0.533 | 0.534 | 0.535 | 0.535 | 0.536 | 0.536 | 0.536 | 0.536 | 0.535 | 0.534 | 0.535 | 0.54 | 0.553 | 0.571 | 0.59 | 0.609 | 0.619 | 0.62 | 0.611 | 0.588 | 0.554 | 0.509 | 0.461 | 0.416 | 0.377 | 0.345 | 0.32 | 0.301 | 0.287 | 0.276 | 0.27 | 0.267 | 0.266 | 0.267 | 0.27 | 0.274 | 0.277 | 0.285 | 0.299 | 0.314 | 0.327 | 0.332 | 0.328 | 0.323 | 0.318 | 0.319 | 0.325 | 0.341 | 0.367 | 0.4 | 0.432 | 0.454 | 0.468 | 0.48 | 0.491 | 0.503 | 0.524 | 0.554 | 0.505 | 0.531 | 0.541 | 0.541 | 0.537 | 0.532 | 0.527 | 0.524 | 0.522 | 0.525 | 0.53 | 0.536 | 0.541 | 0.543 | 0.545 | 0.554 | 0.567 | 0.586 | 0.602 | 0.611 | 0.614 | 0.609 | 0.603 | 0.596 | 0.587 | [288 empty] | 0.579 | 0.569 | 0.562 | 0.558 | 0.557 | 0.558 | 0.557 | 0.555 | 0.552 | 0.55 | 0.548 | 0.547 | 0.547 | 0.547 | 0.547 | 0.547 | 0.547 | 0.547 | 0.547 | 0.547 | 0.546 | 0.545 | 0.543 | 0.542 | 0.545 | 0.556 | 0.571 | 0.59 | 0.606 | 0.616 | 0.619 | 0.61 | 0.59 | 0.555 | 0.508 | 0.457 | 0.409 | 0.367 | 0.334 | 0.31 | 0.29 | 0.277 | 0.268 | 0.263 | 0.261 | 0.263 | 0.266 | 0.269 | 0.274 | 0.277 | 0.285 | 0.299 | 0.314 | 0.327 | 0.333 | 0.33 | 0.323 | 0.319 | 0.318 | 0.323 | 0.337 | 0.371 | 0.405 | 0.445 | 0.469 | 0.479 | 0.495 | 0.506 | 0.521 | 0.54 | 0.569 | 0.504 | 0.529 | 0.54 | 0.541 | 0.536 | 0.531 | 0.526 | 0.521 | 0.518 | 0.519 | 0.523 | 0.527 | 0.531 | 0.531 | 0.533 | 0.542 | 0.556 | 0.575 | 0.592 | 0.601 | 0.603 | 0.601 | 0.595 | 0.588 | 0.578 | [288 empty] | 1 | 0.835 | 0.574 | 0.24 | 0.185 | 0.153 | 0.151 | 0.146 | 0.173 | 0.517 | 0.731 | 1.056
Warmtepomp portiekwoning | 0.95 | WP | 0 | 25.647 |  |  |  | 11.998 |  |  |  | 0.575 | 0.564 | 0.556 | 0.554 | 0.553 | 0.554 | 0.554 | 0.553 | 0.55 | 0.549 | 0.547 | 0.546 | 0.546 | 0.546 | 0.546 | 0.547 | 0.547 | 0.547 | 0.548 | 0.547 | 0.546 | 0.545 | 0.543 | 0.542 | 0.544 | 0.554 | 0.569 | 0.585 | 0.601 | 0.608 | 0.608 | 0.597 | 0.574 | 0.54 | 0.497 | 0.452 | 0.409 | 0.373 | 0.345 | 0.323 | 0.307 | 0.295 | 0.287 | 0.282 | 0.28 | 0.28 | 0.283 | 0.287 | 0.292 | 0.297 | 0.306 | 0.32 | 0.335 | 0.347 | 0.352 | 0.349 | 0.343 | 0.341 | 0.344 | 0.354 | 0.385 | 0.418 | 0.446 | 0.464 | 0.477 | 0.49 | 0.502 | 0.509 | 0.521 | 0.537 | 0.565 | 0.516 | 0.541 | 0.553 | 0.553 | 0.55 | 0.545 | 0.54 | 0.536 | 0.534 | 0.536 | 0.541 | 0.546 | 0.55 | 0.551 | 0.553 | 0.56 | 0.573 | 0.59 | 0.606 | 0.614 | 0.617 | 0.612 | 0.607 | 0.6 | 0.59 | [288 empty] | 0.582 | 0.572 | 0.566 | 0.564 | 0.564 | 0.564 | 0.565 | 0.562 | 0.56 | 0.558 | 0.557 | 0.556 | 0.556 | 0.556 | 0.556 | 0.557 | 0.557 | 0.557 | 0.557 | 0.557 | 0.555 | 0.553 | 0.55 | 0.546 | 0.547 | 0.555 | 0.567 | 0.585 | 0.597 | 0.605 | 0.605 | 0.595 | 0.574 | 0.54 | 0.495 | 0.448 | 0.403 | 0.365 | 0.337 | 0.314 | 0.298 | 0.286 | 0.279 | 0.277 | 0.277 | 0.28 | 0.284 | 0.29 | 0.297 | 0.302 | 0.312 | 0.326 | 0.341 | 0.354 | 0.359 | 0.356 | 0.35 | 0.346 | 0.347 | 0.358 | 0.389 | 0.432 | 0.462 | 0.476 | 0.492 | 0.505 | 0.51 | 0.522 | 0.531 | 0.55 | 0.563 | 0.511 | 0.535 | 0.545 | 0.545 | 0.54 | 0.535 | 0.53 | 0.525 | 0.523 | 0.524 | 0.528 | 0.533 | 0.536 | 0.537 | 0.538 | 0.546 | 0.56 | 0.578 | 0.594 | 0.603 | 0.605 | 0.604 | 0.598 | 0.591 | 0.584 | [288 empty] | 1 | 0.858 | 0.641 | 0.264 | 0.188 | 0.144 | 0.142 | 0.137 | 0.171 | 0.552 | 0.743 | 1.05
Warmtepomp tussenwoning | 0.95 | WP | 0 | 29.152 |  |  |  | 13.4 |  |  |  | 0.633 | 0.624 | 0.618 | 0.616 | 0.617 | 0.618 | 0.619 | 0.618 | 0.617 | 0.616 | 0.616 | 0.616 | 0.616 | 0.616 | 0.617 | 0.618 | 0.618 | 0.618 | 0.619 | 0.619 | 0.618 | 0.618 | 0.616 | 0.613 | 0.612 | 0.616 | 0.623 | 0.632 | 0.639 | 0.64 | 0.633 | 0.619 | 0.593 | 0.559 | 0.517 | 0.473 | 0.433 | 0.398 | 0.371 | 0.351 | 0.335 | 0.324 | 0.316 | 0.311 | 0.308 | 0.308 | 0.31 | 0.315 | 0.32 | 0.326 | 0.335 | 0.349 | 0.364 | 0.376 | 0.383 | 0.382 | 0.379 | 0.38 | 0.387 | 0.411 | 0.449 | 0.479 | 0.507 | 0.525 | 0.541 | 0.553 | 0.566 | 0.573 | 0.583 | 0.595 | 0.614 | 0.56 | 0.583 | 0.595 | 0.599 | 0.598 | 0.596 | 0.595 | 0.594 | 0.593 | 0.596 | 0.6 | 0.605 | 0.609 | 0.611 | 0.612 | 0.617 | 0.627 | 0.641 | 0.655 | 0.663 | 0.666 | 0.663 | 0.659 | 0.654 | 0.647 | [288 empty] | 0.644 | 0.637 | 0.632 | 0.63 | 0.631 | 0.632 | 0.633 | 0.633 | 0.63 | 0.629 | 0.629 | 0.629 | 0.629 | 0.63 | 0.63 | 0.631 | 0.632 | 0.632 | 0.632 | 0.632 | 0.631 | 0.629 | 0.626 | 0.62 | 0.618 | 0.62 | 0.624 | 0.632 | 0.636 | 0.636 | 0.631 | 0.618 | 0.595 | 0.561 | 0.517 | 0.47 | 0.427 | 0.392 | 0.364 | 0.343 | 0.327 | 0.316 | 0.311 | 0.308 | 0.308 | 0.31 | 0.314 | 0.32 | 0.327 | 0.335 | 0.345 | 0.359 | 0.375 | 0.387 | 0.394 | 0.394 | 0.39 | 0.39 | 0.397 | 0.421 | 0.459 | 0.507 | 0.533 | 0.552 | 0.563 | 0.575 | 0.585 | 0.596 | 0.603 | 0.614 | 0.633 | 0.558 | 0.579 | 0.59 | 0.592 | 0.59 | 0.589 | 0.586 | 0.585 | 0.583 | 0.584 | 0.589 | 0.593 | 0.596 | 0.598 | 0.598 | 0.602 | 0.613 | 0.627 | 0.642 | 0.65 | 0.653 | 0.652 | 0.649 | 0.645 | 0.639 | [288 empty] | 1 | 0.853 | 0.614 | 0.23 | 0.153 | 0.12 | 0.117 | 0.113 | 0.139 | 0.521 | 0.725 | 1.042
Warmtepomp vrijstaande woning | 0.95 | WP | 0 | 38.613 |  |  |  | 15.751 |  |  |  | 0.693 | 0.688 | 0.685 | 0.685 | 0.687 | 0.688 | 0.69 | 0.692 | 0.692 | 0.692 | 0.693 | 0.693 | 0.694 | 0.695 | 0.696 | 0.698 | 0.698 | 0.699 | 0.699 | 0.7 | 0.7 | 0.699 | 0.696 | 0.691 | 0.685 | 0.678 | 0.672 | 0.665 | 0.659 | 0.646 | 0.63 | 0.611 | 0.582 | 0.55 | 0.512 | 0.474 | 0.441 | 0.413 | 0.392 | 0.376 | 0.363 | 0.354 | 0.347 | 0.342 | 0.341 | 0.341 | 0.344 | 0.349 | 0.356 | 0.362 | 0.37 | 0.382 | 0.394 | 0.405 | 0.412 | 0.415 | 0.419 | 0.431 | 0.476 | 0.514 | 0.532 | 0.548 | 0.568 | 0.585 | 0.604 | 0.62 | 0.63 | 0.639 | 0.644 | 0.647 | 0.648 | 0.599 | 0.616 | 0.63 | 0.637 | 0.64 | 0.643 | 0.645 | 0.648 | 0.65 | 0.652 | 0.656 | 0.66 | 0.665 | 0.668 | 0.669 | 0.671 | 0.677 | 0.685 | 0.696 | 0.704 | 0.707 | 0.706 | 0.707 | 0.705 | 0.704 | [288 empty] | 0.712 | 0.709 | 0.706 | 0.706 | 0.708 | 0.709 | 0.711 | 0.713 | 0.712 | 0.713 | 0.714 | 0.714 | 0.715 | 0.716 | 0.717 | 0.718 | 0.719 | 0.72 | 0.72 | 0.72 | 0.719 | 0.717 | 0.713 | 0.704 | 0.695 | 0.685 | 0.675 | 0.666 | 0.655 | 0.643 | 0.628 | 0.612 | 0.587 | 0.555 | 0.515 | 0.472 | 0.436 | 0.406 | 0.385 | 0.37 | 0.358 | 0.351 | 0.348 | 0.344 | 0.345 | 0.348 | 0.353 | 0.361 | 0.37 | 0.376 | 0.385 | 0.395 | 0.408 | 0.419 | 0.426 | 0.43 | 0.434 | 0.442 | 0.485 | 0.541 | 0.561 | 0.586 | 0.607 | 0.619 | 0.635 | 0.649 | 0.662 | 0.673 | 0.676 | 0.667 | 0.651 | 0.603 | 0.619 | 0.633 | 0.639 | 0.641 | 0.644 | 0.645 | 0.647 | 0.648 | 0.649 | 0.652 | 0.655 | 0.658 | 0.661 | 0.66 | 0.661 | 0.667 | 0.674 | 0.685 | 0.694 | 0.697 | 0.699 | 0.7 | 0.699 | 0.698 | [288 empty] | 1 | 0.845 | 0.574 | 0.196 | 0.118 | 0.082 | 0.078 | 0.074 | 0.106 | 0.485 | 0.705 | 1.035
PV | 1 | PV | 1 | -8.756 |  |  |  | 15.009 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 0.848 | 0.893 | 0.922 | 0.942 | 0.957 | 0.967 | 0.973 | 0.977 | 0.98 | 0.982 | 0.983 | 0.983 | 0.983 | 0.983 | 0.982 | 0.981 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.979 | 0.979 | 0.979 | 0.979 | 0.979 | 0.979 | 0.979 | 0.98 | 0.98 | 0.981 | 0.982 | 0.981 | 0.982 | 0.982 | 0.982 | 0.983 | 0.981 | 0.978 | 0.974 | 0.969 | 0.963 | 0.956 | 0.945 | 0.934 | 0.928 | 0.861 | 0.741 | 0.597 | 0.424 | 0.296 | 0.217 | 0.156 | 0.115 | 0.088 | 0.07 | 0.057 | 0.049 | 0.043 | 0.039 | 0.036 | 0.035 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [288 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.79 | 0.848 | 0.893 | 0.922 | 0.942 | 0.957 | 0.967 | 0.973 | 0.977 | 0.98 | 0.982 | 0.983 | 0.983 | 0.983 | 0.983 | 0.982 | 0.981 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.979 | 0.979 | 0.979 | 0.979 | 0.979 | 0.979 | 0.979 | 0.98 | 0.98 | 0.981 | 0.982 | 0.981 | 0.982 | 0.982 | 0.982 | 0.983 | 0.981 | 0.978 | 0.974 | 0.969 | 0.963 | 0.956 | 0.945 | 0.934 | 0.928 | 0.861 | 0.741 | 0.597 | 0.424 | 0.296 | 0.217 | 0.156 | 0.115 | 0.088 | 0.07 | 0.057 | 0.049 | 0.043 | 0.039 | 0.036 | 0.035 | 0.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [288 empty] | 1 | 1.007 | 1.004 | 1.007 | 1.035 | 1.042 | 1.047 | 1.053 | 1.033 | 1.011 | 0.999 | 0.993 | [36 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.005 | -0.079 | -0.287 | -0.701 | -1.766 | -3.209 | -5.077 | -7.037 | -8.985 | -12.374 | -15.97 | -19.487 | -24.058 | -28.86 | -33.051 | -37.845 | -41.176 | -45.278 | -48.468 | -52.685 | -53.991 | -53.93 | -56.356 | -58.678 | -59.682 | -63.037 | -63.12 | -65.745 | -65.35 | -70.078 | -68.571 | -69.108 | -69.043 | -69.464 | -70.423 | -68.194 | -68.778 | -64.324 | -59.094 | -58.957 | -53.913 | -51.056 | -49.331 | -43.199 | -41.197 | -37.194 | -36.424 | -31.343 | -26.049 | -21.757 | -19.079 | -16.474 | -15.577 | -12.494 | -9.299 | -7.421 | -5.6 | -3.295 | -1.792 | -0.807 | -0.453 | -0.236 | -0.099 | -0.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.005 | -0.079 | -0.287 | -0.701 | -1.766 | -3.209 | -5.077 | -7.037 | -8.985 | -12.374 | -15.97 | -19.487 | -24.058 | -28.86 | -33.051 | -37.845 | -41.176 | -45.278 | -48.468 | -52.685 | -53.991 | -53.93 | -56.356 | -58.678 | -59.682 | -63.037 | -63.12 | -65.745 | -65.35 | -70.078 | -68.571 | -69.108 | -69.043 | -69.464 | -70.423 | -68.194 | -68.778 | -64.324 | -59.094 | -58.957 | -53.913 | -51.056 | -49.331 | -43.199 | -41.197 | -37.194 | -36.424 | -31.343 | -26.049 | -21.757 | -19.079 | -16.474 | -15.577 | -12.494 | -9.299 | -7.421 | -5.6 | -3.295 | -1.792 | -0.807 | -0.453 | -0.236 | -0.099 | -0.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.254 | 0.399 | 0.302 | 0.391 | 0.805 | 0.947 | 0.939 | 1 | 0.752 | 0.44 | 0.308 | 0.172
EV | 1 | EV | 0 | 88.267 |  |  |  | 21.814 |  |  |  | 0.113 | 0.107 | 0.103 | 0.097 | 0.097 | 0.09 | 0.085 | 0.077 | 0.071 | 0.065 | 0.06 | 0.054 | 0.049 | 0.044 | 0.039 | 0.034 | 0.033 | 0.031 | 0.029 | 0.024 | 0.025 | 0.03 | 0.038 | 0.038 | 0.044 | 0.053 | 0.069 | 0.069 | 0.066 | 0.061 | 0.065 | 0.065 | 0.066 | 0.064 | 0.064 | 0.063 | 0.065 | 0.063 | 0.064 | 0.063 | 0.063 | 0.061 | 0.061 | 0.058 | 0.057 | 0.054 | 0.055 | 0.052 | 0.053 | 0.052 | 0.053 | 0.052 | 0.053 | 0.051 | 0.052 | 0.052 | 0.054 | 0.054 | 0.058 | 0.06 | 0.065 | 0.067 | 0.074 | 0.077 | 0.087 | 0.093 | 0.105 | 0.11 | 0.122 | 0.129 | 0.141 | 0.145 | 0.154 | 0.157 | 0.167 | 0.17 | 0.177 | 0.177 | 0.182 | 0.179 | 0.18 | 0.174 | 0.173 | 0.167 | 0.167 | 0.162 | 0.16 | 0.154 | 0.157 | 0.149 | 0.145 | 0.137 | 0.133 | 0.125 | 0.121 | 0.116 | [288 empty] | 0.094 | 0.089 | 0.085 | 0.08 | 0.081 | 0.076 | 0.071 | 0.065 | 0.06 | 0.055 | 0.051 | 0.046 | 0.042 | 0.037 | 0.034 | 0.03 | 0.029 | 0.027 | 0.027 | 0.024 | 0.024 | 0.028 | 0.036 | 0.033 | 0.036 | 0.042 | 0.052 | 0.054 | 0.052 | 0.049 | 0.052 | 0.053 | 0.054 | 0.053 | 0.055 | 0.054 | 0.055 | 0.055 | 0.056 | 0.054 | 0.055 | 0.054 | 0.055 | 0.054 | 0.056 | 0.055 | 0.056 | 0.055 | 0.058 | 0.059 | 0.062 | 0.063 | 0.065 | 0.065 | 0.068 | 0.068 | 0.071 | 0.072 | 0.076 | 0.077 | 0.081 | 0.082 | 0.088 | 0.092 | 0.101 | 0.106 | 0.115 | 0.117 | 0.125 | 0.128 | 0.138 | 0.14 | 0.145 | 0.146 | 0.152 | 0.152 | 0.156 | 0.155 | 0.156 | 0.152 | 0.15 | 0.143 | 0.14 | 0.133 | 0.132 | 0.127 | 0.125 | 0.121 | 0.123 | 0.117 | 0.113 | 0.107 | 0.105 | 0.099 | 0.093 | 0.082 | [288 empty] | 1.008 | 0.892 | 0.798 | 0.803 | 0.8 | 1.41 | 1.08 | 0.958 | 1.04 | 1.003 | 1.085 | 1.122
Huislaadpunt | 1 | EV | 0 | 88.267 |  |  |  | 21.814 |  |  |  | 0.113 | 0.107 | 0.103 | 0.097 | 0.097 | 0.09 | 0.085 | 0.077 | 0.071 | 0.065 | 0.06 | 0.054 | 0.049 | 0.044 | 0.039 | 0.034 | 0.033 | 0.031 | 0.029 | 0.024 | 0.025 | 0.03 | 0.038 | 0.038 | 0.044 | 0.053 | 0.069 | 0.069 | 0.066 | 0.061 | 0.065 | 0.065 | 0.066 | 0.064 | 0.064 | 0.063 | 0.065 | 0.063 | 0.064 | 0.063 | 0.063 | 0.061 | 0.061 | 0.058 | 0.057 | 0.054 | 0.055 | 0.052 | 0.053 | 0.052 | 0.053 | 0.052 | 0.053 | 0.051 | 0.052 | 0.052 | 0.054 | 0.054 | 0.058 | 0.06 | 0.065 | 0.067 | 0.074 | 0.077 | 0.087 | 0.093 | 0.105 | 0.11 | 0.122 | 0.129 | 0.141 | 0.145 | 0.154 | 0.157 | 0.167 | 0.17 | 0.177 | 0.177 | 0.182 | 0.179 | 0.18 | 0.174 | 0.173 | 0.167 | 0.167 | 0.162 | 0.16 | 0.154 | 0.157 | 0.149 | 0.145 | 0.137 | 0.133 | 0.125 | 0.121 | 0.116 | [288 empty] | 0.094 | 0.089 | 0.085 | 0.08 | 0.081 | 0.076 | 0.071 | 0.065 | 0.06 | 0.055 | 0.051 | 0.046 | 0.042 | 0.037 | 0.034 | 0.03 | 0.029 | 0.027 | 0.027 | 0.024 | 0.024 | 0.028 | 0.036 | 0.033 | 0.036 | 0.042 | 0.052 | 0.054 | 0.052 | 0.049 | 0.052 | 0.053 | 0.054 | 0.053 | 0.055 | 0.054 | 0.055 | 0.055 | 0.056 | 0.054 | 0.055 | 0.054 | 0.055 | 0.054 | 0.056 | 0.055 | 0.056 | 0.055 | 0.058 | 0.059 | 0.062 | 0.063 | 0.065 | 0.065 | 0.068 | 0.068 | 0.071 | 0.072 | 0.076 | 0.077 | 0.081 | 0.082 | 0.088 | 0.092 | 0.101 | 0.106 | 0.115 | 0.117 | 0.125 | 0.128 | 0.138 | 0.14 | 0.145 | 0.146 | 0.152 | 0.152 | 0.156 | 0.155 | 0.156 | 0.152 | 0.15 | 0.143 | 0.14 | 0.133 | 0.132 | 0.127 | 0.125 | 0.121 | 0.123 | 0.117 | 0.113 | 0.107 | 0.105 | 0.099 | 0.093 | 0.082 | [288 empty] | 1.008 | 0.892 | 0.798 | 0.803 | 0.8 | 1.41 | 1.08 | 0.958 | 1.04 | 1.003 | 1.085 | 1.122
Kantoorlaadpunt | 1 | EV | 0 | 55.198 |  |  |  | 15.679 |  |  |  | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.003 | 0.005 | 0.014 | 0.03 | 0.06 | 0.092 | 0.134 | 0.177 | 0.22 | 0.227 | 0.227 | 0.221 | 0.217 | 0.197 | 0.181 | 0.167 | 0.155 | 0.138 | 0.125 | 0.113 | 0.108 | 0.1 | 0.096 | 0.097 | 0.1 | 0.097 | 0.093 | 0.09 | 0.088 | 0.08 | 0.077 | 0.071 | 0.068 | 0.063 | 0.057 | 0.052 | 0.049 | 0.043 | 0.039 | 0.035 | 0.031 | 0.026 | 0.024 | 0.022 | 0.022 | 0.021 | 0.02 | 0.02 | 0.02 | 0.019 | 0.018 | 0.019 | 0.019 | 0.018 | 0.018 | 0.016 | 0.015 | 0.014 | 0.013 | 0.012 | 0.011 | 0.01 | 0.009 | 0.009 | 0.008 | 0.007 | 0.006 | 0.006 | 0.005 | 0.004 | 0.004 | 0.004 | [288 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [288 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Openbaar laadpunt | 1 | EV | 0 | 55.198 |  |  |  | 15.679 |  |  |  | 0.074 | 0.068 | 0.061 | 0.055 | 0.05 | 0.045 | 0.04 | 0.035 | 0.031 | 0.028 | 0.024 | 0.022 | 0.019 | 0.017 | 0.015 | 0.014 | 0.013 | 0.012 | 0.011 | 0.01 | 0.01 | 0.01 | 0.011 | 0.011 | 0.012 | 0.014 | 0.016 | 0.02 | 0.025 | 0.03 | 0.035 | 0.041 | 0.047 | 0.053 | 0.058 | 0.062 | 0.065 | 0.067 | 0.068 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.069 | 0.07 | 0.07 | 0.071 | 0.072 | 0.073 | 0.074 | 0.075 | 0.076 | 0.077 | 0.078 | 0.079 | 0.081 | 0.082 | 0.084 | 0.087 | 0.09 | 0.093 | 0.098 | 0.104 | 0.111 | 0.12 | 0.13 | 0.14 | 0.15 | 0.159 | 0.167 | 0.174 | 0.178 | 0.181 | 0.183 | 0.183 | 0.181 | 0.178 | 0.175 | 0.171 | 0.166 | 0.162 | 0.157 | 0.153 | 0.148 | 0.143 | 0.138 | 0.133 | 0.128 | 0.122 | 0.117 | 0.11 | 0.104 | 0.097 | 0.091 | 0.084 | [288 empty] | 0.088 | 0.083 | 0.078 | 0.073 | 0.068 | 0.063 | 0.058 | 0.053 | 0.048 | 0.044 | 0.039 | 0.035 | 0.032 | 0.029 | 0.025 | 0.022 | 0.02 | 0.018 | 0.017 | 0.015 | 0.014 | 0.013 | 0.013 | 0.012 | 0.011 | 0.011 | 0.012 | 0.012 | 0.013 | 0.014 | 0.016 | 0.018 | 0.02 | 0.024 | 0.027 | 0.031 | 0.035 | 0.04 | 0.045 | 0.05 | 0.054 | 0.059 | 0.064 | 0.069 | 0.074 | 0.078 | 0.083 | 0.088 | 0.093 | 0.097 | 0.1 | 0.104 | 0.107 | 0.11 | 0.114 | 0.117 | 0.12 | 0.123 | 0.125 | 0.127 | 0.129 | 0.132 | 0.135 | 0.138 | 0.141 | 0.145 | 0.148 | 0.151 | 0.155 | 0.157 | 0.159 | 0.16 | 0.159 | 0.158 | 0.156 | 0.153 | 0.151 | 0.149 | 0.146 | 0.144 | 0.141 | 0.138 | 0.135 | 0.133 | 0.13 | 0.127 | 0.124 | 0.121 | 0.117 | 0.112 | 0.108 | 0.103 | 0.098 | 0.094 | 0.089 | 0.084 | [288 empty] | 1.008 | 1.011 | 1.007 | 1.017 | 1.047 | 0.997 | 0.999 | 0.995 | 0.998 | 1 | 0.982 | 1.021
Laadpunt met vermogen | 1 | EV | 0 | 100 |  |  |  | 0.1 |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [288 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | [288 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Netbewust laden | 1 | EV | 0 | 100 |  |  |  | 0.1 |  |  |  | 0.113 | 0.107 | 0.103 | 0.097 | 0.097 | 0.09 | 0.085 | 0.077 | 0.071 | 0.065 | 0.06 | 0.054 | 0.049 | 0.044 | 0.039 | 0.034 | 0.033 | 0.031 | 0.029 | 0.024 | 0.025 | 0.03 | 0.038 | 0.038 | 0.044 | 0.053 | 0.069 | 0.069 | 0.066 | 0.061 | 0.065 | 0.065 | 0.066 | 0.064 | 0.064 | 0.063 | 0.065 | 0.063 | 0.064 | 0.063 | 0.063 | 0.061 | 0.061 | 0.058 | 0.057 | 0.054 | 0.055 | 0.052 | 0.053 | 0.052 | 0.053 | 0.052 | 0.053 | 0.051 | 0.052 | 0.052 | 0.054 | 0.054 | 0.058 | 0.06 | 0.065 | 0.067 | 0.074 | 0.077 | 0.087 | 0.093 | 0.105 | 0.11 | 0.122 | 0.129 | 0.141 | 0.145 | 0.154 | 0.157 | 0.167 | 0.17 | 0.177 | 0.177 | 0.182 | 0.179 | 0.18 | 0.174 | 0.173 | 0.167 | 0.167 | 0.162 | 0.16 | 0.154 | 0.157 | 0.149 | 0.145 | 0.137 | 0.133 | 0.125 | 0.121 | 0.116 | [288 empty] | 0.094 | 0.089 | 0.085 | 0.08 | 0.081 | 0.076 | 0.071 | 0.065 | 0.06 | 0.055 | 0.051 | 0.046 | 0.042 | 0.037 | 0.034 | 0.03 | 0.029 | 0.027 | 0.027 | 0.024 | 0.024 | 0.028 | 0.036 | 0.033 | 0.036 | 0.042 | 0.052 | 0.054 | 0.052 | 0.049 | 0.052 | 0.053 | 0.054 | 0.053 | 0.055 | 0.054 | 0.055 | 0.055 | 0.056 | 0.054 | 0.055 | 0.054 | 0.055 | 0.054 | 0.056 | 0.055 | 0.056 | 0.055 | 0.058 | 0.059 | 0.062 | 0.063 | 0.065 | 0.065 | 0.068 | 0.068 | 0.071 | 0.072 | 0.076 | 0.077 | 0.081 | 0.082 | 0.088 | 0.092 | 0.101 | 0.106 | 0.115 | 0.117 | 0.125 | 0.128 | 0.138 | 0.14 | 0.145 | 0.146 | 0.152 | 0.152 | 0.156 | 0.155 | 0.156 | 0.152 | 0.15 | 0.143 | 0.14 | 0.133 | 0.132 | 0.127 | 0.125 | 0.121 | 0.123 | 0.117 | 0.113 | 0.107 | 0.105 | 0.099 | 0.093 | 0.082 | [288 empty] | 1.008 | 0.892 | 0.798 | 0.803 | 0.8 | 1.41 | 1.08 | 0.958 | 1.04 | 1.003 | 1.085 | 1.122 | [36 empty] | -54.545 | -52.273 | -50 | -47.727 | -45.455 | -43.182 | -40.909 | -38.636 | -36.364 | -34.091 | -31.818 | -29.545 | -27.273 | -25 | -22.727 | -20.455 | -18.182 | -15.909 | -13.636 | -11.364 | -9.091 | -6.818 | -4.545 | -2.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -61.364 | -59.091 | -56.818 | -54.545 | -52.273 | -50 | -47.727 | -45.455 | -43.182 | -40.909 | -38.636 | -36.364 | -34.091 | -31.818 | -29.545 | -27.273 | -25 | -22.727 | -20.455 | -18.182 | -15.909 | -13.636 | -11.364 | -9.091 | -6.818 | -4.545 | -2.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -63.636 | -61.364 | -59.091 | -56.818 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Koken | 0.95 | Koken | 0 | 29.969 |  |  |  | 18.573 |  |  |  | 0.015 | 0.014 | 0.013 | 0.005 | 0.002 | 0.002 | 0.001 | 0 | 0.001 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.001 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.005 | 0.008 | 0.017 | 0.022 | 0.021 | 0.03 | 0.043 | 0.054 | 0.05 | 0.057 | 0.061 | 0.069 | 0.078 | 0.077 | 0.092 | 0.095 | 0.093 | 0.092 | 0.099 | 0.101 | 0.116 | 0.125 | 0.123 | 0.143 | 0.16 | 0.172 | 0.177 | 0.193 | 0.189 | 0.185 | 0.191 | 0.194 | 0.183 | 0.163 | 0.173 | 0.17 | 0.19 | 0.201 | 0.22 | 0.226 | 0.281 | 0.301 | 0.354 | 0.419 | 0.515 | 0.579 | 0.629 | 0.626 | 0.569 | 0.551 | 0.508 | 0.462 | 0.403 | 0.345 | 0.297 | 0.289 | 0.25 | 0.228 | 0.21 | 0.182 | 0.147 | 0.138 | 0.105 | 0.083 | 0.066 | 0.061 | 0.049 | 0.037 | 0.034 | 0.022 | 0.015 | 0.013 | 0.011 | [288 empty] | 0.015 | 0.014 | 0.013 | 0.005 | 0.002 | 0.002 | 0.001 | 0 | 0.001 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.001 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.005 | 0.008 | 0.017 | 0.022 | 0.021 | 0.03 | 0.043 | 0.054 | 0.05 | 0.057 | 0.061 | 0.069 | 0.078 | 0.077 | 0.092 | 0.095 | 0.093 | 0.092 | 0.099 | 0.101 | 0.116 | 0.125 | 0.123 | 0.143 | 0.16 | 0.172 | 0.177 | 0.193 | 0.189 | 0.185 | 0.191 | 0.194 | 0.183 | 0.163 | 0.173 | 0.17 | 0.19 | 0.201 | 0.22 | 0.226 | 0.281 | 0.301 | 0.354 | 0.419 | 0.515 | 0.579 | 0.629 | 0.626 | 0.569 | 0.551 | 0.508 | 0.462 | 0.403 | 0.345 | 0.297 | 0.289 | 0.25 | 0.228 | 0.21 | 0.182 | 0.147 | 0.138 | 0.105 | 0.083 | 0.066 | 0.061 | 0.049 | 0.037 | 0.034 | 0.022 | 0.015 | 0.013 | 0.011 | [288 empty] | 1 | 1.005 | 1.013 | 1.012 | 1.015 | 1.008 | 1.006 | 1.003 | 1.002 | 0.995 | 1.003 | 1
Airco | 0.95 | Apparaat | 0 | 36.122 |  |  |  | 9.749 |  |  |  | 0.871 | 0.871 | 0.871 | 0.872 | 0.872 | 0.873 | 0.873 | 0.874 | 0.875 | 0.876 | 0.878 | 0.879 | 0.881 | 0.883 | 0.884 | 0.886 | 0.889 | 0.892 | 0.896 | 0.9 | 0.9 | 0.901 | 0.9 | 0.902 | 0.902 | 0.901 | 0.904 | 0.907 | 0.91 | 0.911 | 0.911 | 0.911 | 0.909 | 0.908 | 0.908 | 0.909 | 0.909 | 0.908 | 0.906 | 0.906 | 0.907 | 0.91 | 0.912 | 0.914 | 0.92 | 0.918 | 0.925 | 0.928 | 0.927 | 0.922 | 0.927 | 0.929 | 0.924 | 0.92 | 0.927 | 0.931 | 0.928 | 0.921 | 0.924 | 0.927 | 0.935 | 0.934 | 0.934 | 0.937 | 0.943 | 0.948 | 0.95 | 0.953 | 0.954 | 0.954 | 0.953 | 0.955 | 0.957 | 0.956 | 0.954 | 0.958 | 0.953 | 0.954 | 0.955 | 0.955 | 0.954 | 0.953 | 0.952 | 0.951 | 0.948 | 0.939 | 0.941 | 0.94 | 0.921 | 0.906 | 0.915 | 0.894 | 0.878 | 0.875 | 0.871 | 0.883 | [288 empty] | 0.871 | 0.871 | 0.871 | 0.872 | 0.872 | 0.873 | 0.873 | 0.874 | 0.875 | 0.876 | 0.878 | 0.879 | 0.881 | 0.883 | 0.884 | 0.886 | 0.889 | 0.892 | 0.896 | 0.9 | 0.9 | 0.901 | 0.9 | 0.902 | 0.902 | 0.901 | 0.904 | 0.907 | 0.91 | 0.911 | 0.911 | 0.911 | 0.909 | 0.908 | 0.908 | 0.909 | 0.909 | 0.908 | 0.906 | 0.906 | 0.907 | 0.91 | 0.912 | 0.914 | 0.92 | 0.918 | 0.925 | 0.928 | 0.927 | 0.922 | 0.927 | 0.929 | 0.924 | 0.92 | 0.927 | 0.931 | 0.928 | 0.921 | 0.924 | 0.927 | 0.935 | 0.934 | 0.934 | 0.937 | 0.943 | 0.948 | 0.95 | 0.953 | 0.954 | 0.954 | 0.953 | 0.955 | 0.957 | 0.956 | 0.954 | 0.958 | 0.953 | 0.954 | 0.955 | 0.955 | 0.954 | 0.953 | 0.952 | 0.951 | 0.948 | 0.939 | 0.941 | 0.94 | 0.921 | 0.906 | 0.915 | 0.894 | 0.878 | 0.875 | 0.871 | 0.883 | [288 empty] | 0.01 | 0.01 | 0.19 | 0.24 | 0.51 | 0.87 | 1 | 0.81 | 0.38 | 0.19 | 0.01 | 0.01
sjv500 | 0.98 | Belasting | 0 | 0.056 | 0.16 | 0.017 | 0.602 | 0.022 | 0.07 | 0.012 | 0.334 | 0.434 | 0.432 | 0.426 | 0.425 | 0.42 | 0.42 | 0.416 | 0.416 | 0.412 | 0.408 | 0.406 | 0.403 | 0.401 | 0.399 | 0.399 | 0.399 | 0.401 | 0.403 | 0.405 | 0.407 | 0.407 | 0.412 | 0.411 | 0.416 | 0.417 | 0.419 | 0.423 | 0.422 | 0.425 | 0.422 | 0.423 | 0.421 | 0.423 | 0.423 | 0.424 | 0.423 | 0.424 | 0.424 | 0.425 | 0.427 | 0.428 | 0.428 | 0.429 | 0.427 | 0.427 | 0.426 | 0.428 | 0.429 | 0.433 | 0.435 | 0.438 | 0.441 | 0.444 | 0.448 | 0.451 | 0.453 | 0.455 | 0.457 | 0.457 | 0.458 | 0.46 | 0.459 | 0.462 | 0.46 | 0.46 | 0.458 | 0.454 | 0.45 | 0.445 | 0.439 | 0.434 | 0.428 | 0.426 | 0.421 | 0.419 | 0.416 | 0.415 | 0.414 | 0.414 | 0.413 | 0.414 | 0.415 | 0.415 | 0.42 | 0.421 | 0.429 | 0.432 | 0.44 | 0.441 | 0.444 | 0.444 | 0.443 | 0.442 | 0.443 | 0.439 | 0.438 | 0.073 | 0.064 | 0.057 | 0.05 | 0.045 | 0.04 | 0.037 | 0.034 | 0.032 | 0.031 | 0.03 | 0.029 | 0.028 | 0.028 | 0.029 | 0.031 | 0.035 | 0.04 | 0.046 | 0.053 | 0.061 | 0.071 | 0.082 | 0.094 | 0.107 | 0.12 | 0.132 | 0.142 | 0.15 | 0.157 | 0.162 | 0.163 | 0.164 | 0.162 | 0.158 | 0.155 | 0.149 | 0.146 | 0.141 | 0.138 | 0.135 | 0.132 | 0.13 | 0.129 | 0.127 | 0.126 | 0.125 | 0.122 | 0.12 | 0.119 | 0.116 | 0.116 | 0.115 | 0.114 | 0.114 | 0.115 | 0.117 | 0.121 | 0.125 | 0.131 | 0.137 | 0.144 | 0.15 | 0.159 | 0.167 | 0.177 | 0.184 | 0.197 | 0.205 | 0.217 | 0.226 | 0.236 | 0.243 | 0.251 | 0.257 | 0.266 | 0.272 | 0.28 | 0.285 | 0.29 | 0.29 | 0.29 | 0.286 | 0.278 | 0.271 | 0.255 | 0.242 | 0.221 | 0.204 | 0.18 | 0.163 | 0.141 | 0.125 | 0.109 | 0.096 | 0.084 | 0.488 | 0.499 | 0.513 | 0.521 | 0.532 | 0.536 | 0.544 | 0.547 | 0.553 | 0.558 | 0.562 | 0.566 | 0.568 | 0.571 | 0.57 | 0.567 | 0.561 | 0.554 | 0.546 | 0.536 | 0.527 | 0.512 | 0.5 | 0.481 | 0.466 | 0.451 | 0.433 | 0.423 | 0.41 | 0.403 | 0.395 | 0.394 | 0.389 | 0.392 | 0.392 | 0.397 | 0.401 | 0.404 | 0.408 | 0.409 | 0.411 | 0.414 | 0.416 | 0.419 | 0.421 | 0.422 | 0.422 | 0.423 | 0.422 | 0.421 | 0.421 | 0.419 | 0.418 | 0.416 | 0.413 | 0.411 | 0.406 | 0.4 | 0.395 | 0.388 | 0.38 | 0.372 | 0.362 | 0.354 | 0.344 | 0.335 | 0.328 | 0.318 | 0.312 | 0.303 | 0.295 | 0.288 | 0.281 | 0.277 | 0.272 | 0.268 | 0.265 | 0.26 | 0.258 | 0.257 | 0.258 | 0.26 | 0.266 | 0.272 | 0.28 | 0.291 | 0.302 | 0.318 | 0.335 | 0.359 | 0.378 | 0.403 | 0.422 | 0.439 | 0.457 | 0.472 | 0.006 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.003 | 0.003 | 0.004 | 0.005 | 0.006 | 0.007 | 0.008 | 0.01 | 0.011 | 0.012 | 0.014 | 0.016 | 0.018 | 0.02 | 0.022 | 0.024 | 0.024 | 0.025 | 0.026 | 0.026 | 0.027 | 0.026 | 0.026 | 0.026 | 0.026 | 0.025 | 0.026 | 0.025 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.023 | 0.023 | 0.025 | 0.026 | 0.027 | 0.029 | 0.03 | 0.033 | 0.035 | 0.038 | 0.041 | 0.044 | 0.048 | 0.05 | 0.052 | 0.052 | 0.05 | 0.048 | 0.046 | 0.044 | 0.041 | 0.038 | 0.035 | 0.033 | 0.03 | 0.028 | 0.025 | 0.023 | 0.021 | 0.019 | 0.017 | 0.015 | 0.013 | 0.011 | 0.009 | 0.008 | 0.006 | 0.431 | 0.429 | 0.423 | 0.422 | 0.417 | 0.417 | 0.412 | 0.409 | 0.406 | 0.403 | 0.402 | 0.4 | 0.399 | 0.398 | 0.399 | 0.399 | 0.4 | 0.401 | 0.403 | 0.405 | 0.406 | 0.411 | 0.411 | 0.417 | 0.42 | 0.42 | 0.423 | 0.423 | 0.424 | 0.423 | 0.425 | 0.425 | 0.425 | 0.427 | 0.428 | 0.429 | 0.432 | 0.432 | 0.433 | 0.434 | 0.436 | 0.439 | 0.441 | 0.443 | 0.442 | 0.442 | 0.445 | 0.446 | 0.45 | 0.451 | 0.453 | 0.451 | 0.455 | 0.458 | 0.46 | 0.463 | 0.465 | 0.466 | 0.465 | 0.468 | 0.467 | 0.465 | 0.469 | 0.465 | 0.465 | 0.465 | 0.459 | 0.455 | 0.448 | 0.437 | 0.433 | 0.424 | 0.42 | 0.414 | 0.41 | 0.406 | 0.405 | 0.402 | 0.403 | 0.401 | 0.4 | 0.399 | 0.4 | 0.405 | 0.409 | 0.419 | 0.425 | 0.432 | 0.436 | 0.441 | 0.443 | 0.446 | 0.444 | 0.441 | 0.436 | 0.436 | 0.069 | 0.061 | 0.053 | 0.047 | 0.042 | 0.038 | 0.035 | 0.032 | 0.03 | 0.028 | 0.027 | 0.027 | 0.026 | 0.027 | 0.028 | 0.03 | 0.034 | 0.04 | 0.046 | 0.055 | 0.063 | 0.075 | 0.087 | 0.099 | 0.112 | 0.124 | 0.135 | 0.145 | 0.154 | 0.16 | 0.163 | 0.162 | 0.16 | 0.156 | 0.15 | 0.146 | 0.139 | 0.135 | 0.131 | 0.129 | 0.127 | 0.124 | 0.122 | 0.12 | 0.12 | 0.12 | 0.119 | 0.117 | 0.115 | 0.114 | 0.111 | 0.112 | 0.111 | 0.111 | 0.113 | 0.114 | 0.116 | 0.12 | 0.125 | 0.131 | 0.137 | 0.145 | 0.151 | 0.159 | 0.169 | 0.178 | 0.187 | 0.2 | 0.207 | 0.221 | 0.23 | 0.241 | 0.25 | 0.259 | 0.269 | 0.28 | 0.289 | 0.299 | 0.305 | 0.312 | 0.315 | 0.317 | 0.315 | 0.307 | 0.299 | 0.28 | 0.266 | 0.24 | 0.22 | 0.192 | 0.172 | 0.145 | 0.127 | 0.105 | 0.091 | 0.078 | 0.494 | 0.506 | 0.52 | 0.527 | 0.538 | 0.543 | 0.551 | 0.557 | 0.562 | 0.566 | 0.569 | 0.572 | 0.573 | 0.573 | 0.572 | 0.569 | 0.564 | 0.557 | 0.549 | 0.536 | 0.526 | 0.508 | 0.494 | 0.474 | 0.457 | 0.443 | 0.428 | 0.418 | 0.406 | 0.401 | 0.394 | 0.393 | 0.394 | 0.397 | 0.399 | 0.404 | 0.407 | 0.411 | 0.416 | 0.417 | 0.418 | 0.417 | 0.417 | 0.416 | 0.418 | 0.418 | 0.415 | 0.416 | 0.415 | 0.415 | 0.416 | 0.417 | 0.415 | 0.413 | 0.41 | 0.406 | 0.403 | 0.397 | 0.393 | 0.383 | 0.377 | 0.369 | 0.358 | 0.352 | 0.341 | 0.328 | 0.322 | 0.309 | 0.303 | 0.296 | 0.287 | 0.279 | 0.272 | 0.265 | 0.259 | 0.253 | 0.247 | 0.243 | 0.239 | 0.236 | 0.237 | 0.239 | 0.244 | 0.25 | 0.258 | 0.27 | 0.281 | 0.304 | 0.322 | 0.349 | 0.37 | 0.396 | 0.418 | 0.445 | 0.465 | 0.479 | 0.006 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.006 | 0.008 | 0.009 | 0.01 | 0.012 | 0.013 | 0.014 | 0.016 | 0.017 | 0.018 | 0.02 | 0.021 | 0.021 | 0.022 | 0.022 | 0.022 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.019 | 0.019 | 0.018 | 0.018 | 0.017 | 0.017 | 0.017 | 0.017 | 0.018 | 0.019 | 0.02 | 0.022 | 0.024 | 0.026 | 0.028 | 0.032 | 0.036 | 0.041 | 0.046 | 0.05 | 0.056 | 0.059 | 0.062 | 0.062 | 0.06 | 0.059 | 0.056 | 0.054 | 0.051 | 0.048 | 0.044 | 0.042 | 0.038 | 0.035 | 0.031 | 0.028 | 0.025 | 0.022 | 0.019 | 0.016 | 0.014 | 0.013 | 0.009 | 0.008 | 0.007 | 1 | 1.066 | 1.088 | 1.194 | 1.182 | 1.226 | 1.364 | 1.277 | 1.128 | 1.088 | 1.032 | 1.003 | 1 | 0.986 | 1.011 | 0.778 | 0.676 | 0.635 | 0.647 | 0.587 | 0.619 | 0.697 | 0.885 | 0.882 | 1 | 0.96 | 0.948 | 1.023 | 1.126 | 1.122 | 0.99 | 1.111 | 1.218 | 1.193 | 1.095 | 1.117 | 1 | 0.922 | 0.768 | 0.575 | 0.397 | 0.326 | 0.306 | 0.282 | 0.351 | 0.447 | 0.657 | 0.701
sjv1000 | 0.98 | Belasting | 0 | 0.112 | 0.32 | 0.035 | 1.204 | 0.045 | 0.14 | 0.024 | 0.668 | 0.434 | 0.432 | 0.426 | 0.425 | 0.42 | 0.42 | 0.416 | 0.416 | 0.412 | 0.408 | 0.406 | 0.403 | 0.401 | 0.399 | 0.399 | 0.399 | 0.401 | 0.403 | 0.405 | 0.407 | 0.407 | 0.412 | 0.411 | 0.416 | 0.417 | 0.419 | 0.423 | 0.422 | 0.425 | 0.422 | 0.423 | 0.421 | 0.423 | 0.423 | 0.424 | 0.423 | 0.424 | 0.424 | 0.425 | 0.427 | 0.428 | 0.428 | 0.429 | 0.427 | 0.427 | 0.426 | 0.428 | 0.429 | 0.433 | 0.435 | 0.438 | 0.441 | 0.444 | 0.448 | 0.451 | 0.453 | 0.455 | 0.457 | 0.457 | 0.458 | 0.46 | 0.459 | 0.462 | 0.46 | 0.46 | 0.458 | 0.454 | 0.45 | 0.445 | 0.439 | 0.434 | 0.428 | 0.426 | 0.421 | 0.419 | 0.416 | 0.415 | 0.414 | 0.414 | 0.413 | 0.414 | 0.415 | 0.415 | 0.42 | 0.421 | 0.429 | 0.432 | 0.44 | 0.441 | 0.444 | 0.444 | 0.443 | 0.442 | 0.443 | 0.439 | 0.438 | 0.073 | 0.064 | 0.057 | 0.05 | 0.045 | 0.04 | 0.037 | 0.034 | 0.032 | 0.031 | 0.03 | 0.029 | 0.028 | 0.028 | 0.029 | 0.031 | 0.035 | 0.04 | 0.046 | 0.053 | 0.061 | 0.071 | 0.082 | 0.094 | 0.107 | 0.12 | 0.132 | 0.142 | 0.15 | 0.157 | 0.162 | 0.163 | 0.164 | 0.162 | 0.158 | 0.155 | 0.149 | 0.146 | 0.141 | 0.138 | 0.135 | 0.132 | 0.13 | 0.129 | 0.127 | 0.126 | 0.125 | 0.122 | 0.12 | 0.119 | 0.116 | 0.116 | 0.115 | 0.114 | 0.114 | 0.115 | 0.117 | 0.121 | 0.125 | 0.131 | 0.137 | 0.144 | 0.15 | 0.159 | 0.167 | 0.177 | 0.184 | 0.197 | 0.205 | 0.217 | 0.226 | 0.236 | 0.243 | 0.251 | 0.257 | 0.266 | 0.272 | 0.28 | 0.285 | 0.29 | 0.29 | 0.29 | 0.286 | 0.278 | 0.271 | 0.255 | 0.242 | 0.221 | 0.204 | 0.18 | 0.163 | 0.141 | 0.125 | 0.109 | 0.096 | 0.084 | 0.488 | 0.499 | 0.513 | 0.521 | 0.532 | 0.536 | 0.544 | 0.547 | 0.553 | 0.558 | 0.562 | 0.566 | 0.568 | 0.571 | 0.57 | 0.567 | 0.561 | 0.554 | 0.546 | 0.536 | 0.527 | 0.512 | 0.5 | 0.481 | 0.466 | 0.451 | 0.433 | 0.423 | 0.41 | 0.403 | 0.395 | 0.394 | 0.389 | 0.392 | 0.392 | 0.397 | 0.401 | 0.404 | 0.408 | 0.409 | 0.411 | 0.414 | 0.416 | 0.419 | 0.421 | 0.422 | 0.422 | 0.423 | 0.422 | 0.421 | 0.421 | 0.419 | 0.418 | 0.416 | 0.413 | 0.411 | 0.406 | 0.4 | 0.395 | 0.388 | 0.38 | 0.372 | 0.362 | 0.354 | 0.344 | 0.335 | 0.328 | 0.318 | 0.312 | 0.303 | 0.295 | 0.288 | 0.281 | 0.277 | 0.272 | 0.268 | 0.265 | 0.26 | 0.258 | 0.257 | 0.258 | 0.26 | 0.266 | 0.272 | 0.28 | 0.291 | 0.302 | 0.318 | 0.335 | 0.359 | 0.378 | 0.403 | 0.422 | 0.439 | 0.457 | 0.472 | 0.006 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.003 | 0.003 | 0.004 | 0.005 | 0.006 | 0.007 | 0.008 | 0.01 | 0.011 | 0.012 | 0.014 | 0.016 | 0.018 | 0.02 | 0.022 | 0.024 | 0.024 | 0.025 | 0.026 | 0.026 | 0.027 | 0.026 | 0.026 | 0.026 | 0.026 | 0.025 | 0.026 | 0.025 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.023 | 0.023 | 0.025 | 0.026 | 0.027 | 0.029 | 0.03 | 0.033 | 0.035 | 0.038 | 0.041 | 0.044 | 0.048 | 0.05 | 0.052 | 0.052 | 0.05 | 0.048 | 0.046 | 0.044 | 0.041 | 0.038 | 0.035 | 0.033 | 0.03 | 0.028 | 0.025 | 0.023 | 0.021 | 0.019 | 0.017 | 0.015 | 0.013 | 0.011 | 0.009 | 0.008 | 0.006 | 0.431 | 0.429 | 0.423 | 0.422 | 0.417 | 0.417 | 0.412 | 0.409 | 0.406 | 0.403 | 0.402 | 0.4 | 0.399 | 0.398 | 0.399 | 0.399 | 0.4 | 0.401 | 0.403 | 0.405 | 0.406 | 0.411 | 0.411 | 0.417 | 0.42 | 0.42 | 0.423 | 0.423 | 0.424 | 0.423 | 0.425 | 0.425 | 0.425 | 0.427 | 0.428 | 0.429 | 0.432 | 0.432 | 0.433 | 0.434 | 0.436 | 0.439 | 0.441 | 0.443 | 0.442 | 0.442 | 0.445 | 0.446 | 0.45 | 0.451 | 0.453 | 0.451 | 0.455 | 0.458 | 0.46 | 0.463 | 0.465 | 0.466 | 0.465 | 0.468 | 0.467 | 0.465 | 0.469 | 0.465 | 0.465 | 0.465 | 0.459 | 0.455 | 0.448 | 0.437 | 0.433 | 0.424 | 0.42 | 0.414 | 0.41 | 0.406 | 0.405 | 0.402 | 0.403 | 0.401 | 0.4 | 0.399 | 0.4 | 0.405 | 0.409 | 0.419 | 0.425 | 0.432 | 0.436 | 0.441 | 0.443 | 0.446 | 0.444 | 0.441 | 0.436 | 0.436 | 0.069 | 0.061 | 0.053 | 0.047 | 0.042 | 0.038 | 0.035 | 0.032 | 0.03 | 0.028 | 0.027 | 0.027 | 0.026 | 0.027 | 0.028 | 0.03 | 0.034 | 0.04 | 0.046 | 0.055 | 0.063 | 0.075 | 0.087 | 0.099 | 0.112 | 0.124 | 0.135 | 0.145 | 0.154 | 0.16 | 0.163 | 0.162 | 0.16 | 0.156 | 0.15 | 0.146 | 0.139 | 0.135 | 0.131 | 0.129 | 0.127 | 0.124 | 0.122 | 0.12 | 0.12 | 0.12 | 0.119 | 0.117 | 0.115 | 0.114 | 0.111 | 0.112 | 0.111 | 0.111 | 0.113 | 0.114 | 0.116 | 0.12 | 0.125 | 0.131 | 0.137 | 0.145 | 0.151 | 0.159 | 0.169 | 0.178 | 0.187 | 0.2 | 0.207 | 0.221 | 0.23 | 0.241 | 0.25 | 0.259 | 0.269 | 0.28 | 0.289 | 0.299 | 0.305 | 0.312 | 0.315 | 0.317 | 0.315 | 0.307 | 0.299 | 0.28 | 0.266 | 0.24 | 0.22 | 0.192 | 0.172 | 0.145 | 0.127 | 0.105 | 0.091 | 0.078 | 0.494 | 0.506 | 0.52 | 0.527 | 0.538 | 0.543 | 0.551 | 0.557 | 0.562 | 0.566 | 0.569 | 0.572 | 0.573 | 0.573 | 0.572 | 0.569 | 0.564 | 0.557 | 0.549 | 0.536 | 0.526 | 0.508 | 0.494 | 0.474 | 0.457 | 0.443 | 0.428 | 0.418 | 0.406 | 0.401 | 0.394 | 0.393 | 0.394 | 0.397 | 0.399 | 0.404 | 0.407 | 0.411 | 0.416 | 0.417 | 0.418 | 0.417 | 0.417 | 0.416 | 0.418 | 0.418 | 0.415 | 0.416 | 0.415 | 0.415 | 0.416 | 0.417 | 0.415 | 0.413 | 0.41 | 0.406 | 0.403 | 0.397 | 0.393 | 0.383 | 0.377 | 0.369 | 0.358 | 0.352 | 0.341 | 0.328 | 0.322 | 0.309 | 0.303 | 0.296 | 0.287 | 0.279 | 0.272 | 0.265 | 0.259 | 0.253 | 0.247 | 0.243 | 0.239 | 0.236 | 0.237 | 0.239 | 0.244 | 0.25 | 0.258 | 0.27 | 0.281 | 0.304 | 0.322 | 0.349 | 0.37 | 0.396 | 0.418 | 0.445 | 0.465 | 0.479 | 0.006 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.006 | 0.008 | 0.009 | 0.01 | 0.012 | 0.013 | 0.014 | 0.016 | 0.017 | 0.018 | 0.02 | 0.021 | 0.021 | 0.022 | 0.022 | 0.022 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.019 | 0.019 | 0.018 | 0.018 | 0.017 | 0.017 | 0.017 | 0.017 | 0.018 | 0.019 | 0.02 | 0.022 | 0.024 | 0.026 | 0.028 | 0.032 | 0.036 | 0.041 | 0.046 | 0.05 | 0.056 | 0.059 | 0.062 | 0.062 | 0.06 | 0.059 | 0.056 | 0.054 | 0.051 | 0.048 | 0.044 | 0.042 | 0.038 | 0.035 | 0.031 | 0.028 | 0.025 | 0.022 | 0.019 | 0.016 | 0.014 | 0.013 | 0.009 | 0.008 | 0.007 | 1 | 1.066 | 1.088 | 1.194 | 1.182 | 1.226 | 1.364 | 1.277 | 1.128 | 1.088 | 1.032 | 1.003 | 1 | 0.986 | 1.011 | 0.778 | 0.676 | 0.635 | 0.647 | 0.587 | 0.619 | 0.697 | 0.885 | 0.882 | 1 | 0.96 | 0.948 | 1.023 | 1.126 | 1.122 | 0.99 | 1.111 | 1.218 | 1.193 | 1.095 | 1.117 | 1 | 0.922 | 0.768 | 0.575 | 0.397 | 0.326 | 0.306 | 0.282 | 0.351 | 0.447 | 0.657 | 0.701
sjv1500 | 0.98 | Belasting | 0 | 0.171 | 0.39 | 2.034 | 0.051 | 0.071 | 0.157 | 1.461 | 0.03 | 0.42 | 0.405 | 0.388 | 0.373 | 0.358 | 0.345 | 0.333 | 0.322 | 0.313 | 0.305 | 0.297 | 0.29 | 0.282 | 0.276 | 0.27 | 0.267 | 0.264 | 0.263 | 0.263 | 0.267 | 0.274 | 0.284 | 0.297 | 0.311 | 0.327 | 0.343 | 0.361 | 0.379 | 0.398 | 0.415 | 0.431 | 0.443 | 0.452 | 0.459 | 0.465 | 0.468 | 0.472 | 0.473 | 0.473 | 0.472 | 0.469 | 0.467 | 0.465 | 0.464 | 0.463 | 0.463 | 0.463 | 0.464 | 0.464 | 0.465 | 0.465 | 0.468 | 0.471 | 0.473 | 0.476 | 0.477 | 0.478 | 0.481 | 0.485 | 0.489 | 0.494 | 0.498 | 0.503 | 0.51 | 0.516 | 0.522 | 0.528 | 0.533 | 0.537 | 0.541 | 0.545 | 0.548 | 0.551 | 0.554 | 0.559 | 0.565 | 0.572 | 0.579 | 0.586 | 0.592 | 0.597 | 0.602 | 0.606 | 0.608 | 0.608 | 0.603 | 0.595 | 0.584 | 0.568 | 0.552 | 0.531 | 0.511 | 0.49 | 0.472 | 0.453 | 0.437 | 0.08 | 0.07 | 0.061 | 0.053 | 0.047 | 0.041 | 0.036 | 0.032 | 0.029 | 0.026 | 0.024 | 0.022 | 0.021 | 0.02 | 0.019 | 0.018 | 0.018 | 0.018 | 0.018 | 0.019 | 0.02 | 0.022 | 0.025 | 0.029 | 0.034 | 0.04 | 0.046 | 0.053 | 0.06 | 0.067 | 0.073 | 0.08 | 0.085 | 0.09 | 0.092 | 0.094 | 0.095 | 0.096 | 0.096 | 0.095 | 0.094 | 0.093 | 0.092 | 0.091 | 0.09 | 0.09 | 0.089 | 0.089 | 0.09 | 0.09 | 0.09 | 0.09 | 0.089 | 0.089 | 0.088 | 0.088 | 0.087 | 0.087 | 0.086 | 0.086 | 0.087 | 0.089 | 0.091 | 0.094 | 0.098 | 0.103 | 0.11 | 0.117 | 0.126 | 0.135 | 0.143 | 0.152 | 0.16 | 0.167 | 0.174 | 0.178 | 0.181 | 0.183 | 0.185 | 0.187 | 0.188 | 0.189 | 0.19 | 0.19 | 0.188 | 0.185 | 0.18 | 0.173 | 0.165 | 0.155 | 0.144 | 0.133 | 0.122 | 0.11 | 0.1 | 0.089 | 0.014 | 0.012 | 0.011 | 0.009 | 0.008 | 0.007 | 0.006 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.003 | 0.003 | 0.002 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.005 | 0.006 | 0.007 | 0.008 | 0.01 | 0.012 | 0.014 | 0.016 | 0.019 | 0.022 | 0.025 | 0.028 | 0.03 | 0.032 | 0.033 | 0.034 | 0.035 | 0.036 | 0.037 | 0.037 | 0.037 | 0.038 | 0.038 | 0.039 | 0.04 | 0.041 | 0.042 | 0.042 | 0.043 | 0.043 | 0.042 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.038 | 0.04 | 0.042 | 0.045 | 0.047 | 0.05 | 0.053 | 0.056 | 0.059 | 0.061 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.056 | 0.054 | 0.052 | 0.05 | 0.047 | 0.044 | 0.041 | 0.037 | 0.034 | 0.032 | 0.029 | 0.027 | 0.025 | 0.023 | 0.02 | 0.018 | 0.016 | 0.486 | 0.513 | 0.54 | 0.565 | 0.588 | 0.608 | 0.625 | 0.64 | 0.653 | 0.665 | 0.675 | 0.684 | 0.694 | 0.702 | 0.708 | 0.713 | 0.716 | 0.717 | 0.716 | 0.711 | 0.702 | 0.689 | 0.672 | 0.653 | 0.631 | 0.607 | 0.581 | 0.555 | 0.526 | 0.499 | 0.473 | 0.452 | 0.435 | 0.421 | 0.412 | 0.404 | 0.399 | 0.396 | 0.396 | 0.396 | 0.4 | 0.402 | 0.405 | 0.407 | 0.408 | 0.407 | 0.406 | 0.406 | 0.404 | 0.403 | 0.402 | 0.401 | 0.4 | 0.399 | 0.398 | 0.398 | 0.397 | 0.395 | 0.392 | 0.388 | 0.382 | 0.376 | 0.369 | 0.359 | 0.348 | 0.335 | 0.32 | 0.306 | 0.29 | 0.275 | 0.259 | 0.244 | 0.231 | 0.217 | 0.206 | 0.196 | 0.187 | 0.179 | 0.172 | 0.166 | 0.16 | 0.157 | 0.154 | 0.155 | 0.161 | 0.171 | 0.188 | 0.209 | 0.235 | 0.264 | 0.298 | 0.331 | 0.366 | 0.398 | 0.428 | 0.457 | 0.416 | 0.397 | 0.38 | 0.365 | 0.351 | 0.34 | 0.329 | 0.318 | 0.308 | 0.3 | 0.293 | 0.288 | 0.283 | 0.278 | 0.272 | 0.266 | 0.261 | 0.26 | 0.261 | 0.265 | 0.273 | 0.282 | 0.294 | 0.307 | 0.323 | 0.34 | 0.358 | 0.376 | 0.395 | 0.411 | 0.429 | 0.442 | 0.453 | 0.459 | 0.463 | 0.464 | 0.465 | 0.466 | 0.465 | 0.465 | 0.462 | 0.461 | 0.456 | 0.453 | 0.452 | 0.451 | 0.452 | 0.454 | 0.456 | 0.46 | 0.464 | 0.468 | 0.473 | 0.477 | 0.48 | 0.484 | 0.487 | 0.491 | 0.493 | 0.493 | 0.495 | 0.499 | 0.505 | 0.515 | 0.523 | 0.53 | 0.537 | 0.54 | 0.543 | 0.545 | 0.547 | 0.551 | 0.552 | 0.555 | 0.558 | 0.562 | 0.569 | 0.576 | 0.585 | 0.592 | 0.6 | 0.604 | 0.608 | 0.609 | 0.606 | 0.6 | 0.592 | 0.582 | 0.568 | 0.553 | 0.532 | 0.512 | 0.49 | 0.47 | 0.45 | 0.433 | 0.077 | 0.067 | 0.059 | 0.051 | 0.045 | 0.039 | 0.034 | 0.03 | 0.027 | 0.024 | 0.022 | 0.021 | 0.02 | 0.018 | 0.018 | 0.017 | 0.017 | 0.017 | 0.017 | 0.018 | 0.019 | 0.021 | 0.025 | 0.028 | 0.034 | 0.04 | 0.047 | 0.054 | 0.062 | 0.069 | 0.076 | 0.084 | 0.089 | 0.093 | 0.094 | 0.095 | 0.094 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.082 | 0.082 | 0.081 | 0.081 | 0.081 | 0.082 | 0.082 | 0.083 | 0.083 | 0.083 | 0.083 | 0.082 | 0.081 | 0.081 | 0.08 | 0.081 | 0.082 | 0.083 | 0.086 | 0.089 | 0.093 | 0.099 | 0.106 | 0.115 | 0.125 | 0.134 | 0.145 | 0.154 | 0.164 | 0.173 | 0.181 | 0.187 | 0.19 | 0.192 | 0.193 | 0.195 | 0.196 | 0.196 | 0.196 | 0.196 | 0.194 | 0.192 | 0.186 | 0.179 | 0.171 | 0.161 | 0.15 | 0.138 | 0.125 | 0.112 | 0.101 | 0.088 | 0.015 | 0.012 | 0.01 | 0.008 | 0.007 | 0.006 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.004 | 0.005 | 0.006 | 0.007 | 0.008 | 0.01 | 0.012 | 0.014 | 0.017 | 0.02 | 0.023 | 0.025 | 0.027 | 0.03 | 0.031 | 0.033 | 0.034 | 0.035 | 0.036 | 0.036 | 0.036 | 0.035 | 0.035 | 0.036 | 0.037 | 0.037 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.034 | 0.034 | 0.035 | 0.035 | 0.036 | 0.037 | 0.037 | 0.039 | 0.04 | 0.043 | 0.045 | 0.048 | 0.05 | 0.053 | 0.056 | 0.059 | 0.061 | 0.062 | 0.062 | 0.063 | 0.062 | 0.061 | 0.059 | 0.057 | 0.055 | 0.053 | 0.05 | 0.046 | 0.043 | 0.039 | 0.036 | 0.032 | 0.03 | 0.026 | 0.024 | 0.021 | 0.019 | 0.017 | 0.462 | 0.524 | 0.552 | 0.576 | 0.597 | 0.614 | 0.632 | 0.647 | 0.66 | 0.673 | 0.681 | 0.688 | 0.695 | 0.701 | 0.708 | 0.715 | 0.719 | 0.721 | 0.719 | 0.713 | 0.704 | 0.692 | 0.676 | 0.658 | 0.635 | 0.61 | 0.583 | 0.555 | 0.527 | 0.5 | 0.472 | 0.449 | 0.431 | 0.419 | 0.411 | 0.407 | 0.406 | 0.406 | 0.408 | 0.41 | 0.415 | 0.419 | 0.425 | 0.429 | 0.43 | 0.431 | 0.429 | 0.426 | 0.424 | 0.42 | 0.416 | 0.411 | 0.408 | 0.405 | 0.402 | 0.4 | 0.398 | 0.395 | 0.393 | 0.392 | 0.388 | 0.382 | 0.372 | 0.36 | 0.346 | 0.332 | 0.317 | 0.303 | 0.288 | 0.273 | 0.258 | 0.242 | 0.227 | 0.213 | 0.201 | 0.189 | 0.179 | 0.169 | 0.16 | 0.153 | 0.146 | 0.142 | 0.14 | 0.142 | 0.15 | 0.162 | 0.179 | 0.2 | 0.226 | 0.253 | 0.288 | 0.324 | 0.361 | 0.397 | 0.431 | 0.447 | 1 | 1.001 | 1.062 | 1.083 | 1.091 | 1.13 | 1.211 | 1.123 | 1.06 | 1.023 | 1.04 | 1.034 | 1 | 0.915 | 0.883 | 0.743 | 0.636 | 0.56 | 0.564 | 0.619 | 0.655 | 0.774 | 0.865 | 0.853 | 1 | 0.919 | 0.902 | 0.73 | 0.611 | 0.568 | 0.504 | 0.517 | 0.604 | 0.696 | 0.86 | 0.855 | 1 | 1.045 | 0.998 | 1.059 | 1.112 | 1.109 | 1.032 | 1.098 | 1.137 | 1.112 | 1.034 | 1.047
sjv2000 | 0.98 | Belasting | 0 | 0.231 | 0.459 | 2.864 | 0.067 | 0.098 | 0.174 | 2.254 | 0.036 | 0.42 | 0.405 | 0.388 | 0.373 | 0.358 | 0.345 | 0.333 | 0.322 | 0.313 | 0.305 | 0.297 | 0.29 | 0.282 | 0.276 | 0.27 | 0.267 | 0.264 | 0.263 | 0.263 | 0.267 | 0.274 | 0.284 | 0.297 | 0.311 | 0.327 | 0.343 | 0.361 | 0.379 | 0.398 | 0.415 | 0.431 | 0.443 | 0.452 | 0.459 | 0.465 | 0.468 | 0.472 | 0.473 | 0.473 | 0.472 | 0.469 | 0.467 | 0.465 | 0.464 | 0.463 | 0.463 | 0.463 | 0.464 | 0.464 | 0.465 | 0.465 | 0.468 | 0.471 | 0.473 | 0.476 | 0.477 | 0.478 | 0.481 | 0.485 | 0.489 | 0.494 | 0.498 | 0.503 | 0.51 | 0.516 | 0.522 | 0.528 | 0.533 | 0.537 | 0.541 | 0.545 | 0.548 | 0.551 | 0.554 | 0.559 | 0.565 | 0.572 | 0.579 | 0.586 | 0.592 | 0.597 | 0.602 | 0.606 | 0.608 | 0.608 | 0.603 | 0.595 | 0.584 | 0.568 | 0.552 | 0.531 | 0.511 | 0.49 | 0.472 | 0.453 | 0.437 | 0.08 | 0.07 | 0.061 | 0.053 | 0.047 | 0.041 | 0.036 | 0.032 | 0.029 | 0.026 | 0.024 | 0.022 | 0.021 | 0.02 | 0.019 | 0.018 | 0.018 | 0.018 | 0.018 | 0.019 | 0.02 | 0.022 | 0.025 | 0.029 | 0.034 | 0.04 | 0.046 | 0.053 | 0.06 | 0.067 | 0.073 | 0.08 | 0.085 | 0.09 | 0.092 | 0.094 | 0.095 | 0.096 | 0.096 | 0.095 | 0.094 | 0.093 | 0.092 | 0.091 | 0.09 | 0.09 | 0.089 | 0.089 | 0.09 | 0.09 | 0.09 | 0.09 | 0.089 | 0.089 | 0.088 | 0.088 | 0.087 | 0.087 | 0.086 | 0.086 | 0.087 | 0.089 | 0.091 | 0.094 | 0.098 | 0.103 | 0.11 | 0.117 | 0.126 | 0.135 | 0.143 | 0.152 | 0.16 | 0.167 | 0.174 | 0.178 | 0.181 | 0.183 | 0.185 | 0.187 | 0.188 | 0.189 | 0.19 | 0.19 | 0.188 | 0.185 | 0.18 | 0.173 | 0.165 | 0.155 | 0.144 | 0.133 | 0.122 | 0.11 | 0.1 | 0.089 | 0.014 | 0.012 | 0.011 | 0.009 | 0.008 | 0.007 | 0.006 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.003 | 0.003 | 0.002 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.005 | 0.006 | 0.007 | 0.008 | 0.01 | 0.012 | 0.014 | 0.016 | 0.019 | 0.022 | 0.025 | 0.028 | 0.03 | 0.032 | 0.033 | 0.034 | 0.035 | 0.036 | 0.037 | 0.037 | 0.037 | 0.038 | 0.038 | 0.039 | 0.04 | 0.041 | 0.042 | 0.042 | 0.043 | 0.043 | 0.042 | 0.04 | 0.039 | 0.038 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.038 | 0.04 | 0.042 | 0.045 | 0.047 | 0.05 | 0.053 | 0.056 | 0.059 | 0.061 | 0.062 | 0.061 | 0.06 | 0.059 | 0.058 | 0.056 | 0.054 | 0.052 | 0.05 | 0.047 | 0.044 | 0.041 | 0.037 | 0.034 | 0.032 | 0.029 | 0.027 | 0.025 | 0.023 | 0.02 | 0.018 | 0.016 | 0.486 | 0.513 | 0.54 | 0.565 | 0.588 | 0.608 | 0.625 | 0.64 | 0.653 | 0.665 | 0.675 | 0.684 | 0.694 | 0.702 | 0.708 | 0.713 | 0.716 | 0.717 | 0.716 | 0.711 | 0.702 | 0.689 | 0.672 | 0.653 | 0.631 | 0.607 | 0.581 | 0.555 | 0.526 | 0.499 | 0.473 | 0.452 | 0.435 | 0.421 | 0.412 | 0.404 | 0.399 | 0.396 | 0.396 | 0.396 | 0.4 | 0.402 | 0.405 | 0.407 | 0.408 | 0.407 | 0.406 | 0.406 | 0.404 | 0.403 | 0.402 | 0.401 | 0.4 | 0.399 | 0.398 | 0.398 | 0.397 | 0.395 | 0.392 | 0.388 | 0.382 | 0.376 | 0.369 | 0.359 | 0.348 | 0.335 | 0.32 | 0.306 | 0.29 | 0.275 | 0.259 | 0.244 | 0.231 | 0.217 | 0.206 | 0.196 | 0.187 | 0.179 | 0.172 | 0.166 | 0.16 | 0.157 | 0.154 | 0.155 | 0.161 | 0.171 | 0.188 | 0.209 | 0.235 | 0.264 | 0.298 | 0.331 | 0.366 | 0.398 | 0.428 | 0.457 | 0.416 | 0.397 | 0.38 | 0.365 | 0.351 | 0.34 | 0.329 | 0.318 | 0.308 | 0.3 | 0.293 | 0.288 | 0.283 | 0.278 | 0.272 | 0.266 | 0.261 | 0.26 | 0.261 | 0.265 | 0.273 | 0.282 | 0.294 | 0.307 | 0.323 | 0.34 | 0.358 | 0.376 | 0.395 | 0.411 | 0.429 | 0.442 | 0.453 | 0.459 | 0.463 | 0.464 | 0.465 | 0.466 | 0.465 | 0.465 | 0.462 | 0.461 | 0.456 | 0.453 | 0.452 | 0.451 | 0.452 | 0.454 | 0.456 | 0.46 | 0.464 | 0.468 | 0.473 | 0.477 | 0.48 | 0.484 | 0.487 | 0.491 | 0.493 | 0.493 | 0.495 | 0.499 | 0.505 | 0.515 | 0.523 | 0.53 | 0.537 | 0.54 | 0.543 | 0.545 | 0.547 | 0.551 | 0.552 | 0.555 | 0.558 | 0.562 | 0.569 | 0.576 | 0.585 | 0.592 | 0.6 | 0.604 | 0.608 | 0.609 | 0.606 | 0.6 | 0.592 | 0.582 | 0.568 | 0.553 | 0.532 | 0.512 | 0.49 | 0.47 | 0.45 | 0.433 | 0.077 | 0.067 | 0.059 | 0.051 | 0.045 | 0.039 | 0.034 | 0.03 | 0.027 | 0.024 | 0.022 | 0.021 | 0.02 | 0.018 | 0.018 | 0.017 | 0.017 | 0.017 | 0.017 | 0.018 | 0.019 | 0.021 | 0.025 | 0.028 | 0.034 | 0.04 | 0.047 | 0.054 | 0.062 | 0.069 | 0.076 | 0.084 | 0.089 | 0.093 | 0.094 | 0.095 | 0.094 | 0.093 | 0.091 | 0.089 | 0.087 | 0.085 | 0.083 | 0.082 | 0.082 | 0.082 | 0.081 | 0.081 | 0.081 | 0.082 | 0.082 | 0.083 | 0.083 | 0.083 | 0.083 | 0.082 | 0.081 | 0.081 | 0.08 | 0.081 | 0.082 | 0.083 | 0.086 | 0.089 | 0.093 | 0.099 | 0.106 | 0.115 | 0.125 | 0.134 | 0.145 | 0.154 | 0.164 | 0.173 | 0.181 | 0.187 | 0.19 | 0.192 | 0.193 | 0.195 | 0.196 | 0.196 | 0.196 | 0.196 | 0.194 | 0.192 | 0.186 | 0.179 | 0.171 | 0.161 | 0.15 | 0.138 | 0.125 | 0.112 | 0.101 | 0.088 | 0.015 | 0.012 | 0.01 | 0.008 | 0.007 | 0.006 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.004 | 0.005 | 0.006 | 0.007 | 0.008 | 0.01 | 0.012 | 0.014 | 0.017 | 0.02 | 0.023 | 0.025 | 0.027 | 0.03 | 0.031 | 0.033 | 0.034 | 0.035 | 0.036 | 0.036 | 0.036 | 0.035 | 0.035 | 0.036 | 0.037 | 0.037 | 0.038 | 0.038 | 0.038 | 0.038 | 0.038 | 0.037 | 0.036 | 0.036 | 0.035 | 0.034 | 0.034 | 0.033 | 0.034 | 0.034 | 0.035 | 0.035 | 0.036 | 0.037 | 0.037 | 0.039 | 0.04 | 0.043 | 0.045 | 0.048 | 0.05 | 0.053 | 0.056 | 0.059 | 0.061 | 0.062 | 0.062 | 0.063 | 0.062 | 0.061 | 0.059 | 0.057 | 0.055 | 0.053 | 0.05 | 0.046 | 0.043 | 0.039 | 0.036 | 0.032 | 0.03 | 0.026 | 0.024 | 0.021 | 0.019 | 0.017 | 0.462 | 0.524 | 0.552 | 0.576 | 0.597 | 0.614 | 0.632 | 0.647 | 0.66 | 0.673 | 0.681 | 0.688 | 0.695 | 0.701 | 0.708 | 0.715 | 0.719 | 0.721 | 0.719 | 0.713 | 0.704 | 0.692 | 0.676 | 0.658 | 0.635 | 0.61 | 0.583 | 0.555 | 0.527 | 0.5 | 0.472 | 0.449 | 0.431 | 0.419 | 0.411 | 0.407 | 0.406 | 0.406 | 0.408 | 0.41 | 0.415 | 0.419 | 0.425 | 0.429 | 0.43 | 0.431 | 0.429 | 0.426 | 0.424 | 0.42 | 0.416 | 0.411 | 0.408 | 0.405 | 0.402 | 0.4 | 0.398 | 0.395 | 0.393 | 0.392 | 0.388 | 0.382 | 0.372 | 0.36 | 0.346 | 0.332 | 0.317 | 0.303 | 0.288 | 0.273 | 0.258 | 0.242 | 0.227 | 0.213 | 0.201 | 0.189 | 0.179 | 0.169 | 0.16 | 0.153 | 0.146 | 0.142 | 0.14 | 0.142 | 0.15 | 0.162 | 0.179 | 0.2 | 0.226 | 0.253 | 0.288 | 0.324 | 0.361 | 0.397 | 0.431 | 0.447 | 1 | 1.001 | 1.062 | 1.083 | 1.091 | 1.13 | 1.211 | 1.123 | 1.06 | 1.023 | 1.04 | 1.034 | 1 | 0.915 | 0.883 | 0.743 | 0.636 | 0.56 | 0.564 | 0.619 | 0.655 | 0.774 | 0.865 | 0.853 | 1 | 0.919 | 0.902 | 0.73 | 0.611 | 0.568 | 0.504 | 0.517 | 0.604 | 0.696 | 0.86 | 0.855 | 1 | 1.045 | 0.998 | 1.059 | 1.112 | 1.109 | 1.032 | 1.098 | 1.137 | 1.112 | 1.034 | 1.047
sjv2500 | 0.98 | Belasting | 0 | 0.057 | 2.579 | 0.18 | 0.447 | 0.022 | 1.922 | 0.078 | 0.185 | 0.138 | 0.154 | 0.169 | 0.182 | 0.194 | 0.204 | 0.213 | 0.22 | 0.227 | 0.232 | 0.237 | 0.242 | 0.247 | 0.251 | 0.254 | 0.257 | 0.26 | 0.262 | 0.265 | 0.268 | 0.268 | 0.267 | 0.263 | 0.257 | 0.249 | 0.239 | 0.226 | 0.212 | 0.198 | 0.183 | 0.169 | 0.156 | 0.144 | 0.134 | 0.125 | 0.117 | 0.111 | 0.106 | 0.101 | 0.097 | 0.095 | 0.094 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.091 | 0.091 | 0.09 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.079 | 0.077 | 0.075 | 0.072 | 0.07 | 0.068 | 0.065 | 0.062 | 0.059 | 0.056 | 0.053 | 0.05 | 0.047 | 0.043 | 0.041 | 0.038 | 0.035 | 0.033 | 0.03 | 0.028 | 0.026 | 0.025 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.024 | 0.026 | 0.03 | 0.036 | 0.044 | 0.053 | 0.063 | 0.073 | 0.084 | 0.097 | 0.11 | 0.124 | 0.02 | 0.018 | 0.015 | 0.013 | 0.011 | 0.01 | 0.009 | 0.008 | 0.007 | 0.006 | 0.006 | 0.006 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.004 | 0.004 | 0.005 | 0.006 | 0.007 | 0.009 | 0.012 | 0.015 | 0.019 | 0.024 | 0.029 | 0.035 | 0.041 | 0.046 | 0.051 | 0.055 | 0.059 | 0.062 | 0.066 | 0.069 | 0.072 | 0.075 | 0.078 | 0.079 | 0.08 | 0.082 | 0.083 | 0.083 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.083 | 0.083 | 0.082 | 0.082 | 0.082 | 0.082 | 0.082 | 0.083 | 0.085 | 0.087 | 0.089 | 0.093 | 0.098 | 0.102 | 0.106 | 0.109 | 0.111 | 0.113 | 0.115 | 0.116 | 0.116 | 0.116 | 0.115 | 0.115 | 0.113 | 0.11 | 0.107 | 0.104 | 0.1 | 0.095 | 0.09 | 0.085 | 0.08 | 0.075 | 0.071 | 0.066 | 0.061 | 0.056 | 0.051 | 0.046 | 0.041 | 0.036 | 0.031 | 0.028 | 0.024 | 0.578 | 0.598 | 0.614 | 0.627 | 0.636 | 0.643 | 0.648 | 0.653 | 0.656 | 0.658 | 0.659 | 0.66 | 0.66 | 0.659 | 0.659 | 0.659 | 0.658 | 0.657 | 0.654 | 0.649 | 0.643 | 0.636 | 0.627 | 0.618 | 0.607 | 0.595 | 0.583 | 0.57 | 0.557 | 0.547 | 0.538 | 0.533 | 0.53 | 0.528 | 0.527 | 0.525 | 0.524 | 0.521 | 0.518 | 0.515 | 0.513 | 0.512 | 0.512 | 0.511 | 0.511 | 0.511 | 0.512 | 0.512 | 0.513 | 0.511 | 0.51 | 0.508 | 0.507 | 0.507 | 0.507 | 0.505 | 0.503 | 0.501 | 0.496 | 0.489 | 0.481 | 0.471 | 0.459 | 0.445 | 0.431 | 0.415 | 0.399 | 0.383 | 0.367 | 0.35 | 0.335 | 0.321 | 0.308 | 0.296 | 0.285 | 0.276 | 0.268 | 0.262 | 0.257 | 0.252 | 0.249 | 0.246 | 0.246 | 0.247 | 0.251 | 0.259 | 0.272 | 0.291 | 0.315 | 0.344 | 0.378 | 0.414 | 0.452 | 0.489 | 0.522 | 0.552 | 0.264 | 0.23 | 0.202 | 0.178 | 0.159 | 0.142 | 0.13 | 0.12 | 0.111 | 0.104 | 0.098 | 0.092 | 0.088 | 0.085 | 0.082 | 0.08 | 0.078 | 0.076 | 0.076 | 0.078 | 0.083 | 0.09 | 0.1 | 0.113 | 0.129 | 0.147 | 0.168 | 0.189 | 0.21 | 0.23 | 0.246 | 0.261 | 0.271 | 0.28 | 0.286 | 0.291 | 0.295 | 0.3 | 0.306 | 0.31 | 0.313 | 0.314 | 0.314 | 0.314 | 0.314 | 0.313 | 0.312 | 0.312 | 0.312 | 0.314 | 0.317 | 0.319 | 0.322 | 0.325 | 0.327 | 0.33 | 0.334 | 0.338 | 0.344 | 0.351 | 0.36 | 0.37 | 0.381 | 0.392 | 0.405 | 0.419 | 0.436 | 0.454 | 0.471 | 0.488 | 0.506 | 0.522 | 0.538 | 0.553 | 0.567 | 0.581 | 0.594 | 0.605 | 0.615 | 0.624 | 0.633 | 0.641 | 0.647 | 0.651 | 0.65 | 0.644 | 0.631 | 0.612 | 0.585 | 0.552 | 0.514 | 0.472 | 0.428 | 0.383 | 0.341 | 0.3 | 0.143 | 0.151 | 0.166 | 0.18 | 0.193 | 0.205 | 0.216 | 0.222 | 0.228 | 0.233 | 0.237 | 0.241 | 0.244 | 0.248 | 0.251 | 0.254 | 0.258 | 0.26 | 0.262 | 0.265 | 0.265 | 0.263 | 0.26 | 0.254 | 0.242 | 0.231 | 0.215 | 0.199 | 0.183 | 0.168 | 0.154 | 0.141 | 0.132 | 0.124 | 0.118 | 0.114 | 0.109 | 0.105 | 0.102 | 0.099 | 0.097 | 0.097 | 0.096 | 0.097 | 0.098 | 0.098 | 0.099 | 0.1 | 0.101 | 0.101 | 0.099 | 0.098 | 0.097 | 0.096 | 0.094 | 0.091 | 0.089 | 0.086 | 0.083 | 0.08 | 0.077 | 0.074 | 0.071 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.049 | 0.045 | 0.041 | 0.038 | 0.035 | 0.033 | 0.03 | 0.028 | 0.026 | 0.024 | 0.023 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.023 | 0.026 | 0.031 | 0.037 | 0.045 | 0.054 | 0.065 | 0.077 | 0.088 | 0.1 | 0.114 | 0.127 | 0.02 | 0.016 | 0.014 | 0.012 | 0.01 | 0.009 | 0.008 | 0.007 | 0.006 | 0.006 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.005 | 0.006 | 0.007 | 0.01 | 0.012 | 0.016 | 0.021 | 0.026 | 0.033 | 0.039 | 0.047 | 0.053 | 0.058 | 0.062 | 0.064 | 0.066 | 0.068 | 0.069 | 0.07 | 0.071 | 0.071 | 0.072 | 0.073 | 0.075 | 0.076 | 0.077 | 0.079 | 0.08 | 0.08 | 0.081 | 0.08 | 0.08 | 0.079 | 0.078 | 0.076 | 0.075 | 0.075 | 0.075 | 0.076 | 0.077 | 0.08 | 0.083 | 0.088 | 0.094 | 0.1 | 0.105 | 0.11 | 0.113 | 0.115 | 0.117 | 0.119 | 0.119 | 0.119 | 0.119 | 0.118 | 0.117 | 0.116 | 0.114 | 0.112 | 0.108 | 0.103 | 0.098 | 0.094 | 0.09 | 0.087 | 0.084 | 0.078 | 0.073 | 0.066 | 0.059 | 0.053 | 0.047 | 0.041 | 0.036 | 0.031 | 0.027 | 0.023 | 0.589 | 0.612 | 0.626 | 0.638 | 0.645 | 0.649 | 0.652 | 0.657 | 0.659 | 0.661 | 0.662 | 0.663 | 0.664 | 0.664 | 0.664 | 0.665 | 0.662 | 0.662 | 0.659 | 0.653 | 0.647 | 0.641 | 0.631 | 0.619 | 0.609 | 0.592 | 0.578 | 0.563 | 0.548 | 0.535 | 0.525 | 0.518 | 0.513 | 0.511 | 0.511 | 0.513 | 0.517 | 0.519 | 0.52 | 0.521 | 0.521 | 0.521 | 0.522 | 0.521 | 0.522 | 0.522 | 0.521 | 0.521 | 0.519 | 0.519 | 0.518 | 0.516 | 0.515 | 0.514 | 0.513 | 0.513 | 0.511 | 0.508 | 0.503 | 0.496 | 0.486 | 0.475 | 0.461 | 0.446 | 0.43 | 0.413 | 0.396 | 0.376 | 0.358 | 0.34 | 0.323 | 0.308 | 0.295 | 0.283 | 0.272 | 0.262 | 0.253 | 0.246 | 0.241 | 0.236 | 0.232 | 0.229 | 0.229 | 0.231 | 0.236 | 0.245 | 0.262 | 0.284 | 0.311 | 0.345 | 0.38 | 0.417 | 0.458 | 0.496 | 0.532 | 0.565 | 0.285 | 0.221 | 0.194 | 0.17 | 0.152 | 0.137 | 0.125 | 0.115 | 0.107 | 0.101 | 0.095 | 0.091 | 0.087 | 0.083 | 0.081 | 0.078 | 0.076 | 0.075 | 0.075 | 0.077 | 0.082 | 0.089 | 0.1 | 0.115 | 0.133 | 0.156 | 0.18 | 0.205 | 0.229 | 0.25 | 0.268 | 0.282 | 0.293 | 0.301 | 0.305 | 0.305 | 0.305 | 0.305 | 0.307 | 0.309 | 0.31 | 0.309 | 0.307 | 0.305 | 0.303 | 0.301 | 0.3 | 0.299 | 0.299 | 0.3 | 0.304 | 0.307 | 0.31 | 0.315 | 0.318 | 0.321 | 0.325 | 0.33 | 0.337 | 0.344 | 0.354 | 0.364 | 0.374 | 0.387 | 0.401 | 0.417 | 0.435 | 0.456 | 0.476 | 0.496 | 0.517 | 0.535 | 0.552 | 0.567 | 0.581 | 0.594 | 0.606 | 0.617 | 0.628 | 0.638 | 0.648 | 0.655 | 0.66 | 0.661 | 0.657 | 0.65 | 0.634 | 0.613 | 0.584 | 0.549 | 0.509 | 0.465 | 0.418 | 0.372 | 0.327 | 0.306 | 1 | 1.159 | 1.234 | 1.347 | 1.46 | 1.452 | 1.299 | 1.424 | 1.445 | 1.441 | 1.29 | 1.493 | 1 | 0.943 | 0.917 | 0.782 | 0.681 | 0.607 | 0.535 | 0.594 | 0.72 | 0.792 | 0.928 | 0.903 | 1 | 1.043 | 1.06 | 1.19 | 1.262 | 1.321 | 1.341 | 1.249 | 1.17 | 1.1 | 1.03 | 1.046 | 1 | 0.948 | 0.927 | 0.825 | 0.765 | 0.731 | 0.754 | 0.801 | 0.839 | 0.885 | 0.942 | 0.9
sjv3000 | 0.98 | Belasting | 0 | 0.047 | 2.294 | 0.129 | 0.435 | 0.008 | 1.59 | 0.059 | 0.196 | 0.138 | 0.154 | 0.169 | 0.182 | 0.194 | 0.204 | 0.213 | 0.22 | 0.227 | 0.232 | 0.237 | 0.242 | 0.247 | 0.251 | 0.254 | 0.257 | 0.26 | 0.262 | 0.265 | 0.268 | 0.268 | 0.267 | 0.263 | 0.257 | 0.249 | 0.239 | 0.226 | 0.212 | 0.198 | 0.183 | 0.169 | 0.156 | 0.144 | 0.134 | 0.125 | 0.117 | 0.111 | 0.106 | 0.101 | 0.097 | 0.095 | 0.094 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.092 | 0.091 | 0.091 | 0.09 | 0.09 | 0.088 | 0.086 | 0.085 | 0.083 | 0.081 | 0.079 | 0.077 | 0.075 | 0.072 | 0.07 | 0.068 | 0.065 | 0.062 | 0.059 | 0.056 | 0.053 | 0.05 | 0.047 | 0.043 | 0.041 | 0.038 | 0.035 | 0.033 | 0.03 | 0.028 | 0.026 | 0.025 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.024 | 0.026 | 0.03 | 0.036 | 0.044 | 0.053 | 0.063 | 0.073 | 0.084 | 0.097 | 0.11 | 0.124 | 0.02 | 0.018 | 0.015 | 0.013 | 0.011 | 0.01 | 0.009 | 0.008 | 0.007 | 0.006 | 0.006 | 0.006 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.004 | 0.004 | 0.005 | 0.006 | 0.007 | 0.009 | 0.012 | 0.015 | 0.019 | 0.024 | 0.029 | 0.035 | 0.041 | 0.046 | 0.051 | 0.055 | 0.059 | 0.062 | 0.066 | 0.069 | 0.072 | 0.075 | 0.078 | 0.079 | 0.08 | 0.082 | 0.083 | 0.083 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.084 | 0.083 | 0.083 | 0.082 | 0.082 | 0.082 | 0.082 | 0.082 | 0.083 | 0.085 | 0.087 | 0.089 | 0.093 | 0.098 | 0.102 | 0.106 | 0.109 | 0.111 | 0.113 | 0.115 | 0.116 | 0.116 | 0.116 | 0.115 | 0.115 | 0.113 | 0.11 | 0.107 | 0.104 | 0.1 | 0.095 | 0.09 | 0.085 | 0.08 | 0.075 | 0.071 | 0.066 | 0.061 | 0.056 | 0.051 | 0.046 | 0.041 | 0.036 | 0.031 | 0.028 | 0.024 | 0.578 | 0.598 | 0.614 | 0.627 | 0.636 | 0.643 | 0.648 | 0.653 | 0.656 | 0.658 | 0.659 | 0.66 | 0.66 | 0.659 | 0.659 | 0.659 | 0.658 | 0.657 | 0.654 | 0.649 | 0.643 | 0.636 | 0.627 | 0.618 | 0.607 | 0.595 | 0.583 | 0.57 | 0.557 | 0.547 | 0.538 | 0.533 | 0.53 | 0.528 | 0.527 | 0.525 | 0.524 | 0.521 | 0.518 | 0.515 | 0.513 | 0.512 | 0.512 | 0.511 | 0.511 | 0.511 | 0.512 | 0.512 | 0.513 | 0.511 | 0.51 | 0.508 | 0.507 | 0.507 | 0.507 | 0.505 | 0.503 | 0.501 | 0.496 | 0.489 | 0.481 | 0.471 | 0.459 | 0.445 | 0.431 | 0.415 | 0.399 | 0.383 | 0.367 | 0.35 | 0.335 | 0.321 | 0.308 | 0.296 | 0.285 | 0.276 | 0.268 | 0.262 | 0.257 | 0.252 | 0.249 | 0.246 | 0.246 | 0.247 | 0.251 | 0.259 | 0.272 | 0.291 | 0.315 | 0.344 | 0.378 | 0.414 | 0.452 | 0.489 | 0.522 | 0.552 | 0.264 | 0.23 | 0.202 | 0.178 | 0.159 | 0.142 | 0.13 | 0.12 | 0.111 | 0.104 | 0.098 | 0.092 | 0.088 | 0.085 | 0.082 | 0.08 | 0.078 | 0.076 | 0.076 | 0.078 | 0.083 | 0.09 | 0.1 | 0.113 | 0.129 | 0.147 | 0.168 | 0.189 | 0.21 | 0.23 | 0.246 | 0.261 | 0.271 | 0.28 | 0.286 | 0.291 | 0.295 | 0.3 | 0.306 | 0.31 | 0.313 | 0.314 | 0.314 | 0.314 | 0.314 | 0.313 | 0.312 | 0.312 | 0.312 | 0.314 | 0.317 | 0.319 | 0.322 | 0.325 | 0.327 | 0.33 | 0.334 | 0.338 | 0.344 | 0.351 | 0.36 | 0.37 | 0.381 | 0.392 | 0.405 | 0.419 | 0.436 | 0.454 | 0.471 | 0.488 | 0.506 | 0.522 | 0.538 | 0.553 | 0.567 | 0.581 | 0.594 | 0.605 | 0.615 | 0.624 | 0.633 | 0.641 | 0.647 | 0.651 | 0.65 | 0.644 | 0.631 | 0.612 | 0.585 | 0.552 | 0.514 | 0.472 | 0.428 | 0.383 | 0.341 | 0.3 | 0.143 | 0.151 | 0.166 | 0.18 | 0.193 | 0.205 | 0.216 | 0.222 | 0.228 | 0.233 | 0.237 | 0.241 | 0.244 | 0.248 | 0.251 | 0.254 | 0.258 | 0.26 | 0.262 | 0.265 | 0.265 | 0.263 | 0.26 | 0.254 | 0.242 | 0.231 | 0.215 | 0.199 | 0.183 | 0.168 | 0.154 | 0.141 | 0.132 | 0.124 | 0.118 | 0.114 | 0.109 | 0.105 | 0.102 | 0.099 | 0.097 | 0.097 | 0.096 | 0.097 | 0.098 | 0.098 | 0.099 | 0.1 | 0.101 | 0.101 | 0.099 | 0.098 | 0.097 | 0.096 | 0.094 | 0.091 | 0.089 | 0.086 | 0.083 | 0.08 | 0.077 | 0.074 | 0.071 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.049 | 0.045 | 0.041 | 0.038 | 0.035 | 0.033 | 0.03 | 0.028 | 0.026 | 0.024 | 0.023 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.023 | 0.026 | 0.031 | 0.037 | 0.045 | 0.054 | 0.065 | 0.077 | 0.088 | 0.1 | 0.114 | 0.127 | 0.02 | 0.016 | 0.014 | 0.012 | 0.01 | 0.009 | 0.008 | 0.007 | 0.006 | 0.006 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.004 | 0.005 | 0.006 | 0.007 | 0.01 | 0.012 | 0.016 | 0.021 | 0.026 | 0.033 | 0.039 | 0.047 | 0.053 | 0.058 | 0.062 | 0.064 | 0.066 | 0.068 | 0.069 | 0.07 | 0.071 | 0.071 | 0.072 | 0.073 | 0.075 | 0.076 | 0.077 | 0.079 | 0.08 | 0.08 | 0.081 | 0.08 | 0.08 | 0.079 | 0.078 | 0.076 | 0.075 | 0.075 | 0.075 | 0.076 | 0.077 | 0.08 | 0.083 | 0.088 | 0.094 | 0.1 | 0.105 | 0.11 | 0.113 | 0.115 | 0.117 | 0.119 | 0.119 | 0.119 | 0.119 | 0.118 | 0.117 | 0.116 | 0.114 | 0.112 | 0.108 | 0.103 | 0.098 | 0.094 | 0.09 | 0.087 | 0.084 | 0.078 | 0.073 | 0.066 | 0.059 | 0.053 | 0.047 | 0.041 | 0.036 | 0.031 | 0.027 | 0.023 | 0.589 | 0.612 | 0.626 | 0.638 | 0.645 | 0.649 | 0.652 | 0.657 | 0.659 | 0.661 | 0.662 | 0.663 | 0.664 | 0.664 | 0.664 | 0.665 | 0.662 | 0.662 | 0.659 | 0.653 | 0.647 | 0.641 | 0.631 | 0.619 | 0.609 | 0.592 | 0.578 | 0.563 | 0.548 | 0.535 | 0.525 | 0.518 | 0.513 | 0.511 | 0.511 | 0.513 | 0.517 | 0.519 | 0.52 | 0.521 | 0.521 | 0.521 | 0.522 | 0.521 | 0.522 | 0.522 | 0.521 | 0.521 | 0.519 | 0.519 | 0.518 | 0.516 | 0.515 | 0.514 | 0.513 | 0.513 | 0.511 | 0.508 | 0.503 | 0.496 | 0.486 | 0.475 | 0.461 | 0.446 | 0.43 | 0.413 | 0.396 | 0.376 | 0.358 | 0.34 | 0.323 | 0.308 | 0.295 | 0.283 | 0.272 | 0.262 | 0.253 | 0.246 | 0.241 | 0.236 | 0.232 | 0.229 | 0.229 | 0.231 | 0.236 | 0.245 | 0.262 | 0.284 | 0.311 | 0.345 | 0.38 | 0.417 | 0.458 | 0.496 | 0.532 | 0.565 | 0.285 | 0.221 | 0.194 | 0.17 | 0.152 | 0.137 | 0.125 | 0.115 | 0.107 | 0.101 | 0.095 | 0.091 | 0.087 | 0.083 | 0.081 | 0.078 | 0.076 | 0.075 | 0.075 | 0.077 | 0.082 | 0.089 | 0.1 | 0.115 | 0.133 | 0.156 | 0.18 | 0.205 | 0.229 | 0.25 | 0.268 | 0.282 | 0.293 | 0.301 | 0.305 | 0.305 | 0.305 | 0.305 | 0.307 | 0.309 | 0.31 | 0.309 | 0.307 | 0.305 | 0.303 | 0.301 | 0.3 | 0.299 | 0.299 | 0.3 | 0.304 | 0.307 | 0.31 | 0.315 | 0.318 | 0.321 | 0.325 | 0.33 | 0.337 | 0.344 | 0.354 | 0.364 | 0.374 | 0.387 | 0.401 | 0.417 | 0.435 | 0.456 | 0.476 | 0.496 | 0.517 | 0.535 | 0.552 | 0.567 | 0.581 | 0.594 | 0.606 | 0.617 | 0.628 | 0.638 | 0.648 | 0.655 | 0.66 | 0.661 | 0.657 | 0.65 | 0.634 | 0.613 | 0.584 | 0.549 | 0.509 | 0.465 | 0.418 | 0.372 | 0.327 | 0.306 | 1 | 1.159 | 1.234 | 1.347 | 1.46 | 1.452 | 1.299 | 1.424 | 1.445 | 1.441 | 1.29 | 1.493 | 1 | 0.943 | 0.917 | 0.782 | 0.681 | 0.607 | 0.535 | 0.594 | 0.72 | 0.792 | 0.928 | 0.903 | 1 | 1.043 | 1.06 | 1.19 | 1.262 | 1.321 | 1.341 | 1.249 | 1.17 | 1.1 | 1.03 | 1.046 | 1 | 0.948 | 0.927 | 0.825 | 0.765 | 0.731 | 0.754 | 0.801 | 0.839 | 0.885 | 0.942 | 0.9
sjv3500 | 0.98 | Belasting | 0 | 0.195 | 2.671 | 0.078 | 0.515 | 0.074 | 1.98 | 0.028 | 0.194 | 0.418 | 0.412 | 0.405 | 0.398 | 0.391 | 0.383 | 0.376 | 0.37 | 0.364 | 0.359 | 0.354 | 0.349 | 0.345 | 0.341 | 0.338 | 0.337 | 0.335 | 0.333 | 0.333 | 0.334 | 0.337 | 0.343 | 0.351 | 0.36 | 0.371 | 0.385 | 0.397 | 0.41 | 0.422 | 0.431 | 0.439 | 0.448 | 0.454 | 0.459 | 0.463 | 0.467 | 0.47 | 0.473 | 0.473 | 0.473 | 0.473 | 0.471 | 0.469 | 0.467 | 0.465 | 0.463 | 0.461 | 0.459 | 0.458 | 0.457 | 0.458 | 0.458 | 0.458 | 0.46 | 0.46 | 0.461 | 0.461 | 0.46 | 0.459 | 0.458 | 0.455 | 0.451 | 0.445 | 0.437 | 0.428 | 0.418 | 0.407 | 0.395 | 0.383 | 0.371 | 0.359 | 0.349 | 0.341 | 0.334 | 0.329 | 0.325 | 0.321 | 0.32 | 0.318 | 0.318 | 0.319 | 0.321 | 0.324 | 0.329 | 0.336 | 0.345 | 0.355 | 0.367 | 0.379 | 0.391 | 0.403 | 0.411 | 0.418 | 0.421 | 0.423 | 0.421 | 0.025 | 0.023 | 0.02 | 0.018 | 0.016 | 0.014 | 0.013 | 0.012 | 0.011 | 0.01 | 0.009 | 0.009 | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 0.009 | 0.01 | 0.011 | 0.012 | 0.015 | 0.017 | 0.021 | 0.024 | 0.028 | 0.033 | 0.037 | 0.042 | 0.047 | 0.052 | 0.056 | 0.06 | 0.064 | 0.067 | 0.07 | 0.074 | 0.076 | 0.079 | 0.082 | 0.084 | 0.086 | 0.088 | 0.09 | 0.092 | 0.093 | 0.095 | 0.096 | 0.096 | 0.096 | 0.095 | 0.094 | 0.092 | 0.091 | 0.089 | 0.088 | 0.087 | 0.087 | 0.088 | 0.09 | 0.092 | 0.094 | 0.097 | 0.101 | 0.105 | 0.111 | 0.117 | 0.123 | 0.127 | 0.13 | 0.131 | 0.129 | 0.127 | 0.124 | 0.12 | 0.116 | 0.113 | 0.109 | 0.105 | 0.101 | 0.097 | 0.092 | 0.088 | 0.083 | 0.077 | 0.071 | 0.065 | 0.059 | 0.054 | 0.049 | 0.044 | 0.04 | 0.035 | 0.031 | 0.028 | 0.369 | 0.399 | 0.429 | 0.455 | 0.477 | 0.499 | 0.518 | 0.534 | 0.549 | 0.562 | 0.575 | 0.586 | 0.595 | 0.603 | 0.608 | 0.612 | 0.615 | 0.618 | 0.617 | 0.615 | 0.608 | 0.597 | 0.581 | 0.562 | 0.538 | 0.508 | 0.478 | 0.446 | 0.414 | 0.385 | 0.359 | 0.335 | 0.316 | 0.303 | 0.291 | 0.284 | 0.279 | 0.275 | 0.272 | 0.27 | 0.268 | 0.267 | 0.266 | 0.265 | 0.265 | 0.264 | 0.263 | 0.262 | 0.26 | 0.257 | 0.255 | 0.252 | 0.25 | 0.248 | 0.247 | 0.246 | 0.244 | 0.241 | 0.237 | 0.23 | 0.222 | 0.214 | 0.205 | 0.195 | 0.182 | 0.169 | 0.156 | 0.144 | 0.133 | 0.124 | 0.117 | 0.11 | 0.103 | 0.097 | 0.091 | 0.084 | 0.079 | 0.074 | 0.07 | 0.066 | 0.064 | 0.062 | 0.062 | 0.063 | 0.069 | 0.077 | 0.088 | 0.104 | 0.123 | 0.145 | 0.171 | 0.201 | 0.234 | 0.268 | 0.302 | 0.336 | 0.189 | 0.166 | 0.146 | 0.13 | 0.116 | 0.104 | 0.093 | 0.084 | 0.076 | 0.068 | 0.062 | 0.057 | 0.052 | 0.049 | 0.046 | 0.043 | 0.042 | 0.041 | 0.04 | 0.042 | 0.044 | 0.048 | 0.054 | 0.061 | 0.071 | 0.083 | 0.096 | 0.111 | 0.127 | 0.142 | 0.155 | 0.165 | 0.174 | 0.178 | 0.182 | 0.182 | 0.18 | 0.178 | 0.178 | 0.177 | 0.178 | 0.178 | 0.179 | 0.179 | 0.18 | 0.181 | 0.183 | 0.184 | 0.187 | 0.189 | 0.192 | 0.195 | 0.198 | 0.2 | 0.202 | 0.204 | 0.207 | 0.212 | 0.217 | 0.224 | 0.233 | 0.243 | 0.256 | 0.272 | 0.289 | 0.308 | 0.327 | 0.344 | 0.361 | 0.378 | 0.394 | 0.41 | 0.426 | 0.442 | 0.457 | 0.471 | 0.483 | 0.494 | 0.503 | 0.511 | 0.517 | 0.52 | 0.522 | 0.52 | 0.513 | 0.501 | 0.485 | 0.465 | 0.439 | 0.41 | 0.377 | 0.343 | 0.308 | 0.275 | 0.244 | 0.215 | 0.409 | 0.401 | 0.394 | 0.388 | 0.381 | 0.375 | 0.369 | 0.362 | 0.356 | 0.35 | 0.345 | 0.342 | 0.34 | 0.339 | 0.337 | 0.335 | 0.335 | 0.332 | 0.332 | 0.332 | 0.334 | 0.34 | 0.348 | 0.358 | 0.369 | 0.383 | 0.395 | 0.406 | 0.417 | 0.425 | 0.432 | 0.442 | 0.449 | 0.455 | 0.461 | 0.465 | 0.468 | 0.47 | 0.471 | 0.471 | 0.471 | 0.471 | 0.471 | 0.471 | 0.471 | 0.47 | 0.471 | 0.473 | 0.474 | 0.475 | 0.475 | 0.476 | 0.477 | 0.479 | 0.479 | 0.478 | 0.477 | 0.476 | 0.476 | 0.474 | 0.474 | 0.471 | 0.465 | 0.457 | 0.444 | 0.431 | 0.418 | 0.405 | 0.391 | 0.377 | 0.364 | 0.353 | 0.343 | 0.335 | 0.329 | 0.324 | 0.322 | 0.32 | 0.319 | 0.319 | 0.321 | 0.325 | 0.331 | 0.338 | 0.344 | 0.352 | 0.36 | 0.368 | 0.377 | 0.386 | 0.396 | 0.404 | 0.411 | 0.415 | 0.417 | 0.413 | 0.025 | 0.022 | 0.019 | 0.017 | 0.015 | 0.013 | 0.012 | 0.011 | 0.01 | 0.009 | 0.008 | 0.008 | 0.007 | 0.007 | 0.007 | 0.007 | 0.008 | 0.008 | 0.008 | 0.009 | 0.01 | 0.012 | 0.014 | 0.017 | 0.021 | 0.025 | 0.031 | 0.037 | 0.043 | 0.049 | 0.055 | 0.059 | 0.061 | 0.064 | 0.065 | 0.067 | 0.07 | 0.071 | 0.072 | 0.073 | 0.073 | 0.075 | 0.077 | 0.08 | 0.083 | 0.085 | 0.087 | 0.087 | 0.087 | 0.086 | 0.086 | 0.086 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.077 | 0.076 | 0.077 | 0.079 | 0.082 | 0.087 | 0.092 | 0.098 | 0.105 | 0.111 | 0.117 | 0.123 | 0.126 | 0.129 | 0.13 | 0.129 | 0.128 | 0.125 | 0.122 | 0.118 | 0.114 | 0.11 | 0.106 | 0.101 | 0.097 | 0.092 | 0.087 | 0.083 | 0.078 | 0.073 | 0.068 | 0.062 | 0.055 | 0.05 | 0.044 | 0.039 | 0.035 | 0.031 | 0.028 | 0.391 | 0.423 | 0.451 | 0.474 | 0.495 | 0.513 | 0.53 | 0.546 | 0.561 | 0.574 | 0.586 | 0.595 | 0.601 | 0.606 | 0.611 | 0.614 | 0.616 | 0.618 | 0.618 | 0.616 | 0.611 | 0.599 | 0.584 | 0.563 | 0.537 | 0.506 | 0.474 | 0.44 | 0.405 | 0.375 | 0.348 | 0.324 | 0.304 | 0.289 | 0.279 | 0.274 | 0.273 | 0.275 | 0.275 | 0.277 | 0.279 | 0.279 | 0.279 | 0.278 | 0.277 | 0.274 | 0.272 | 0.268 | 0.265 | 0.261 | 0.257 | 0.253 | 0.25 | 0.248 | 0.248 | 0.248 | 0.248 | 0.247 | 0.244 | 0.239 | 0.232 | 0.222 | 0.21 | 0.197 | 0.183 | 0.169 | 0.155 | 0.142 | 0.131 | 0.121 | 0.113 | 0.105 | 0.099 | 0.092 | 0.085 | 0.079 | 0.072 | 0.067 | 0.062 | 0.058 | 0.056 | 0.054 | 0.055 | 0.057 | 0.063 | 0.073 | 0.088 | 0.106 | 0.129 | 0.156 | 0.186 | 0.218 | 0.252 | 0.287 | 0.322 | 0.358 | 0.201 | 0.154 | 0.136 | 0.121 | 0.109 | 0.098 | 0.089 | 0.081 | 0.073 | 0.067 | 0.061 | 0.056 | 0.052 | 0.048 | 0.045 | 0.043 | 0.042 | 0.041 | 0.041 | 0.042 | 0.045 | 0.049 | 0.054 | 0.062 | 0.073 | 0.086 | 0.1 | 0.117 | 0.134 | 0.151 | 0.165 | 0.176 | 0.186 | 0.192 | 0.194 | 0.193 | 0.189 | 0.184 | 0.181 | 0.179 | 0.177 | 0.175 | 0.172 | 0.171 | 0.17 | 0.17 | 0.171 | 0.172 | 0.175 | 0.178 | 0.182 | 0.185 | 0.188 | 0.19 | 0.192 | 0.195 | 0.197 | 0.2 | 0.204 | 0.209 | 0.216 | 0.225 | 0.238 | 0.254 | 0.274 | 0.295 | 0.316 | 0.336 | 0.356 | 0.375 | 0.394 | 0.412 | 0.429 | 0.445 | 0.461 | 0.475 | 0.488 | 0.499 | 0.509 | 0.517 | 0.522 | 0.524 | 0.522 | 0.518 | 0.51 | 0.497 | 0.48 | 0.458 | 0.432 | 0.403 | 0.369 | 0.334 | 0.297 | 0.263 | 0.23 | 0.215 | 1 | 0.986 | 1.019 | 1.108 | 1.173 | 1.225 | 1.296 | 1.185 | 1.101 | 1.031 | 0.987 | 0.962 | 1 | 0.952 | 0.949 | 0.79 | 0.638 | 0.597 | 0.528 | 0.575 | 0.656 | 0.747 | 0.933 | 0.862 | 1 | 1.051 | 1.102 | 1.13 | 1.277 | 1.245 | 1.192 | 1.254 | 1.236 | 1.132 | 0.958 | 1.044 | 1 | 0.991 | 0.912 | 0.843 | 0.702 | 0.682 | 0.669 | 0.729 | 0.812 | 0.945 | 1.072 | 1.056
sjv4000 | 0.98 | Belasting | 0 | 0.262 | 3.047 | 0.109 | 0.596 | 0.09 | 2.371 | 0.048 | 0.192 | 0.418 | 0.412 | 0.405 | 0.398 | 0.391 | 0.383 | 0.376 | 0.37 | 0.364 | 0.359 | 0.354 | 0.349 | 0.345 | 0.341 | 0.338 | 0.337 | 0.335 | 0.333 | 0.333 | 0.334 | 0.337 | 0.343 | 0.351 | 0.36 | 0.371 | 0.385 | 0.397 | 0.41 | 0.422 | 0.431 | 0.439 | 0.448 | 0.454 | 0.459 | 0.463 | 0.467 | 0.47 | 0.473 | 0.473 | 0.473 | 0.473 | 0.471 | 0.469 | 0.467 | 0.465 | 0.463 | 0.461 | 0.459 | 0.458 | 0.457 | 0.458 | 0.458 | 0.458 | 0.46 | 0.46 | 0.461 | 0.461 | 0.46 | 0.459 | 0.458 | 0.455 | 0.451 | 0.445 | 0.437 | 0.428 | 0.418 | 0.407 | 0.395 | 0.383 | 0.371 | 0.359 | 0.349 | 0.341 | 0.334 | 0.329 | 0.325 | 0.321 | 0.32 | 0.318 | 0.318 | 0.319 | 0.321 | 0.324 | 0.329 | 0.336 | 0.345 | 0.355 | 0.367 | 0.379 | 0.391 | 0.403 | 0.411 | 0.418 | 0.421 | 0.423 | 0.421 | 0.025 | 0.023 | 0.02 | 0.018 | 0.016 | 0.014 | 0.013 | 0.012 | 0.011 | 0.01 | 0.009 | 0.009 | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 0.008 | 0.009 | 0.01 | 0.011 | 0.012 | 0.015 | 0.017 | 0.021 | 0.024 | 0.028 | 0.033 | 0.037 | 0.042 | 0.047 | 0.052 | 0.056 | 0.06 | 0.064 | 0.067 | 0.07 | 0.074 | 0.076 | 0.079 | 0.082 | 0.084 | 0.086 | 0.088 | 0.09 | 0.092 | 0.093 | 0.095 | 0.096 | 0.096 | 0.096 | 0.095 | 0.094 | 0.092 | 0.091 | 0.089 | 0.088 | 0.087 | 0.087 | 0.088 | 0.09 | 0.092 | 0.094 | 0.097 | 0.101 | 0.105 | 0.111 | 0.117 | 0.123 | 0.127 | 0.13 | 0.131 | 0.129 | 0.127 | 0.124 | 0.12 | 0.116 | 0.113 | 0.109 | 0.105 | 0.101 | 0.097 | 0.092 | 0.088 | 0.083 | 0.077 | 0.071 | 0.065 | 0.059 | 0.054 | 0.049 | 0.044 | 0.04 | 0.035 | 0.031 | 0.028 | 0.369 | 0.399 | 0.429 | 0.455 | 0.477 | 0.499 | 0.518 | 0.534 | 0.549 | 0.562 | 0.575 | 0.586 | 0.595 | 0.603 | 0.608 | 0.612 | 0.615 | 0.618 | 0.617 | 0.615 | 0.608 | 0.597 | 0.581 | 0.562 | 0.538 | 0.508 | 0.478 | 0.446 | 0.414 | 0.385 | 0.359 | 0.335 | 0.316 | 0.303 | 0.291 | 0.284 | 0.279 | 0.275 | 0.272 | 0.27 | 0.268 | 0.267 | 0.266 | 0.265 | 0.265 | 0.264 | 0.263 | 0.262 | 0.26 | 0.257 | 0.255 | 0.252 | 0.25 | 0.248 | 0.247 | 0.246 | 0.244 | 0.241 | 0.237 | 0.23 | 0.222 | 0.214 | 0.205 | 0.195 | 0.182 | 0.169 | 0.156 | 0.144 | 0.133 | 0.124 | 0.117 | 0.11 | 0.103 | 0.097 | 0.091 | 0.084 | 0.079 | 0.074 | 0.07 | 0.066 | 0.064 | 0.062 | 0.062 | 0.063 | 0.069 | 0.077 | 0.088 | 0.104 | 0.123 | 0.145 | 0.171 | 0.201 | 0.234 | 0.268 | 0.302 | 0.336 | 0.189 | 0.166 | 0.146 | 0.13 | 0.116 | 0.104 | 0.093 | 0.084 | 0.076 | 0.068 | 0.062 | 0.057 | 0.052 | 0.049 | 0.046 | 0.043 | 0.042 | 0.041 | 0.04 | 0.042 | 0.044 | 0.048 | 0.054 | 0.061 | 0.071 | 0.083 | 0.096 | 0.111 | 0.127 | 0.142 | 0.155 | 0.165 | 0.174 | 0.178 | 0.182 | 0.182 | 0.18 | 0.178 | 0.178 | 0.177 | 0.178 | 0.178 | 0.179 | 0.179 | 0.18 | 0.181 | 0.183 | 0.184 | 0.187 | 0.189 | 0.192 | 0.195 | 0.198 | 0.2 | 0.202 | 0.204 | 0.207 | 0.212 | 0.217 | 0.224 | 0.233 | 0.243 | 0.256 | 0.272 | 0.289 | 0.308 | 0.327 | 0.344 | 0.361 | 0.378 | 0.394 | 0.41 | 0.426 | 0.442 | 0.457 | 0.471 | 0.483 | 0.494 | 0.503 | 0.511 | 0.517 | 0.52 | 0.522 | 0.52 | 0.513 | 0.501 | 0.485 | 0.465 | 0.439 | 0.41 | 0.377 | 0.343 | 0.308 | 0.275 | 0.244 | 0.215 | 0.409 | 0.401 | 0.394 | 0.388 | 0.381 | 0.375 | 0.369 | 0.362 | 0.356 | 0.35 | 0.345 | 0.342 | 0.34 | 0.339 | 0.337 | 0.335 | 0.335 | 0.332 | 0.332 | 0.332 | 0.334 | 0.34 | 0.348 | 0.358 | 0.369 | 0.383 | 0.395 | 0.406 | 0.417 | 0.425 | 0.432 | 0.442 | 0.449 | 0.455 | 0.461 | 0.465 | 0.468 | 0.47 | 0.471 | 0.471 | 0.471 | 0.471 | 0.471 | 0.471 | 0.471 | 0.47 | 0.471 | 0.473 | 0.474 | 0.475 | 0.475 | 0.476 | 0.477 | 0.479 | 0.479 | 0.478 | 0.477 | 0.476 | 0.476 | 0.474 | 0.474 | 0.471 | 0.465 | 0.457 | 0.444 | 0.431 | 0.418 | 0.405 | 0.391 | 0.377 | 0.364 | 0.353 | 0.343 | 0.335 | 0.329 | 0.324 | 0.322 | 0.32 | 0.319 | 0.319 | 0.321 | 0.325 | 0.331 | 0.338 | 0.344 | 0.352 | 0.36 | 0.368 | 0.377 | 0.386 | 0.396 | 0.404 | 0.411 | 0.415 | 0.417 | 0.413 | 0.025 | 0.022 | 0.019 | 0.017 | 0.015 | 0.013 | 0.012 | 0.011 | 0.01 | 0.009 | 0.008 | 0.008 | 0.007 | 0.007 | 0.007 | 0.007 | 0.008 | 0.008 | 0.008 | 0.009 | 0.01 | 0.012 | 0.014 | 0.017 | 0.021 | 0.025 | 0.031 | 0.037 | 0.043 | 0.049 | 0.055 | 0.059 | 0.061 | 0.064 | 0.065 | 0.067 | 0.07 | 0.071 | 0.072 | 0.073 | 0.073 | 0.075 | 0.077 | 0.08 | 0.083 | 0.085 | 0.087 | 0.087 | 0.087 | 0.086 | 0.086 | 0.086 | 0.085 | 0.083 | 0.081 | 0.079 | 0.078 | 0.077 | 0.076 | 0.077 | 0.079 | 0.082 | 0.087 | 0.092 | 0.098 | 0.105 | 0.111 | 0.117 | 0.123 | 0.126 | 0.129 | 0.13 | 0.129 | 0.128 | 0.125 | 0.122 | 0.118 | 0.114 | 0.11 | 0.106 | 0.101 | 0.097 | 0.092 | 0.087 | 0.083 | 0.078 | 0.073 | 0.068 | 0.062 | 0.055 | 0.05 | 0.044 | 0.039 | 0.035 | 0.031 | 0.028 | 0.391 | 0.423 | 0.451 | 0.474 | 0.495 | 0.513 | 0.53 | 0.546 | 0.561 | 0.574 | 0.586 | 0.595 | 0.601 | 0.606 | 0.611 | 0.614 | 0.616 | 0.618 | 0.618 | 0.616 | 0.611 | 0.599 | 0.584 | 0.563 | 0.537 | 0.506 | 0.474 | 0.44 | 0.405 | 0.375 | 0.348 | 0.324 | 0.304 | 0.289 | 0.279 | 0.274 | 0.273 | 0.275 | 0.275 | 0.277 | 0.279 | 0.279 | 0.279 | 0.278 | 0.277 | 0.274 | 0.272 | 0.268 | 0.265 | 0.261 | 0.257 | 0.253 | 0.25 | 0.248 | 0.248 | 0.248 | 0.248 | 0.247 | 0.244 | 0.239 | 0.232 | 0.222 | 0.21 | 0.197 | 0.183 | 0.169 | 0.155 | 0.142 | 0.131 | 0.121 | 0.113 | 0.105 | 0.099 | 0.092 | 0.085 | 0.079 | 0.072 | 0.067 | 0.062 | 0.058 | 0.056 | 0.054 | 0.055 | 0.057 | 0.063 | 0.073 | 0.088 | 0.106 | 0.129 | 0.156 | 0.186 | 0.218 | 0.252 | 0.287 | 0.322 | 0.358 | 0.201 | 0.154 | 0.136 | 0.121 | 0.109 | 0.098 | 0.089 | 0.081 | 0.073 | 0.067 | 0.061 | 0.056 | 0.052 | 0.048 | 0.045 | 0.043 | 0.042 | 0.041 | 0.041 | 0.042 | 0.045 | 0.049 | 0.054 | 0.062 | 0.073 | 0.086 | 0.1 | 0.117 | 0.134 | 0.151 | 0.165 | 0.176 | 0.186 | 0.192 | 0.194 | 0.193 | 0.189 | 0.184 | 0.181 | 0.179 | 0.177 | 0.175 | 0.172 | 0.171 | 0.17 | 0.17 | 0.171 | 0.172 | 0.175 | 0.178 | 0.182 | 0.185 | 0.188 | 0.19 | 0.192 | 0.195 | 0.197 | 0.2 | 0.204 | 0.209 | 0.216 | 0.225 | 0.238 | 0.254 | 0.274 | 0.295 | 0.316 | 0.336 | 0.356 | 0.375 | 0.394 | 0.412 | 0.429 | 0.445 | 0.461 | 0.475 | 0.488 | 0.499 | 0.509 | 0.517 | 0.522 | 0.524 | 0.522 | 0.518 | 0.51 | 0.497 | 0.48 | 0.458 | 0.432 | 0.403 | 0.369 | 0.334 | 0.297 | 0.263 | 0.23 | 0.215 | 1 | 0.986 | 1.019 | 1.108 | 1.173 | 1.225 | 1.296 | 1.185 | 1.101 | 1.031 | 0.987 | 0.962 | 1 | 0.952 | 0.949 | 0.79 | 0.638 | 0.597 | 0.528 | 0.575 | 0.656 | 0.747 | 0.933 | 0.862 | 1 | 1.051 | 1.102 | 1.13 | 1.277 | 1.245 | 1.192 | 1.254 | 1.236 | 1.132 | 0.958 | 1.044 | 1 | 0.991 | 0.912 | 0.843 | 0.702 | 0.682 | 0.669 | 0.729 | 0.812 | 0.945 | 1.072 | 1.056
sjv4500 | 0.98 | Belasting | 0 | 0.614 | 0.083 | 0.262 | 3.253 | 0.24 | 0.048 | 0.081 | 2.532 | 0.347 | 0.314 | 0.287 | 0.262 | 0.24 | 0.22 | 0.203 | 0.187 | 0.173 | 0.162 | 0.152 | 0.144 | 0.137 | 0.13 | 0.125 | 0.121 | 0.117 | 0.115 | 0.114 | 0.114 | 0.116 | 0.119 | 0.127 | 0.136 | 0.149 | 0.164 | 0.18 | 0.196 | 0.213 | 0.23 | 0.244 | 0.254 | 0.263 | 0.27 | 0.276 | 0.281 | 0.284 | 0.288 | 0.291 | 0.295 | 0.297 | 0.299 | 0.302 | 0.305 | 0.308 | 0.312 | 0.316 | 0.32 | 0.324 | 0.328 | 0.332 | 0.336 | 0.34 | 0.344 | 0.347 | 0.35 | 0.353 | 0.356 | 0.36 | 0.365 | 0.373 | 0.381 | 0.39 | 0.402 | 0.416 | 0.431 | 0.447 | 0.462 | 0.476 | 0.49 | 0.502 | 0.514 | 0.525 | 0.535 | 0.545 | 0.554 | 0.564 | 0.575 | 0.586 | 0.596 | 0.607 | 0.615 | 0.621 | 0.623 | 0.62 | 0.614 | 0.601 | 0.588 | 0.569 | 0.549 | 0.523 | 0.498 | 0.469 | 0.44 | 0.409 | 0.378 | 0.164 | 0.181 | 0.199 | 0.215 | 0.23 | 0.244 | 0.257 | 0.27 | 0.281 | 0.292 | 0.301 | 0.31 | 0.317 | 0.324 | 0.328 | 0.332 | 0.337 | 0.34 | 0.342 | 0.341 | 0.337 | 0.331 | 0.321 | 0.309 | 0.292 | 0.275 | 0.255 | 0.237 | 0.218 | 0.201 | 0.186 | 0.174 | 0.164 | 0.157 | 0.152 | 0.149 | 0.148 | 0.148 | 0.149 | 0.148 | 0.148 | 0.146 | 0.145 | 0.144 | 0.143 | 0.143 | 0.144 | 0.143 | 0.143 | 0.143 | 0.142 | 0.142 | 0.141 | 0.14 | 0.139 | 0.138 | 0.137 | 0.135 | 0.133 | 0.13 | 0.126 | 0.121 | 0.115 | 0.109 | 0.103 | 0.096 | 0.089 | 0.082 | 0.075 | 0.068 | 0.062 | 0.057 | 0.052 | 0.048 | 0.045 | 0.042 | 0.04 | 0.038 | 0.036 | 0.035 | 0.033 | 0.032 | 0.031 | 0.031 | 0.032 | 0.034 | 0.038 | 0.044 | 0.052 | 0.061 | 0.072 | 0.085 | 0.1 | 0.115 | 0.131 | 0.147 | 0.455 | 0.474 | 0.486 | 0.498 | 0.508 | 0.516 | 0.522 | 0.527 | 0.53 | 0.532 | 0.534 | 0.534 | 0.535 | 0.535 | 0.536 | 0.537 | 0.536 | 0.535 | 0.535 | 0.535 | 0.536 | 0.538 | 0.539 | 0.54 | 0.54 | 0.539 | 0.537 | 0.534 | 0.529 | 0.524 | 0.518 | 0.513 | 0.507 | 0.501 | 0.495 | 0.488 | 0.482 | 0.477 | 0.471 | 0.466 | 0.462 | 0.458 | 0.454 | 0.45 | 0.444 | 0.438 | 0.432 | 0.428 | 0.424 | 0.42 | 0.416 | 0.413 | 0.41 | 0.408 | 0.407 | 0.405 | 0.402 | 0.4 | 0.395 | 0.391 | 0.388 | 0.383 | 0.378 | 0.371 | 0.362 | 0.352 | 0.343 | 0.333 | 0.323 | 0.315 | 0.307 | 0.299 | 0.293 | 0.287 | 0.282 | 0.276 | 0.27 | 0.262 | 0.255 | 0.248 | 0.242 | 0.238 | 0.237 | 0.239 | 0.246 | 0.256 | 0.269 | 0.283 | 0.3 | 0.318 | 0.338 | 0.357 | 0.377 | 0.397 | 0.417 | 0.438 | 0.034 | 0.031 | 0.028 | 0.025 | 0.023 | 0.02 | 0.018 | 0.017 | 0.015 | 0.014 | 0.013 | 0.012 | 0.012 | 0.011 | 0.011 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.011 | 0.012 | 0.013 | 0.015 | 0.019 | 0.023 | 0.028 | 0.033 | 0.039 | 0.045 | 0.052 | 0.059 | 0.066 | 0.072 | 0.077 | 0.082 | 0.085 | 0.088 | 0.089 | 0.091 | 0.093 | 0.096 | 0.099 | 0.102 | 0.105 | 0.106 | 0.108 | 0.109 | 0.109 | 0.109 | 0.11 | 0.109 | 0.109 | 0.108 | 0.107 | 0.108 | 0.109 | 0.11 | 0.112 | 0.113 | 0.114 | 0.116 | 0.117 | 0.118 | 0.119 | 0.12 | 0.122 | 0.123 | 0.125 | 0.127 | 0.129 | 0.13 | 0.131 | 0.13 | 0.129 | 0.128 | 0.126 | 0.125 | 0.123 | 0.121 | 0.118 | 0.115 | 0.111 | 0.107 | 0.101 | 0.096 | 0.091 | 0.085 | 0.079 | 0.073 | 0.067 | 0.061 | 0.054 | 0.048 | 0.043 | 0.038 | 0.326 | 0.3 | 0.275 | 0.251 | 0.229 | 0.209 | 0.192 | 0.177 | 0.165 | 0.153 | 0.144 | 0.136 | 0.129 | 0.123 | 0.119 | 0.116 | 0.113 | 0.112 | 0.111 | 0.111 | 0.113 | 0.117 | 0.126 | 0.136 | 0.151 | 0.166 | 0.185 | 0.203 | 0.222 | 0.241 | 0.255 | 0.267 | 0.276 | 0.282 | 0.286 | 0.288 | 0.29 | 0.29 | 0.289 | 0.288 | 0.286 | 0.286 | 0.288 | 0.291 | 0.294 | 0.297 | 0.3 | 0.305 | 0.308 | 0.312 | 0.316 | 0.318 | 0.322 | 0.324 | 0.327 | 0.33 | 0.334 | 0.34 | 0.345 | 0.352 | 0.359 | 0.367 | 0.378 | 0.392 | 0.408 | 0.426 | 0.445 | 0.462 | 0.478 | 0.493 | 0.508 | 0.521 | 0.534 | 0.546 | 0.556 | 0.566 | 0.576 | 0.586 | 0.597 | 0.606 | 0.615 | 0.623 | 0.627 | 0.63 | 0.627 | 0.621 | 0.609 | 0.594 | 0.573 | 0.549 | 0.52 | 0.491 | 0.459 | 0.427 | 0.393 | 0.358 | 0.17 | 0.183 | 0.199 | 0.214 | 0.228 | 0.241 | 0.255 | 0.268 | 0.281 | 0.292 | 0.301 | 0.309 | 0.316 | 0.321 | 0.325 | 0.33 | 0.334 | 0.337 | 0.338 | 0.338 | 0.333 | 0.328 | 0.319 | 0.306 | 0.289 | 0.27 | 0.248 | 0.227 | 0.207 | 0.188 | 0.173 | 0.16 | 0.15 | 0.142 | 0.139 | 0.138 | 0.14 | 0.144 | 0.147 | 0.15 | 0.152 | 0.153 | 0.154 | 0.155 | 0.155 | 0.155 | 0.155 | 0.153 | 0.152 | 0.15 | 0.149 | 0.148 | 0.147 | 0.146 | 0.145 | 0.144 | 0.142 | 0.139 | 0.136 | 0.133 | 0.128 | 0.123 | 0.116 | 0.109 | 0.102 | 0.093 | 0.085 | 0.077 | 0.069 | 0.062 | 0.056 | 0.05 | 0.045 | 0.042 | 0.039 | 0.037 | 0.035 | 0.033 | 0.031 | 0.03 | 0.028 | 0.027 | 0.026 | 0.026 | 0.028 | 0.03 | 0.035 | 0.041 | 0.05 | 0.06 | 0.074 | 0.087 | 0.103 | 0.12 | 0.136 | 0.153 | 0.469 | 0.485 | 0.499 | 0.511 | 0.522 | 0.53 | 0.535 | 0.539 | 0.54 | 0.541 | 0.543 | 0.544 | 0.545 | 0.545 | 0.546 | 0.545 | 0.542 | 0.541 | 0.542 | 0.541 | 0.543 | 0.544 | 0.542 | 0.543 | 0.542 | 0.54 | 0.538 | 0.535 | 0.529 | 0.522 | 0.515 | 0.508 | 0.502 | 0.497 | 0.492 | 0.487 | 0.481 | 0.476 | 0.473 | 0.471 | 0.469 | 0.466 | 0.462 | 0.456 | 0.452 | 0.448 | 0.444 | 0.439 | 0.437 | 0.435 | 0.433 | 0.433 | 0.431 | 0.43 | 0.428 | 0.426 | 0.423 | 0.419 | 0.416 | 0.411 | 0.408 | 0.403 | 0.397 | 0.388 | 0.377 | 0.365 | 0.354 | 0.341 | 0.33 | 0.318 | 0.308 | 0.299 | 0.291 | 0.281 | 0.273 | 0.265 | 0.258 | 0.25 | 0.243 | 0.237 | 0.233 | 0.229 | 0.229 | 0.231 | 0.238 | 0.247 | 0.262 | 0.278 | 0.297 | 0.318 | 0.34 | 0.363 | 0.384 | 0.406 | 0.429 | 0.451 | 0.038 | 0.031 | 0.028 | 0.024 | 0.022 | 0.019 | 0.017 | 0.016 | 0.014 | 0.013 | 0.012 | 0.012 | 0.011 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.009 | 0.01 | 0.01 | 0.011 | 0.013 | 0.015 | 0.019 | 0.023 | 0.029 | 0.035 | 0.042 | 0.049 | 0.057 | 0.065 | 0.072 | 0.079 | 0.083 | 0.087 | 0.089 | 0.09 | 0.091 | 0.092 | 0.093 | 0.095 | 0.096 | 0.098 | 0.099 | 0.1 | 0.102 | 0.103 | 0.103 | 0.103 | 0.102 | 0.101 | 0.1 | 0.099 | 0.099 | 0.1 | 0.101 | 0.102 | 0.103 | 0.104 | 0.105 | 0.107 | 0.109 | 0.111 | 0.114 | 0.116 | 0.117 | 0.12 | 0.124 | 0.126 | 0.128 | 0.13 | 0.131 | 0.131 | 0.132 | 0.133 | 0.131 | 0.131 | 0.129 | 0.127 | 0.124 | 0.121 | 0.117 | 0.112 | 0.107 | 0.101 | 0.095 | 0.087 | 0.08 | 0.073 | 0.066 | 0.059 | 0.053 | 0.047 | 0.042 | 0.04 | 1 | 0.95 | 0.88 | 0.861 | 0.869 | 0.793 | 0.808 | 0.842 | 0.919 | 1 | 1.101 | 1.05 | 1 | 1.143 | 1.211 | 1.213 | 1.154 | 1.298 | 1.223 | 1.265 | 1.144 | 1.049 | 0.912 | 0.978 | 1 | 1.017 | 1.088 | 1.199 | 1.263 | 1.344 | 1.378 | 1.31 | 1.2 | 1.111 | 0.963 | 1.014 | 1 | 0.971 | 0.945 | 0.734 | 0.613 | 0.507 | 0.452 | 0.475 | 0.624 | 0.686 | 0.87 | 0.836
sjv5000 | 0.98 | Belasting | 0 | 0.057 | 0.262 | 0.632 | 3.459 | 0.048 | 0.072 | 0.287 | 2.694 | 0.164 | 0.181 | 0.199 | 0.215 | 0.23 | 0.244 | 0.257 | 0.27 | 0.281 | 0.292 | 0.301 | 0.31 | 0.317 | 0.324 | 0.328 | 0.332 | 0.337 | 0.34 | 0.342 | 0.341 | 0.337 | 0.331 | 0.321 | 0.309 | 0.292 | 0.275 | 0.255 | 0.237 | 0.218 | 0.201 | 0.186 | 0.174 | 0.164 | 0.157 | 0.152 | 0.149 | 0.148 | 0.148 | 0.149 | 0.148 | 0.148 | 0.146 | 0.145 | 0.144 | 0.143 | 0.143 | 0.144 | 0.143 | 0.143 | 0.143 | 0.142 | 0.142 | 0.141 | 0.14 | 0.139 | 0.138 | 0.137 | 0.135 | 0.133 | 0.13 | 0.126 | 0.121 | 0.115 | 0.109 | 0.103 | 0.096 | 0.089 | 0.082 | 0.075 | 0.068 | 0.062 | 0.057 | 0.052 | 0.048 | 0.045 | 0.042 | 0.04 | 0.038 | 0.036 | 0.035 | 0.033 | 0.032 | 0.031 | 0.031 | 0.032 | 0.034 | 0.038 | 0.044 | 0.052 | 0.061 | 0.072 | 0.085 | 0.1 | 0.115 | 0.131 | 0.147 | 0.455 | 0.474 | 0.486 | 0.498 | 0.508 | 0.516 | 0.522 | 0.527 | 0.53 | 0.532 | 0.534 | 0.534 | 0.535 | 0.535 | 0.536 | 0.537 | 0.536 | 0.535 | 0.535 | 0.535 | 0.536 | 0.538 | 0.539 | 0.54 | 0.54 | 0.539 | 0.537 | 0.534 | 0.529 | 0.524 | 0.518 | 0.513 | 0.507 | 0.501 | 0.495 | 0.488 | 0.482 | 0.477 | 0.471 | 0.466 | 0.462 | 0.458 | 0.454 | 0.45 | 0.444 | 0.438 | 0.432 | 0.428 | 0.424 | 0.42 | 0.416 | 0.413 | 0.41 | 0.408 | 0.407 | 0.405 | 0.402 | 0.4 | 0.395 | 0.391 | 0.388 | 0.383 | 0.378 | 0.371 | 0.362 | 0.352 | 0.343 | 0.333 | 0.323 | 0.315 | 0.307 | 0.299 | 0.293 | 0.287 | 0.282 | 0.276 | 0.27 | 0.262 | 0.255 | 0.248 | 0.242 | 0.238 | 0.237 | 0.239 | 0.246 | 0.256 | 0.269 | 0.283 | 0.3 | 0.318 | 0.338 | 0.357 | 0.377 | 0.397 | 0.417 | 0.438 | 0.347 | 0.314 | 0.287 | 0.262 | 0.24 | 0.22 | 0.203 | 0.187 | 0.173 | 0.162 | 0.152 | 0.144 | 0.137 | 0.13 | 0.125 | 0.121 | 0.117 | 0.115 | 0.114 | 0.114 | 0.116 | 0.119 | 0.127 | 0.136 | 0.149 | 0.164 | 0.18 | 0.196 | 0.213 | 0.23 | 0.244 | 0.254 | 0.263 | 0.27 | 0.276 | 0.281 | 0.284 | 0.288 | 0.291 | 0.295 | 0.297 | 0.299 | 0.302 | 0.305 | 0.308 | 0.312 | 0.316 | 0.32 | 0.324 | 0.328 | 0.332 | 0.336 | 0.34 | 0.344 | 0.347 | 0.35 | 0.353 | 0.356 | 0.36 | 0.365 | 0.373 | 0.381 | 0.39 | 0.402 | 0.416 | 0.431 | 0.447 | 0.462 | 0.476 | 0.49 | 0.502 | 0.514 | 0.525 | 0.535 | 0.545 | 0.554 | 0.564 | 0.575 | 0.586 | 0.596 | 0.607 | 0.615 | 0.621 | 0.623 | 0.62 | 0.614 | 0.601 | 0.588 | 0.569 | 0.549 | 0.523 | 0.498 | 0.469 | 0.44 | 0.409 | 0.378 | 0.034 | 0.031 | 0.028 | 0.025 | 0.023 | 0.02 | 0.018 | 0.017 | 0.015 | 0.014 | 0.013 | 0.012 | 0.012 | 0.011 | 0.011 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.011 | 0.012 | 0.013 | 0.015 | 0.019 | 0.023 | 0.028 | 0.033 | 0.039 | 0.045 | 0.052 | 0.059 | 0.066 | 0.072 | 0.077 | 0.082 | 0.085 | 0.088 | 0.089 | 0.091 | 0.093 | 0.096 | 0.099 | 0.102 | 0.105 | 0.106 | 0.108 | 0.109 | 0.109 | 0.109 | 0.11 | 0.109 | 0.109 | 0.108 | 0.107 | 0.108 | 0.109 | 0.11 | 0.112 | 0.113 | 0.114 | 0.116 | 0.117 | 0.118 | 0.119 | 0.12 | 0.122 | 0.123 | 0.125 | 0.127 | 0.129 | 0.13 | 0.131 | 0.13 | 0.129 | 0.128 | 0.126 | 0.125 | 0.123 | 0.121 | 0.118 | 0.115 | 0.111 | 0.107 | 0.101 | 0.096 | 0.091 | 0.085 | 0.079 | 0.073 | 0.067 | 0.061 | 0.054 | 0.048 | 0.043 | 0.038 | 0.17 | 0.183 | 0.199 | 0.214 | 0.228 | 0.241 | 0.255 | 0.268 | 0.281 | 0.292 | 0.301 | 0.309 | 0.316 | 0.321 | 0.325 | 0.33 | 0.334 | 0.337 | 0.338 | 0.338 | 0.333 | 0.328 | 0.319 | 0.306 | 0.289 | 0.27 | 0.248 | 0.227 | 0.207 | 0.188 | 0.173 | 0.16 | 0.15 | 0.142 | 0.139 | 0.138 | 0.14 | 0.144 | 0.147 | 0.15 | 0.152 | 0.153 | 0.154 | 0.155 | 0.155 | 0.155 | 0.155 | 0.153 | 0.152 | 0.15 | 0.149 | 0.148 | 0.147 | 0.146 | 0.145 | 0.144 | 0.142 | 0.139 | 0.136 | 0.133 | 0.128 | 0.123 | 0.116 | 0.109 | 0.102 | 0.093 | 0.085 | 0.077 | 0.069 | 0.062 | 0.056 | 0.05 | 0.045 | 0.042 | 0.039 | 0.037 | 0.035 | 0.033 | 0.031 | 0.03 | 0.028 | 0.027 | 0.026 | 0.026 | 0.028 | 0.03 | 0.035 | 0.041 | 0.05 | 0.06 | 0.074 | 0.087 | 0.103 | 0.12 | 0.136 | 0.153 | 0.469 | 0.485 | 0.499 | 0.511 | 0.522 | 0.53 | 0.535 | 0.539 | 0.54 | 0.541 | 0.543 | 0.544 | 0.545 | 0.545 | 0.546 | 0.545 | 0.542 | 0.541 | 0.542 | 0.541 | 0.543 | 0.544 | 0.542 | 0.543 | 0.542 | 0.54 | 0.538 | 0.535 | 0.529 | 0.522 | 0.515 | 0.508 | 0.502 | 0.497 | 0.492 | 0.487 | 0.481 | 0.476 | 0.473 | 0.471 | 0.469 | 0.466 | 0.462 | 0.456 | 0.452 | 0.448 | 0.444 | 0.439 | 0.437 | 0.435 | 0.433 | 0.433 | 0.431 | 0.43 | 0.428 | 0.426 | 0.423 | 0.419 | 0.416 | 0.411 | 0.408 | 0.403 | 0.397 | 0.388 | 0.377 | 0.365 | 0.354 | 0.341 | 0.33 | 0.318 | 0.308 | 0.299 | 0.291 | 0.281 | 0.273 | 0.265 | 0.258 | 0.25 | 0.243 | 0.237 | 0.233 | 0.229 | 0.229 | 0.231 | 0.238 | 0.247 | 0.262 | 0.278 | 0.297 | 0.318 | 0.34 | 0.363 | 0.384 | 0.406 | 0.429 | 0.451 | 0.326 | 0.3 | 0.275 | 0.251 | 0.229 | 0.209 | 0.192 | 0.177 | 0.165 | 0.153 | 0.144 | 0.136 | 0.129 | 0.123 | 0.119 | 0.116 | 0.113 | 0.112 | 0.111 | 0.111 | 0.113 | 0.117 | 0.126 | 0.136 | 0.151 | 0.166 | 0.185 | 0.203 | 0.222 | 0.241 | 0.255 | 0.267 | 0.276 | 0.282 | 0.286 | 0.288 | 0.29 | 0.29 | 0.289 | 0.288 | 0.286 | 0.286 | 0.288 | 0.291 | 0.294 | 0.297 | 0.3 | 0.305 | 0.308 | 0.312 | 0.316 | 0.318 | 0.322 | 0.324 | 0.327 | 0.33 | 0.334 | 0.34 | 0.345 | 0.352 | 0.359 | 0.367 | 0.378 | 0.392 | 0.408 | 0.426 | 0.445 | 0.462 | 0.478 | 0.493 | 0.508 | 0.521 | 0.534 | 0.546 | 0.556 | 0.566 | 0.576 | 0.586 | 0.597 | 0.606 | 0.615 | 0.623 | 0.627 | 0.63 | 0.627 | 0.621 | 0.609 | 0.594 | 0.573 | 0.549 | 0.52 | 0.491 | 0.459 | 0.427 | 0.393 | 0.358 | 0.038 | 0.031 | 0.028 | 0.024 | 0.022 | 0.019 | 0.017 | 0.016 | 0.014 | 0.013 | 0.012 | 0.012 | 0.011 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.009 | 0.01 | 0.01 | 0.011 | 0.013 | 0.015 | 0.019 | 0.023 | 0.029 | 0.035 | 0.042 | 0.049 | 0.057 | 0.065 | 0.072 | 0.079 | 0.083 | 0.087 | 0.089 | 0.09 | 0.091 | 0.092 | 0.093 | 0.095 | 0.096 | 0.098 | 0.099 | 0.1 | 0.102 | 0.103 | 0.103 | 0.103 | 0.102 | 0.101 | 0.1 | 0.099 | 0.099 | 0.1 | 0.101 | 0.102 | 0.103 | 0.104 | 0.105 | 0.107 | 0.109 | 0.111 | 0.114 | 0.116 | 0.117 | 0.12 | 0.124 | 0.126 | 0.128 | 0.13 | 0.131 | 0.131 | 0.132 | 0.133 | 0.131 | 0.131 | 0.129 | 0.127 | 0.124 | 0.121 | 0.117 | 0.112 | 0.107 | 0.101 | 0.095 | 0.087 | 0.08 | 0.073 | 0.066 | 0.059 | 0.053 | 0.047 | 0.042 | 0.04 | 1 | 1.143 | 1.211 | 1.213 | 1.154 | 1.298 | 1.223 | 1.265 | 1.144 | 1.049 | 0.912 | 0.978 | 1 | 1.017 | 1.088 | 1.199 | 1.263 | 1.344 | 1.378 | 1.31 | 1.2 | 1.111 | 0.963 | 1.014 | 1 | 0.95 | 0.88 | 0.861 | 0.869 | 0.793 | 0.808 | 0.842 | 0.919 | 1 | 1.101 | 1.05 | 1 | 0.971 | 0.945 | 0.734 | 0.613 | 0.507 | 0.452 | 0.475 | 0.624 | 0.686 | 0.87 | 0.836
sjv6000 | 0.98 | Belasting | 0 | 0.146 | 0.524 | 2.475 | 5.066 | 0.082 | 0.236 | 0.977 | 2.388 | 0.295 | 0.32 | 0.345 | 0.37 | 0.393 | 0.416 | 0.436 | 0.455 | 0.471 | 0.487 | 0.5 | 0.511 | 0.521 | 0.527 | 0.53 | 0.531 | 0.53 | 0.528 | 0.524 | 0.518 | 0.509 | 0.501 | 0.488 | 0.473 | 0.455 | 0.434 | 0.412 | 0.389 | 0.365 | 0.342 | 0.322 | 0.306 | 0.291 | 0.28 | 0.27 | 0.261 | 0.256 | 0.251 | 0.247 | 0.243 | 0.24 | 0.238 | 0.237 | 0.237 | 0.235 | 0.234 | 0.231 | 0.23 | 0.229 | 0.229 | 0.229 | 0.229 | 0.229 | 0.229 | 0.228 | 0.226 | 0.223 | 0.219 | 0.214 | 0.207 | 0.199 | 0.192 | 0.183 | 0.174 | 0.165 | 0.159 | 0.151 | 0.146 | 0.14 | 0.135 | 0.129 | 0.125 | 0.121 | 0.119 | 0.115 | 0.112 | 0.107 | 0.104 | 0.099 | 0.095 | 0.092 | 0.09 | 0.089 | 0.09 | 0.093 | 0.098 | 0.107 | 0.116 | 0.129 | 0.143 | 0.159 | 0.177 | 0.199 | 0.222 | 0.245 | 0.27 | 0.642 | 0.624 | 0.605 | 0.587 | 0.57 | 0.552 | 0.535 | 0.52 | 0.505 | 0.492 | 0.481 | 0.471 | 0.463 | 0.457 | 0.454 | 0.453 | 0.454 | 0.456 | 0.459 | 0.463 | 0.47 | 0.477 | 0.487 | 0.497 | 0.512 | 0.527 | 0.544 | 0.56 | 0.576 | 0.592 | 0.604 | 0.613 | 0.62 | 0.623 | 0.627 | 0.628 | 0.626 | 0.624 | 0.621 | 0.618 | 0.617 | 0.614 | 0.61 | 0.607 | 0.606 | 0.606 | 0.608 | 0.609 | 0.609 | 0.609 | 0.609 | 0.61 | 0.612 | 0.615 | 0.617 | 0.621 | 0.624 | 0.628 | 0.633 | 0.638 | 0.642 | 0.646 | 0.651 | 0.656 | 0.663 | 0.668 | 0.674 | 0.678 | 0.682 | 0.686 | 0.689 | 0.689 | 0.689 | 0.688 | 0.69 | 0.693 | 0.7 | 0.705 | 0.713 | 0.719 | 0.725 | 0.732 | 0.736 | 0.741 | 0.744 | 0.746 | 0.743 | 0.741 | 0.734 | 0.728 | 0.72 | 0.713 | 0.7 | 0.689 | 0.674 | 0.659 | 0.06 | 0.054 | 0.046 | 0.04 | 0.035 | 0.03 | 0.027 | 0.023 | 0.022 | 0.02 | 0.018 | 0.017 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.016 | 0.016 | 0.018 | 0.02 | 0.021 | 0.024 | 0.027 | 0.031 | 0.037 | 0.042 | 0.048 | 0.055 | 0.062 | 0.069 | 0.077 | 0.084 | 0.092 | 0.099 | 0.105 | 0.112 | 0.119 | 0.125 | 0.132 | 0.137 | 0.141 | 0.146 | 0.15 | 0.152 | 0.153 | 0.153 | 0.153 | 0.153 | 0.153 | 0.152 | 0.151 | 0.149 | 0.146 | 0.145 | 0.143 | 0.142 | 0.141 | 0.141 | 0.143 | 0.146 | 0.15 | 0.153 | 0.156 | 0.158 | 0.16 | 0.161 | 0.162 | 0.165 | 0.167 | 0.17 | 0.175 | 0.179 | 0.183 | 0.185 | 0.185 | 0.183 | 0.181 | 0.178 | 0.176 | 0.174 | 0.17 | 0.166 | 0.161 | 0.156 | 0.15 | 0.143 | 0.137 | 0.13 | 0.123 | 0.115 | 0.105 | 0.097 | 0.086 | 0.078 | 0.068 | 0.024 | 0.022 | 0.02 | 0.018 | 0.016 | 0.014 | 0.013 | 0.012 | 0.01 | 0.01 | 0.009 | 0.008 | 0.008 | 0.008 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.008 | 0.009 | 0.01 | 0.011 | 0.014 | 0.017 | 0.02 | 0.024 | 0.028 | 0.033 | 0.038 | 0.043 | 0.047 | 0.052 | 0.055 | 0.059 | 0.061 | 0.063 | 0.064 | 0.066 | 0.067 | 0.069 | 0.071 | 0.073 | 0.075 | 0.076 | 0.077 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.078 | 0.077 | 0.076 | 0.076 | 0.077 | 0.077 | 0.079 | 0.079 | 0.08 | 0.082 | 0.083 | 0.084 | 0.085 | 0.087 | 0.089 | 0.09 | 0.093 | 0.095 | 0.096 | 0.098 | 0.099 | 0.098 | 0.098 | 0.097 | 0.096 | 0.095 | 0.093 | 0.092 | 0.089 | 0.086 | 0.083 | 0.079 | 0.075 | 0.071 | 0.067 | 0.062 | 0.057 | 0.053 | 0.048 | 0.044 | 0.039 | 0.034 | 0.031 | 0.027 | 0.304 | 0.332 | 0.357 | 0.382 | 0.405 | 0.427 | 0.446 | 0.465 | 0.482 | 0.497 | 0.508 | 0.518 | 0.526 | 0.531 | 0.534 | 0.533 | 0.531 | 0.529 | 0.523 | 0.518 | 0.508 | 0.498 | 0.485 | 0.471 | 0.45 | 0.427 | 0.405 | 0.378 | 0.353 | 0.329 | 0.308 | 0.292 | 0.278 | 0.268 | 0.26 | 0.255 | 0.255 | 0.256 | 0.256 | 0.258 | 0.26 | 0.262 | 0.263 | 0.263 | 0.262 | 0.259 | 0.258 | 0.255 | 0.251 | 0.25 | 0.249 | 0.249 | 0.25 | 0.25 | 0.248 | 0.245 | 0.243 | 0.236 | 0.227 | 0.218 | 0.206 | 0.194 | 0.181 | 0.17 | 0.158 | 0.149 | 0.141 | 0.134 | 0.127 | 0.121 | 0.117 | 0.114 | 0.111 | 0.109 | 0.105 | 0.101 | 0.097 | 0.094 | 0.091 | 0.088 | 0.086 | 0.083 | 0.082 | 0.082 | 0.085 | 0.09 | 0.099 | 0.108 | 0.122 | 0.136 | 0.156 | 0.177 | 0.201 | 0.226 | 0.253 | 0.279 | 0.63 | 0.613 | 0.595 | 0.576 | 0.559 | 0.542 | 0.526 | 0.511 | 0.496 | 0.483 | 0.473 | 0.464 | 0.458 | 0.452 | 0.45 | 0.45 | 0.451 | 0.453 | 0.457 | 0.462 | 0.469 | 0.477 | 0.488 | 0.498 | 0.515 | 0.53 | 0.546 | 0.565 | 0.583 | 0.597 | 0.61 | 0.618 | 0.625 | 0.629 | 0.631 | 0.631 | 0.624 | 0.618 | 0.612 | 0.605 | 0.6 | 0.597 | 0.596 | 0.596 | 0.595 | 0.596 | 0.597 | 0.599 | 0.604 | 0.607 | 0.61 | 0.611 | 0.612 | 0.612 | 0.613 | 0.614 | 0.615 | 0.62 | 0.626 | 0.632 | 0.64 | 0.645 | 0.652 | 0.657 | 0.664 | 0.672 | 0.681 | 0.689 | 0.696 | 0.697 | 0.699 | 0.697 | 0.698 | 0.699 | 0.701 | 0.706 | 0.712 | 0.718 | 0.725 | 0.732 | 0.738 | 0.743 | 0.749 | 0.753 | 0.754 | 0.755 | 0.751 | 0.748 | 0.74 | 0.734 | 0.722 | 0.711 | 0.696 | 0.682 | 0.664 | 0.648 | 0.063 | 0.052 | 0.045 | 0.039 | 0.034 | 0.029 | 0.026 | 0.023 | 0.021 | 0.019 | 0.018 | 0.017 | 0.016 | 0.015 | 0.016 | 0.016 | 0.017 | 0.018 | 0.019 | 0.02 | 0.022 | 0.024 | 0.026 | 0.029 | 0.033 | 0.039 | 0.044 | 0.051 | 0.058 | 0.068 | 0.076 | 0.084 | 0.091 | 0.097 | 0.103 | 0.108 | 0.114 | 0.12 | 0.125 | 0.131 | 0.134 | 0.135 | 0.135 | 0.136 | 0.137 | 0.138 | 0.139 | 0.139 | 0.138 | 0.136 | 0.134 | 0.133 | 0.131 | 0.131 | 0.131 | 0.132 | 0.135 | 0.136 | 0.138 | 0.141 | 0.144 | 0.15 | 0.154 | 0.159 | 0.164 | 0.164 | 0.165 | 0.165 | 0.166 | 0.169 | 0.173 | 0.176 | 0.18 | 0.182 | 0.183 | 0.183 | 0.182 | 0.18 | 0.176 | 0.173 | 0.169 | 0.165 | 0.161 | 0.157 | 0.153 | 0.147 | 0.143 | 0.137 | 0.131 | 0.123 | 0.116 | 0.107 | 0.098 | 0.089 | 0.08 | 0.071 | 0.025 | 0.021 | 0.019 | 0.016 | 0.015 | 0.013 | 0.011 | 0.011 | 0.009 | 0.009 | 0.008 | 0.008 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.006 | 0.007 | 0.007 | 0.008 | 0.009 | 0.01 | 0.013 | 0.016 | 0.02 | 0.024 | 0.029 | 0.034 | 0.039 | 0.044 | 0.049 | 0.053 | 0.055 | 0.058 | 0.059 | 0.06 | 0.061 | 0.061 | 0.062 | 0.063 | 0.064 | 0.065 | 0.066 | 0.067 | 0.068 | 0.069 | 0.069 | 0.069 | 0.068 | 0.067 | 0.067 | 0.066 | 0.066 | 0.066 | 0.067 | 0.067 | 0.068 | 0.069 | 0.069 | 0.071 | 0.073 | 0.075 | 0.077 | 0.079 | 0.081 | 0.083 | 0.086 | 0.088 | 0.09 | 0.092 | 0.093 | 0.093 | 0.094 | 0.095 | 0.093 | 0.093 | 0.092 | 0.09 | 0.088 | 0.085 | 0.082 | 0.079 | 0.075 | 0.071 | 0.066 | 0.061 | 0.055 | 0.05 | 0.045 | 0.04 | 0.036 | 0.032 | 0.028 | 0.027 | 1 | 0.939 | 0.861 | 1.096 | 1.223 | 1.204 | 1.243 | 1.174 | 1.179 | 1.042 | 0.931 | 0.83 | 1 | 1.043 | 1.068 | 1.024 | 0.993 | 1.019 | 1.037 | 1.066 | 1.016 | 1.045 | 1.04 | 1.075 | 1 | 0.942 | 0.964 | 0.783 | 0.71 | 0.648 | 0.531 | 0.528 | 0.698 | 0.788 | 0.965 | 0.989 | 1 | 0.895 | 1.012 | 0.796 | 0.708 | 0.633 | 0.533 | 0.587 | 0.664 | 0.811 | 0.891 | 0.924
sjv7000 | 0.98 | Belasting | 0 | 0.155 | 0.74 | 2.244 | 6.673 | 0.102 | 0.387 | 0.872 | 2.368 | 0.393 | 0.415 | 0.437 | 0.456 | 0.474 | 0.49 | 0.504 | 0.517 | 0.528 | 0.538 | 0.547 | 0.554 | 0.561 | 0.567 | 0.571 | 0.574 | 0.576 | 0.578 | 0.577 | 0.575 | 0.57 | 0.564 | 0.554 | 0.542 | 0.527 | 0.508 | 0.489 | 0.467 | 0.446 | 0.425 | 0.405 | 0.389 | 0.376 | 0.366 | 0.359 | 0.355 | 0.352 | 0.35 | 0.349 | 0.348 | 0.349 | 0.349 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.349 | 0.348 | 0.348 | 0.346 | 0.345 | 0.344 | 0.343 | 0.341 | 0.339 | 0.335 | 0.331 | 0.326 | 0.32 | 0.312 | 0.304 | 0.294 | 0.283 | 0.273 | 0.263 | 0.254 | 0.245 | 0.237 | 0.229 | 0.223 | 0.215 | 0.208 | 0.202 | 0.196 | 0.19 | 0.184 | 0.18 | 0.175 | 0.172 | 0.169 | 0.168 | 0.169 | 0.174 | 0.183 | 0.195 | 0.21 | 0.228 | 0.249 | 0.271 | 0.296 | 0.322 | 0.346 | 0.37 | 0.498 | 0.488 | 0.477 | 0.468 | 0.458 | 0.449 | 0.441 | 0.433 | 0.426 | 0.42 | 0.414 | 0.409 | 0.404 | 0.4 | 0.397 | 0.395 | 0.394 | 0.393 | 0.394 | 0.394 | 0.398 | 0.402 | 0.408 | 0.415 | 0.423 | 0.434 | 0.445 | 0.457 | 0.468 | 0.479 | 0.488 | 0.495 | 0.501 | 0.504 | 0.507 | 0.508 | 0.508 | 0.507 | 0.506 | 0.505 | 0.503 | 0.502 | 0.5 | 0.498 | 0.497 | 0.496 | 0.495 | 0.495 | 0.494 | 0.494 | 0.494 | 0.495 | 0.496 | 0.497 | 0.498 | 0.499 | 0.501 | 0.502 | 0.503 | 0.505 | 0.507 | 0.508 | 0.51 | 0.512 | 0.514 | 0.515 | 0.516 | 0.516 | 0.515 | 0.514 | 0.513 | 0.512 | 0.511 | 0.51 | 0.51 | 0.511 | 0.513 | 0.515 | 0.518 | 0.521 | 0.525 | 0.528 | 0.533 | 0.537 | 0.541 | 0.543 | 0.545 | 0.546 | 0.544 | 0.543 | 0.54 | 0.536 | 0.53 | 0.523 | 0.515 | 0.507 | 0.095 | 0.084 | 0.074 | 0.066 | 0.059 | 0.053 | 0.048 | 0.044 | 0.04 | 0.037 | 0.034 | 0.032 | 0.031 | 0.029 | 0.028 | 0.027 | 0.026 | 0.026 | 0.026 | 0.027 | 0.028 | 0.03 | 0.033 | 0.037 | 0.041 | 0.047 | 0.054 | 0.061 | 0.069 | 0.077 | 0.084 | 0.09 | 0.094 | 0.098 | 0.101 | 0.103 | 0.104 | 0.105 | 0.106 | 0.107 | 0.107 | 0.108 | 0.108 | 0.109 | 0.109 | 0.109 | 0.109 | 0.109 | 0.11 | 0.111 | 0.111 | 0.112 | 0.112 | 0.113 | 0.113 | 0.114 | 0.114 | 0.115 | 0.116 | 0.118 | 0.121 | 0.125 | 0.129 | 0.135 | 0.141 | 0.148 | 0.156 | 0.163 | 0.171 | 0.179 | 0.187 | 0.194 | 0.201 | 0.208 | 0.215 | 0.221 | 0.226 | 0.23 | 0.234 | 0.238 | 0.241 | 0.243 | 0.244 | 0.244 | 0.242 | 0.237 | 0.23 | 0.221 | 0.21 | 0.197 | 0.183 | 0.167 | 0.151 | 0.135 | 0.121 | 0.107 | 0.014 | 0.013 | 0.011 | 0.01 | 0.009 | 0.008 | 0.007 | 0.006 | 0.005 | 0.005 | 0.004 | 0.004 | 0.004 | 0.004 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.006 | 0.007 | 0.008 | 0.01 | 0.012 | 0.015 | 0.017 | 0.02 | 0.023 | 0.026 | 0.028 | 0.031 | 0.033 | 0.035 | 0.036 | 0.038 | 0.039 | 0.04 | 0.041 | 0.042 | 0.043 | 0.043 | 0.044 | 0.045 | 0.045 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.046 | 0.045 | 0.044 | 0.044 | 0.044 | 0.044 | 0.045 | 0.045 | 0.046 | 0.047 | 0.048 | 0.05 | 0.051 | 0.053 | 0.055 | 0.057 | 0.06 | 0.062 | 0.063 | 0.065 | 0.066 | 0.066 | 0.066 | 0.066 | 0.065 | 0.065 | 0.063 | 0.062 | 0.059 | 0.057 | 0.054 | 0.051 | 0.048 | 0.045 | 0.042 | 0.038 | 0.035 | 0.032 | 0.029 | 0.026 | 0.023 | 0.02 | 0.018 | 0.016 | 0.394 | 0.422 | 0.443 | 0.462 | 0.479 | 0.493 | 0.508 | 0.519 | 0.531 | 0.54 | 0.548 | 0.554 | 0.56 | 0.564 | 0.568 | 0.571 | 0.573 | 0.574 | 0.573 | 0.571 | 0.566 | 0.56 | 0.55 | 0.537 | 0.521 | 0.501 | 0.48 | 0.456 | 0.432 | 0.411 | 0.391 | 0.376 | 0.363 | 0.355 | 0.35 | 0.349 | 0.35 | 0.352 | 0.355 | 0.357 | 0.359 | 0.361 | 0.364 | 0.365 | 0.366 | 0.365 | 0.365 | 0.363 | 0.362 | 0.36 | 0.358 | 0.357 | 0.355 | 0.354 | 0.353 | 0.352 | 0.349 | 0.346 | 0.342 | 0.338 | 0.331 | 0.325 | 0.316 | 0.306 | 0.295 | 0.283 | 0.271 | 0.26 | 0.249 | 0.239 | 0.231 | 0.222 | 0.214 | 0.207 | 0.2 | 0.193 | 0.187 | 0.181 | 0.175 | 0.169 | 0.164 | 0.16 | 0.156 | 0.155 | 0.157 | 0.162 | 0.171 | 0.183 | 0.2 | 0.218 | 0.242 | 0.268 | 0.295 | 0.323 | 0.349 | 0.372 | 0.502 | 0.492 | 0.48 | 0.47 | 0.461 | 0.453 | 0.444 | 0.437 | 0.429 | 0.422 | 0.417 | 0.413 | 0.409 | 0.406 | 0.404 | 0.402 | 0.4 | 0.399 | 0.4 | 0.401 | 0.404 | 0.408 | 0.414 | 0.422 | 0.431 | 0.443 | 0.455 | 0.468 | 0.481 | 0.491 | 0.501 | 0.509 | 0.515 | 0.518 | 0.521 | 0.521 | 0.518 | 0.516 | 0.514 | 0.512 | 0.51 | 0.508 | 0.506 | 0.504 | 0.504 | 0.504 | 0.504 | 0.505 | 0.505 | 0.507 | 0.508 | 0.509 | 0.511 | 0.511 | 0.512 | 0.513 | 0.514 | 0.516 | 0.518 | 0.52 | 0.523 | 0.525 | 0.526 | 0.529 | 0.531 | 0.533 | 0.536 | 0.537 | 0.537 | 0.536 | 0.534 | 0.534 | 0.533 | 0.532 | 0.532 | 0.532 | 0.534 | 0.535 | 0.538 | 0.541 | 0.545 | 0.548 | 0.554 | 0.557 | 0.56 | 0.563 | 0.564 | 0.565 | 0.563 | 0.562 | 0.556 | 0.55 | 0.542 | 0.533 | 0.524 | 0.513 | 0.092 | 0.076 | 0.068 | 0.06 | 0.054 | 0.048 | 0.044 | 0.04 | 0.037 | 0.034 | 0.031 | 0.03 | 0.028 | 0.027 | 0.026 | 0.025 | 0.024 | 0.024 | 0.024 | 0.025 | 0.026 | 0.028 | 0.031 | 0.035 | 0.041 | 0.047 | 0.054 | 0.062 | 0.071 | 0.079 | 0.086 | 0.092 | 0.097 | 0.1 | 0.102 | 0.102 | 0.102 | 0.102 | 0.101 | 0.101 | 0.1 | 0.1 | 0.099 | 0.099 | 0.098 | 0.098 | 0.098 | 0.098 | 0.099 | 0.099 | 0.1 | 0.101 | 0.101 | 0.102 | 0.102 | 0.103 | 0.104 | 0.106 | 0.108 | 0.11 | 0.112 | 0.116 | 0.121 | 0.127 | 0.133 | 0.141 | 0.149 | 0.157 | 0.166 | 0.175 | 0.184 | 0.192 | 0.2 | 0.207 | 0.213 | 0.219 | 0.224 | 0.229 | 0.233 | 0.237 | 0.24 | 0.242 | 0.243 | 0.243 | 0.24 | 0.235 | 0.228 | 0.218 | 0.207 | 0.192 | 0.178 | 0.161 | 0.145 | 0.128 | 0.113 | 0.102 | 0.012 | 0.01 | 0.009 | 0.008 | 0.007 | 0.006 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.007 | 0.009 | 0.011 | 0.013 | 0.016 | 0.019 | 0.021 | 0.023 | 0.025 | 0.027 | 0.027 | 0.029 | 0.029 | 0.03 | 0.03 | 0.03 | 0.031 | 0.031 | 0.031 | 0.032 | 0.032 | 0.033 | 0.033 | 0.034 | 0.034 | 0.034 | 0.034 | 0.033 | 0.033 | 0.033 | 0.032 | 0.032 | 0.032 | 0.032 | 0.032 | 0.033 | 0.033 | 0.035 | 0.037 | 0.038 | 0.04 | 0.042 | 0.044 | 0.046 | 0.048 | 0.05 | 0.051 | 0.053 | 0.054 | 0.054 | 0.055 | 0.056 | 0.055 | 0.055 | 0.054 | 0.053 | 0.051 | 0.049 | 0.047 | 0.045 | 0.043 | 0.04 | 0.037 | 0.034 | 0.03 | 0.027 | 0.024 | 0.021 | 0.019 | 0.016 | 0.014 | 0.013 | 1 | 1.075 | 1.103 | 1.15 | 1.17 | 1.193 | 1.225 | 1.221 | 1.126 | 1.016 | 0.912 | 0.965 | 1 | 0.942 | 0.936 | 0.951 | 0.883 | 0.857 | 0.91 | 0.927 | 0.964 | 1.02 | 0.993 | 0.981 | 1 | 1.01 | 0.973 | 0.828 | 0.927 | 0.934 | 0.765 | 0.71 | 0.791 | 0.897 | 1.154 | 1.046 | 1 | 0.94 | 0.858 | 0.888 | 1.327 | 1.459 | 1.046 | 1.174 | 1.35 | 1.098 | 1.496 | 1.734
sjv8000 | 0.98 | Belasting | 0 | 1.301 | 7.391 | 0.212 | 6.43 | 0.777 | 0.477 | 0.124 | 2.523 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv9000 | 0.98 | Belasting | 0 | 1.464 | 8.315 | 0.239 | 7.234 | 0.874 | 0.537 | 0.14 | 2.839 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv10000 | 0.98 | Belasting | 0 | 1.626 | 9.239 | 0.265 | 8.037 | 0.971 | 0.596 | 0.155 | 3.154 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv15000 | 0.98 | Belasting | 0 | 2.439 | 13.858 | 0.398 | 12.056 | 1.457 | 0.894 | 0.232 | 4.731 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv20000 | 0.98 | Belasting | 0 | 3.252 | 18.477 | 0.531 | 16.075 | 1.942 | 1.192 | 0.309 | 6.308 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv25000 | 0.98 | Belasting | 0 | 4.065 | 23.097 | 0.664 | 20.094 | 2.428 | 1.49 | 0.387 | 7.885 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv30000 | 0.98 | Belasting | 0 | 4.878 | 27.716 | 0.796 | 24.112 | 2.913 | 1.788 | 0.464 | 9.462 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv35000 | 0.98 | Belasting | 0 | 5.691 | 32.336 | 0.929 | 28.131 | 3.399 | 2.086 | 0.542 | 11.039 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv40000 | 0.98 | Belasting | 0 | 6.504 | 36.955 | 1.061 | 32.149 | 3.884 | 2.384 | 0.619 | 12.616 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv45000 | 0.98 | Belasting | 0 | 7.317 | 41.574 | 1.194 | 36.168 | 4.37 | 2.682 | 0.697 | 14.193 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv50000 | 0.98 | Belasting | 0 | 8.13 | 46.193 | 1.326 | 40.187 | 4.855 | 2.98 | 0.774 | 15.77 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv60000 | 0.98 | Belasting | 0 | 9.756 | 55.432 | 1.592 | 48.224 | 5.827 | 3.576 | 0.928 | 18.924 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv70000 | 0.98 | Belasting | 0 | 11.382 | 64.671 | 1.857 | 56.261 | 6.798 | 4.172 | 1.083 | 22.078 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv80000 | 0.98 | Belasting | 0 | 13.008 | 73.909 | 2.122 | 64.299 | 7.769 | 4.768 | 1.238 | 25.232 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv90000 | 0.98 | Belasting | 0 | 14.634 | 83.147 | 2.387 | 72.337 | 8.74 | 5.364 | 1.393 | 28.386 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892
sjv100000 | 0.98 | Belasting | 0 | 16.26 | 92.385 | 2.652 | 80.375 | 9.711 | 5.96 | 1.548 | 31.54 | 0.245 | 0.226 | 0.209 | 0.195 | 0.182 | 0.172 | 0.164 | 0.154 | 0.149 | 0.142 | 0.138 | 0.135 | 0.136 | 0.134 | 0.137 | 0.137 | 0.141 | 0.147 | 0.156 | 0.169 | 0.185 | 0.205 | 0.227 | 0.253 | 0.277 | 0.298 | 0.314 | 0.327 | 0.335 | 0.342 | 0.343 | 0.343 | 0.34 | 0.339 | 0.337 | 0.338 | 0.334 | 0.335 | 0.333 | 0.333 | 0.333 | 0.331 | 0.33 | 0.331 | 0.332 | 0.336 | 0.337 | 0.337 | 0.338 | 0.338 | 0.341 | 0.343 | 0.347 | 0.349 | 0.352 | 0.358 | 0.364 | 0.374 | 0.386 | 0.399 | 0.414 | 0.428 | 0.44 | 0.449 | 0.456 | 0.462 | 0.467 | 0.475 | 0.484 | 0.493 | 0.502 | 0.511 | 0.519 | 0.53 | 0.543 | 0.554 | 0.569 | 0.582 | 0.596 | 0.607 | 0.616 | 0.62 | 0.619 | 0.611 | 0.598 | 0.578 | 0.554 | 0.526 | 0.495 | 0.46 | 0.423 | 0.389 | 0.354 | 0.32 | 0.292 | 0.267 | 0.009 | 0.008 | 0.006 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.003 | 0.004 | 0.005 | 0.005 | 0.004 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.003 | 0.002 | 0.003 | 0.003 | 0.002 | 0.003 | 0.003 | 0.003 | 0.004 | 0.004 | 0.005 | 0.005 | 0.005 | 0.004 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.009 | 0.009 | 0.718 | 0.737 | 0.757 | 0.773 | 0.788 | 0.8 | 0.809 | 0.819 | 0.826 | 0.834 | 0.838 | 0.841 | 0.841 | 0.843 | 0.841 | 0.84 | 0.837 | 0.831 | 0.823 | 0.81 | 0.793 | 0.771 | 0.747 | 0.716 | 0.687 | 0.658 | 0.634 | 0.617 | 0.608 | 0.604 | 0.605 | 0.608 | 0.613 | 0.614 | 0.617 | 0.616 | 0.62 | 0.619 | 0.62 | 0.619 | 0.62 | 0.622 | 0.623 | 0.623 | 0.623 | 0.62 | 0.618 | 0.617 | 0.614 | 0.614 | 0.612 | 0.611 | 0.608 | 0.608 | 0.606 | 0.601 | 0.597 | 0.587 | 0.574 | 0.557 | 0.538 | 0.517 | 0.499 | 0.483 | 0.469 | 0.458 | 0.449 | 0.44 | 0.432 | 0.422 | 0.412 | 0.401 | 0.392 | 0.383 | 0.373 | 0.364 | 0.353 | 0.344 | 0.334 | 0.327 | 0.322 | 0.322 | 0.326 | 0.336 | 0.353 | 0.375 | 0.403 | 0.437 | 0.473 | 0.514 | 0.548 | 0.582 | 0.612 | 0.642 | 0.67 | 0.695 | 0.029 | 0.028 | 0.028 | 0.027 | 0.027 | 0.026 | 0.025 | 0.025 | 0.024 | 0.024 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.023 | 0.024 | 0.029 | 0.034 | 0.041 | 0.047 | 0.051 | 0.052 | 0.051 | 0.049 | 0.047 | 0.046 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.046 | 0.047 | 0.046 | 0.046 | 0.046 | 0.044 | 0.044 | 0.043 | 0.044 | 0.045 | 0.047 | 0.047 | 0.046 | 0.045 | 0.043 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.041 | 0.046 | 0.052 | 0.059 | 0.066 | 0.073 | 0.078 | 0.081 | 0.082 | 0.082 | 0.082 | 0.083 | 0.084 | 0.085 | 0.083 | 0.08 | 0.077 | 0.074 | 0.072 | 0.068 | 0.064 | 0.06 | 0.057 | 0.053 | 0.052 | 0.048 | 0.045 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.028 | 0.03 | 0.029 | 0.029 | 0.228 | 0.211 | 0.195 | 0.183 | 0.172 | 0.162 | 0.156 | 0.149 | 0.145 | 0.14 | 0.138 | 0.135 | 0.135 | 0.133 | 0.135 | 0.135 | 0.141 | 0.146 | 0.157 | 0.172 | 0.189 | 0.212 | 0.238 | 0.269 | 0.297 | 0.321 | 0.335 | 0.348 | 0.355 | 0.359 | 0.36 | 0.355 | 0.344 | 0.336 | 0.325 | 0.323 | 0.318 | 0.315 | 0.313 | 0.31 | 0.31 | 0.309 | 0.309 | 0.31 | 0.311 | 0.313 | 0.315 | 0.314 | 0.313 | 0.313 | 0.315 | 0.317 | 0.321 | 0.325 | 0.332 | 0.339 | 0.349 | 0.358 | 0.368 | 0.382 | 0.398 | 0.419 | 0.438 | 0.455 | 0.466 | 0.475 | 0.485 | 0.497 | 0.508 | 0.52 | 0.531 | 0.539 | 0.549 | 0.557 | 0.566 | 0.578 | 0.591 | 0.603 | 0.618 | 0.63 | 0.642 | 0.649 | 0.652 | 0.646 | 0.632 | 0.609 | 0.58 | 0.545 | 0.506 | 0.464 | 0.422 | 0.379 | 0.337 | 0.308 | 0.276 | 0.25 | 0.01 | 0.009 | 0.007 | 0.006 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.002 | 0.004 | 0.006 | 0.008 | 0.008 | 0.007 | 0.005 | 0.004 | 0.003 | 0.003 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.002 | 0.002 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.003 | 0.004 | 0.007 | 0.009 | 0.01 | 0.011 | 0.736 | 0.754 | 0.772 | 0.786 | 0.799 | 0.81 | 0.818 | 0.826 | 0.831 | 0.836 | 0.839 | 0.843 | 0.843 | 0.845 | 0.844 | 0.844 | 0.839 | 0.834 | 0.823 | 0.808 | 0.79 | 0.762 | 0.732 | 0.693 | 0.657 | 0.622 | 0.6 | 0.586 | 0.58 | 0.58 | 0.584 | 0.593 | 0.606 | 0.614 | 0.625 | 0.628 | 0.633 | 0.637 | 0.639 | 0.643 | 0.646 | 0.647 | 0.648 | 0.647 | 0.646 | 0.645 | 0.644 | 0.646 | 0.647 | 0.647 | 0.645 | 0.643 | 0.639 | 0.635 | 0.629 | 0.622 | 0.613 | 0.605 | 0.594 | 0.577 | 0.558 | 0.53 | 0.506 | 0.481 | 0.462 | 0.446 | 0.432 | 0.417 | 0.404 | 0.394 | 0.383 | 0.377 | 0.368 | 0.359 | 0.349 | 0.339 | 0.328 | 0.318 | 0.308 | 0.298 | 0.292 | 0.288 | 0.291 | 0.301 | 0.319 | 0.344 | 0.377 | 0.417 | 0.461 | 0.51 | 0.55 | 0.592 | 0.63 | 0.656 | 0.688 | 0.713 | 0.026 | 0.026 | 0.026 | 0.025 | 0.025 | 0.024 | 0.023 | 0.023 | 0.023 | 0.022 | 0.022 | 0.022 | 0.021 | 0.021 | 0.021 | 0.021 | 0.02 | 0.02 | 0.02 | 0.02 | 0.021 | 0.025 | 0.028 | 0.036 | 0.042 | 0.05 | 0.056 | 0.059 | 0.058 | 0.055 | 0.052 | 0.049 | 0.047 | 0.048 | 0.048 | 0.048 | 0.048 | 0.047 | 0.046 | 0.046 | 0.044 | 0.044 | 0.042 | 0.042 | 0.042 | 0.041 | 0.04 | 0.039 | 0.039 | 0.039 | 0.04 | 0.04 | 0.04 | 0.04 | 0.039 | 0.039 | 0.037 | 0.036 | 0.038 | 0.04 | 0.044 | 0.05 | 0.055 | 0.063 | 0.071 | 0.078 | 0.082 | 0.084 | 0.086 | 0.085 | 0.084 | 0.083 | 0.082 | 0.082 | 0.083 | 0.081 | 0.08 | 0.077 | 0.073 | 0.071 | 0.065 | 0.062 | 0.056 | 0.052 | 0.048 | 0.046 | 0.042 | 0.037 | 0.032 | 0.026 | 0.026 | 0.025 | 0.025 | 0.027 | 0.026 | 0.027 | 1 | 0.801 | 0.853 | 0.792 | 0.837 | 0.794 | 0.66 | 0.878 | 0.822 | 0.888 | 0.922 | 0.865 | 1 | 2.127 | 1.933 | 0.802 | 0.198 | 0.115 | 0.137 | 0.127 | 0.363 | 0.34 | 0.996 | 0.786 | 1 | 1.196 | 1.158 | 1.342 | 1.311 | 1.398 | 1.582 | 1.298 | 1.36 | 1.238 | 1.131 | 1.198 | 1 | 1.277 | 1.136 | 0.653 | 0.533 | 0.384 | 0.338 | 0.342 | 0.387 | 0.562 | 0.854 | 0.892

## PL
Name | Unom | Inom | Irunup | Cosnom
| kV | A | A
CDM-ET 830 70 W | 0.23 | 0.45 | 0.6 | 0.82
CDM-ET 840 70 W | 0.23 | 0.45 | 0.6 | 0.82
CDM-OT 830 70 W | 0.23 | 0.45 | 0.6 | 0.82
CDM-T 830 35 W | 0.23 | 0.24 | 0.55 | 0.85
CDM-T 70 W | 0.23 | 0.45 | 0.6 | 0.82
CDM-T 150 W | 0.23 | 0.85 | 1.2 | 0.87
CDM-T 830 70 W | 0.23 | 0.45 | 0.6 | 0.82
CDM-T 830 150 W | 0.23 | 0.85 | 1.2 | 0.87
CDM-TD 830 70 W | 0.23 | 0.45 | 0.6 | 0.82
CDM-TD 830 150 W | 0.23 | 0.85 | 1.2 | 0.87
CDM-TM 830 20 W | 0.23 | 0.12 | 0.12 | 0.95
CDM-TT 70 W | 0.23 | 0.45 | 0.6 | 0.82
CDM-TT 830 150 W | 0.23 | 0.85 | 1.2 | 0.87
CDO-ET 828 70 W | 0.23 | 0.37 | 0.37 | 0.95
CDO-ET 830 70 W | 0.23 | 0.37 | 0.37 | 0.95
CDO-ET 100 W | 0.23 | 0.53 | 0.53 | 0.95
CDO-ET 150 W | 0.23 | 0.76 | 0.76 | 0.95
CDO-TT 70 W | 0.23 | 0.37 | 0.37 | 0.95
CDO-TT 100 W | 0.23 | 0.53 | 0.53 | 0.95
CDO-TT 150 W | 0.23 | 0.76 | 0.76 | 0.95
CPO 60 W | 0.23 | 0.31 | 0.31 | 0.95
CPO 90 W | 0.23 | 0.46 | 0.46 | 0.95
DULUX D/E 26 W | 0.23 | 0.15 | 0.15 | 1
DULUX -F 840 36 W | 0.23 | 0.2 | 0.2 | 1
GLOEI 25 W | 0.23 | 0.11 | 0.11 | 1
GLOEI 60 W | 0.23 | 0.26 | 0.26 | 1
GLOEI 100 W | 0.23 | 0.44 | 0.44 | 1
GLOEI TWINARC 100 W | 0.23 | 0.44 | 0.44 | 1
GLOEI 150 W | 0.23 | 0.44 | 0.44 | 1
HALOGEEN PAR 56 300 W | 0.23 | 1.35 | 1.35 | 1
HALOGEEN TWIST DICHR GZ10 50 W | 0.23 | 0.24 | 0.24 | 1
HIT E1 70 W | 0.23 | 0.37 | 0.37 | 0.95
HME-80 125 W | 0.23 | 0.7 | 1.1 | 0.85
HPL 400 W | 0.23 | 2.15 | 3.9 | 0.85
HPI-T 400 W | 0.23 | 2.15 | 3.9 | 0.85
HPL-N 50 W | 0.23 | 0.3 | 0.4 | 0.81
HPL-N 80 W | 0.23 | 0.45 | 0.65 | 0.87
HPL-N 125 W | 0.23 | 0.7 | 1.1 | 0.85
HPL-N 250 W | 0.23 | 1.35 | 2.2 | 0.86
HQI-TS-WDL 70 W | 0.23 | 0.37 | 0.37 | 0.95
HQI-TS 250 W | 0.23 | 1.4 | 2.3 | 0.86
IQL 85 W | 0.23 | 0.37 | 0.37 | 1
LED 15 W (30 LEDS GEEL) | 0.23 | 0.08 | 0.08 | 0.9
LED 27 W (18 LUXEON I & III LEDS) | 0.23 | 0.15 | 0.15 | 0.9
LED 27 W 1&3 | 0.23 | 0.15 | 0.15 | 0.9
LED 36 W | 0.23 | 0.2 | 0.2 | 0.9
MHN-TD 70 W | 0.23 | 0.37 | 0.37 | 0.95
ML 160 W | 0.23 | 0.77 | 1 | 0.9
PL 20 W | 0.23 | 0.09 | 0.09 | 1
PL FLAT 36 W | 0.23 | 0.2 | 0.2 | 1
PLC 18 W | 0.23 | 0.09 | 0.09 | 1
PLC 26 W | 0.23 | 0.15 | 0.15 | 1
PLC 2P 827 18 W | 0.23 | 0.11 | 0.11 | 1
PLC 2P 827 26 W | 0.23 | 0.15 | 0.15 | 1
PLC 2P 830 18 W | 0.23 | 0.11 | 0.11 | 1
PLC 2P 830 26 W | 0.23 | 0.15 | 0.15 | 1
PLC 2P 840 18 W | 0.23 | 0.11 | 0.11 | 1
PLC 2P 840 26 W | 0.23 | 0.15 | 0.15 | 1
PLC 4P HF 26 W | 0.23 | 0.13 | 0.13 | 1
PLC 4P HF 827 18 W | 0.23 | 0.09 | 0.09 | 1
PLC 4P HF 827 26 W | 0.23 | 0.13 | 0.13 | 1
PLC 4P HF 830 18 W | 0.23 | 0.09 | 0.09 | 1
PLC 4P HF 830 26 W | 0.23 | 0.13 | 0.13 | 1
PLC 4P HF 840 18 W | 0.23 | 0.09 | 0.09 | 1
PLC 4P HF 840 26 W | 0.23 | 0.13 | 0.13 | 1
PLE 827 11 W | 0.23 | 0.05 | 0.05 | 1
PLE 830 E27 18 W | 0.23 | 0.08 | 0.08 | 1
PLE PROF 827 20 W | 0.23 | 0.09 | 0.09 | 1
PLE PROF 830 20 W | 0.23 | 0.09 | 0.09 | 1
PLE PROF 840 20 W | 0.23 | 0.09 | 0.09 | 1
PLE-T 11 W | 0.23 | 0.05 | 0.05 | 1
PLE-T 15 W | 0.23 | 0.07 | 0.07 | 1
PLE-T 20 W | 0.23 | 0.09 | 0.09 | 1
PLE-T 84 23 W | 0.23 | 0.1 | 0.1 | 1
PLE 827 27 W | 0.23 | 0.12 | 0.12 | 1
PLL 4P 827 18 W | 0.23 | 0.12 | 0.12 | 1
PLL 4P 827 24 W | 0.23 | 0.14 | 0.14 | 1
PLL 4P 827 36 W | 0.23 | 0.2 | 0.2 | 1
PLL 4P 830 18 W | 0.23 | 0.12 | 0.12 | 1
PLL 4P 830 24 W | 0.23 | 0.14 | 0.14 | 1
PLL 4P 830 36 W | 0.23 | 0.2 | 0.2 | 1
PLL 4P 830 40 W | 0.23 | 0.2 | 0.2 | 1
PLL 4P 840 18 W | 0.23 | 0.12 | 0.12 | 1
PLL 4P 840 24 W | 0.23 | 0.14 | 0.14 | 1
PLL 4P 840 36 W | 0.23 | 0.2 | 0.2 | 1
PLL 4P A/N 827 24 W | 0.23 | 0.14 | 0.14 | 1
PLL 4P A/N 830 24 W | 0.23 | 0.14 | 0.14 | 1
PLL 4P A/N 840 24 W | 0.23 | 0.14 | 0.14 | 1
PLL 4P HF 827 18 W | 0.23 | 0.09 | 0.09 | 1
PLL 4P HF 827 24 W | 0.23 | 0.12 | 0.12 | 1
PLL 4P HF 827 36 W | 0.23 | 0.16 | 0.16 | 1
PLL 4P HF 827 55 W | 0.23 | 0.26 | 0.26 | 1
PLL 4P HF 830 18 W | 0.23 | 0.09 | 0.09 | 1
PLL 4P HF 830 24 W | 0.23 | 0.12 | 0.12 | 1
PLL 4P HF 830 36 W | 0.23 | 0.16 | 0.16 | 1
PLL 4P HF 830 40 W | 0.23 | 0.2 | 0.2 | 1
PLL 4P HF 830 55 W | 0.23 | 0.26 | 0.26 | 1
PLL 4P HF 830 80 W | 0.23 | 0.38 | 0.38 | 1
PLL 4P HF 840 18 W | 0.23 | 0.09 | 0.09 | 1
PLL 4P HF 840 24 W | 0.23 | 0.12 | 0.12 | 1
PLL 4P HF 840 36 W | 0.23 | 0.16 | 0.16 | 1
PLL 4P HF 840 40 W | 0.23 | 0.2 | 0.2 | 1
PLL 4P HF 840 55 W | 0.23 | 0.26 | 0.26 | 1
PLL 4P HF A/N 827 24 W | 0.23 | 0.12 | 0.12 | 1
PLL 4P HF A/N 830 24 W | 0.23 | 0.12 | 0.12 | 1
PLL 4P HF A/N 840 24 W | 0.23 | 0.12 | 0.12 | 1
PLL 4P HF DIM 827 36 W | 0.23 | 0.16 | 0.16 | 1
PLL 4P HF DIM 830 36 W | 0.23 | 0.16 | 0.16 | 1
PLL 4P HF DIM 830 55 W | 0.23 | 0.26 | 0.26 | 1
PLL 4P HF DIM 840 36 W | 0.23 | 0.16 | 0.16 | 1
PLL 4P HF DIM 840 55 W | 0.23 | 0.26 | 0.26 | 1
PLQ 4P HF 835 28 W | 0.23 | 0.14 | 0.14 | 1
PLS 7 W | 0.23 | 0.06 | 0.06 | 1
PLS 9 W | 0.23 | 0.07 | 0.07 | 1
PLS 11 W | 0.23 | 0.07 | 0.07 | 1
PLS 2P 827 5 W | 0.23 | 0.05 | 0.05 | 1
PLS 2P 827 9 W | 0.23 | 0.07 | 0.07 | 1
PLS 2P 827 11 W | 0.23 | 0.07 | 0.07 | 1
PLS 2P 830 9 W | 0.23 | 0.07 | 0.07 | 1
PLS 2P 830 11 W | 0.23 | 0.07 | 0.07 | 1
PLS 2P 840 9 W | 0.23 | 0.07 | 0.07 | 1
PLS 2P 840 11 W | 0.23 | 0.07 | 0.07 | 1
PLS 4P HF 827 9 W | 0.23 | 0.05 | 0.05 | 1
PLS 4P HF 827 11 W | 0.23 | 0.06 | 0.06 | 1
PLS 4P HF 830 9 W | 0.23 | 0.05 | 0.05 | 1
PLS 4P HF 830 11 W | 0.23 | 0.06 | 0.06 | 1
PLS 4P HF 840 9 W | 0.23 | 0.05 | 0.05 | 1
PLS 4P HF 840 11 W | 0.23 | 0.06 | 0.06 | 1
PLT 26 W | 0.23 | 0.15 | 0.15 | 1
PLT 42 W | 0.23 | 0.21 | 0.21 | 1
PLT 840 26 W | 0.23 | 0.15 | 0.15 | 1
PLT 840 32 W | 0.23 | 0.16 | 0.16 | 1
PLT 2P 827 18 W | 0.23 | 0.11 | 0.11 | 1
PLT 2P 827 26 W | 0.23 | 0.15 | 0.15 | 1
PLT 4P 827 32 W | 0.23 | 0.16 | 0.16 | 1
PLT 2P 830 18 W | 0.23 | 0.11 | 0.11 | 1
PLT 2P 830 26 W | 0.23 | 0.15 | 0.15 | 1
PLT 4P 830 32 W | 0.23 | 0.16 | 0.16 | 1
PLT 4P 830 42 W | 0.23 | 0.21 | 0.21 | 1
PLT 2P 840 18 W | 0.23 | 0.11 | 0.11 | 1
PLT 2P 840 26 W | 0.23 | 0.15 | 0.15 | 1
PLT 4P 840 26 W | 0.23 | 0.13 | 0.13 | 1
PLT 4P 840 32 W | 0.23 | 0.16 | 0.16 | 1
PLT 4P 840 42 W | 0.23 | 0.21 | 0.21 | 1
PLT 4P HF 827 18 W | 0.23 | 0.09 | 0.09 | 1
PLT 4P HF 827 26 W | 0.23 | 0.13 | 0.13 | 1
PLT 4P HF 827 32 W | 0.23 | 0.16 | 0.16 | 1
PLT 4P HF 827 42 W | 0.23 | 0.21 | 0.21 | 1
PLT 4P HF 827 57 W | 0.23 | 0.27 | 0.27 | 1
PLT 4P HF 830 18 W | 0.23 | 0.09 | 0.09 | 1
PLT 4P HF 830 26 W | 0.23 | 0.13 | 0.13 | 1
PLT 4P HF 830 32 W | 0.23 | 0.16 | 0.16 | 1
PLT 4P HF 830 42 W | 0.23 | 0.21 | 0.21 | 1
PLT 4P HF 830 57 W | 0.23 | 0.27 | 0.27 | 1
PLT 4P HF 840 18 W | 0.23 | 0.09 | 0.09 | 1
PLT 4P HF 840 26 W | 0.23 | 0.13 | 0.13 | 1
PLT 4P HF 840 32 W | 0.23 | 0.16 | 0.16 | 1
PLT 4P HF 840 42 W | 0.23 | 0.21 | 0.21 | 1
PLT 4P HF 840 57 W | 0.23 | 0.27 | 0.27 | 1
PLT 4P HF DIM 827 42 W | 0.23 | 0.21 | 0.21 | 1
PLT 4P HF DIM 830 42 W | 0.23 | 0.21 | 0.21 | 1
PLT 4P HF DIM 840 42 W | 0.23 | 0.21 | 0.21 | 1
QL 55 W | 0.23 | 0.24 | 0.24 | 1
QL 85 W | 0.23 | 0.37 | 0.37 | 1
QL 827 55 W | 0.23 | 0.24 | 0.24 | 1
QL 827 85 W | 0.23 | 0.37 | 0.37 | 1
QL 830 55 W | 0.23 | 0.24 | 0.24 | 1
QL 830 85 W | 0.23 | 0.37 | 0.37 | 1
QL 840 55 W | 0.23 | 0.24 | 0.24 | 1
QL 840 85 W | 0.23 | 0.37 | 0.37 | 1
QL HF 55 W | 0.23 | 0.24 | 0.24 | 1
QL HF 85 W | 0.23 | 0.37 | 0.37 | 1
SL 17 W | 0.23 | 0.08 | 0.08 | 1
SL 18 W | 0.23 | 0.09 | 0.09 | 1
SL 25 W | 0.23 | 0.11 | 0.11 | 1
SL 840 25 W | 0.23 | 0.11 | 0.11 | 1
SON 50 W | 0.23 | 0.3 | 0.45 | 0.88
SON 70 W | 0.23 | 0.45 | 0.6 | 0.77
SON 250 W | 0.23 | 1.4 | 2.3 | 0.86
SON 400 W | 0.23 | 2.2 | 3.6 | 0.86
SON 600 W | 0.23 | 4.9 | 3.2 | 0.91
SON-E 150 W | 0.23 | 0.85 | 1.2 | 0.86
SON SDW-T 50 W | 0.23 | 0.35 | 0.9 | 0.8
SON SDW-T 100 W | 0.23 | 0.55 | 1.3 | 0.91
SON-T 50 W | 0.23 | 0.3 | 0.45 | 0.88
SON-T 70 W | 0.23 | 0.45 | 0.6 | 0.77
SON-T 100 W | 0.23 | 0.65 | 1 | 0.76
SON-T 150 W | 0.23 | 0.85 | 1.2 | 0.86
SON-T 250 W | 0.23 | 1.4 | 2.3 | 0.86
SON-T 400 W | 0.23 | 2.2 | 3.6 | 0.86
SON-T 600 W | 0.23 | 4.9 | 3.2 | 0.91
SON-T DECO 250 W | 0.23 | 1.4 | 2.3 | 0.86
SON-T PLUS 50 W | 0.23 | 0.3 | 0.45 | 0.88
SON-T PLUS 70 W | 0.23 | 0.45 | 0.6 | 0.77
SON-T PLUS 100 W | 0.23 | 0.65 | 1 | 0.76
SON-T PLUS 150 W | 0.23 | 0.85 | 1.2 | 0.86
SON-T PLUS 250 W | 0.23 | 1.4 | 2.3 | 0.86
SON-T PLUS 400 W | 0.23 | 2.2 | 3.6 | 0.86
SON-T PLUS DIM 70 W | 0.23 | 0.45 | 0.6 | 0.77
SON-T PLUS DIM 100 W | 0.23 | 0.65 | 1 | 0.76
SON-T PLUS DIM 150 W | 0.23 | 0.85 | 1.2 | 0.86
SOX 35 W | 0.23 | 0.22 | 0.28 | 0.89
SOX 55 W | 0.23 | 0.34 | 0.39 | 0.94
SOX 90 W | 0.23 | 0.5 | 0.57 | 0.95
SOX 135 W | 0.23 | 0.73 | 0.95 | 0.92
SOX 180 W | 0.23 | 1 | 1.3 | 0.91
SOX-E 18 W | 0.23 | 0.35 | 0.19 | 0.78
SOX-E 26 W | 0.23 | 0.16 | 0.22 | 0.84
SOX-E 36 W | 0.23 | 0.22 | 0.31 | 0.95
SOX-E 66 W | 0.23 | 0.39 | 0.49 | 0.9
SOX-E 91 W | 0.23 | 0.49 | 0.66 | 0.95
SOX-E 131 W | 0.23 | 0.6 | 0.95 | 0.99
SOX-E HF 35 W | 0.23 | 0.17 | 0.17 | 0.95
SOX-E HF 36 W | 0.23 | 0.18 | 0.18 | 0.95
SOX-E HF 55 W | 0.23 | 0.26 | 0.26 | 0.95
SOX-E HF 66 W | 0.23 | 0.31 | 0.31 | 0.95
SOX-E HF 91 W | 0.23 | 0.43 | 0.43 | 0.95
TC-L 840 32 W | 0.23 | 0.16 | 0.16 | 1
TC-TEL 32 W | 0.23 | 0.16 | 0.16 | 1
TL 8 W | 0.23 | 0.06 | 0.06 | 1
TL 65 W | 0.23 | 0.34 | 0.34 | 1
TL 29 8 W | 0.23 | 0.06 | 0.06 | 1
TL 33 8 W | 0.23 | 0.06 | 0.06 | 1
TL 33 40 W | 0.23 | 0.24 | 0.24 | 1
TL 827 8 W | 0.23 | 0.06 | 0.06 | 1
TL 830 8 W | 0.23 | 0.06 | 0.06 | 1
TL 830 65 W | 0.23 | 0.34 | 0.34 | 1
TL 840 8 W | 0.23 | 0.06 | 0.06 | 1
TL 965 8 W | 0.23 | 0.06 | 0.06 | 1
TLD 18 W | 0.23 | 0.12 | 0.12 | 1
TLD 29 18 W | 0.23 | 0.12 | 0.12 | 1
TLD 33 18 W | 0.23 | 0.12 | 0.12 | 1
TLD 54 18 W | 0.23 | 0.12 | 0.12 | 1
TLD 330 18 W | 0.23 | 0.12 | 0.12 | 1
TLD 827 18 W | 0.23 | 0.12 | 0.12 | 1
TLD 827 36 W | 0.23 | 0.2 | 0.2 | 1
TLD 830 18 W | 0.23 | 0.12 | 0.12 | 1
TLD 830 36 W | 0.23 | 0.2 | 0.2 | 1
TLD 830 58 W | 0.23 | 0.3 | 0.3 | 1
TLD 840 18 W | 0.23 | 0.12 | 0.12 | 1
TLD 840 36 W | 0.23 | 0.2 | 0.2 | 1
TLD 865 18 W | 0.23 | 0.12 | 0.12 | 1
TLD 930 18 W | 0.23 | 0.12 | 0.12 | 1
TLD 940 18 W | 0.23 | 0.12 | 0.12 | 1
TLD 950 18 W | 0.23 | 0.12 | 0.12 | 1
TLD 965 18 W | 0.23 | 0.12 | 0.12 | 1
TLD HF 827 18 W | 0.23 | 0.09 | 0.09 | 1
TLD HF 827 36 W | 0.23 | 0.16 | 0.16 | 1
TLD HF 830 18 W | 0.23 | 0.09 | 0.09 | 1
TLD HF 830 36 W | 0.23 | 0.16 | 0.16 | 1
TLD HF 830 58 W | 0.23 | 0.3 | 0.3 | 1
TLD HF 840 18 W | 0.23 | 0.09 | 0.09 | 1
TLD HF 840 36 W | 0.23 | 0.16 | 0.16 | 1
TLD HF 865 18 W | 0.23 | 0.09 | 0.09 | 1
TLD HF 930 18 W | 0.23 | 0.09 | 0.09 | 1
TLD HF 940 18 W | 0.23 | 0.09 | 0.09 | 1
TLD HF 950 18 W | 0.23 | 0.09 | 0.09 | 1
TLD HF 965 18 W | 0.23 | 0.09 | 0.09 | 1
TLEM 40 W | 0.23 | 0.24 | 0.24 | 1
TLF 40 W | 0.23 | 0.24 | 0.24 | 1
TLF 65 W | 0.23 | 0.34 | 0.34 | 1
TLM 40 W | 0.23 | 0.24 | 0.24 | 1
TLM 65 W | 0.23 | 0.34 | 0.34 | 1
TLM 29 40 W | 0.23 | 0.24 | 0.24 | 1
TLM 33 RS 65 W | 0.23 | 0.34 | 0.34 | 1
TLMF 58 W | 0.23 | 0.3 | 0.3 | 1
TLMF 65 W | 0.23 | 0.34 | 0.34 | 1
TLS 20 W | 0.23 | 0.14 | 0.14 | 1
TLS 40 W | 0.23 | 0.24 | 0.24 | 1
TLX 40 W | 0.23 | 0.24 | 0.24 | 1
TLX 33 40 W | 0.23 | 0.24 | 0.24 | 1
Test 400 V 100 W | 0.4 | 0.35 | 0.5 | 0.99
Test 400 V 200 W | 0.4 | 0.7 | 1 | 0.99
Test 400 V 300 W | 0.4 | 1 | 1.5 | 0.99

## Profile
Name | Sort | f1 | f2 | f3 | f4 | f5 | f6 | f7 | f8 | f9 | f10 | f11 | f12 | f13 | f14 | f15 | f16 | f17 | f18 | f19 | f20 | f21 | f22 | f23 | f24 | f25 | f26 | f27 | f28 | f29 | f30 | f31 | f32 | f33 | f34 | f35 | f36 | f37 | f38 | f39 | f40 | f41 | f42 | f43 | f44 | f45 | f46 | f47 | f48 | f49 | f50 | f51 | f52 | f53 | f54 | f55 | f56 | f57 | f58 | f59 | f60 | f61 | f62 | f63 | f64 | f65 | f66 | f67 | f68 | f69 | f70 | f71 | f72 | f73 | f74 | f75 | f76 | f77 | f78 | f79 | f80 | f81 | f82 | f83 | f84 | f85 | f86 | f87 | f88 | f89 | f90 | f91 | f92 | f93 | f94 | f95 | f96 | f97 | f98 | f99 | f100 | f101 | f102 | f103 | f104 | f105 | f106 | f107 | f108 | f109 | f110 | f111 | f112 | f113 | f114 | f115 | f116 | f117 | f118 | f119 | f120 | f121 | f122 | f123 | f124 | f125 | f126 | f127 | f128 | f129 | f130 | f131 | f132 | f133 | f134 | f135 | f136 | f137 | f138 | f139 | f140 | f141 | f142 | f143 | f144 | f145 | f146 | f147 | f148 | f149 | f150 | f151 | f152 | f153 | f154 | f155 | f156 | f157 | f158 | f159 | f160 | f161 | f162 | f163 | f164 | f165 | f166 | f167 | f168 | f169 | f170 | f171 | f172 | f173 | f174 | f175 | f176 | f177 | f178 | f179 | f180 | f181 | f182 | f183 | f184 | f185 | f186 | f187 | f188 | f189 | f190 | f191 | f192 | f193 | f194 | f195 | f196 | f197 | f198 | f199 | f200 | f201 | f202 | f203 | f204 | f205 | f206 | f207 | f208 | f209 | f210 | f211 | f212 | f213 | f214 | f215 | f216 | f217 | f218 | f219 | f220 | f221 | f222 | f223 | f224 | f225 | f226 | f227 | f228 | f229 | f230 | f231 | f232 | f233 | f234 | f235 | f236 | f237 | f238 | f239 | f240 | f241 | f242 | f243 | f244 | f245 | f246 | f247 | f248 | f249 | f250 | f251 | f252 | f253 | f254 | f255 | f256 | f257 | f258 | f259 | f260 | f261 | f262 | f263 | f264 | f265 | f266 | f267 | f268 | f269 | f270 | f271 | f272 | f273 | f274 | f275 | f276 | f277 | f278 | f279 | f280 | f281 | f282 | f283 | f284 | f285 | f286 | f287 | f288 | f289 | f290 | f291 | f292 | f293 | f294 | f295 | f296 | f297 | f298 | f299 | f300 | f301 | f302 | f303 | f304 | f305 | f306 | f307 | f308 | f309 | f310 | f311 | f312 | f313 | f314 | f315 | f316 | f317 | f318 | f319 | f320 | f321 | f322 | f323 | f324 | f325 | f326 | f327 | f328 | f329 | f330 | f331 | f332 | f333 | f334 | f335 | f336 | f337 | f338 | f339 | f340 | f341 | f342 | f343 | f344 | f345 | f346 | f347 | f348 | f349 | f350 | f351 | f352 | f353 | f354 | f355 | f356 | f357 | f358 | f359 | f360 | f361 | f362 | f363 | f364 | f365 | f366 | f367 | f368 | f369 | f370 | f371 | f372 | f373 | f374 | f375 | f376 | f377 | f378 | f379 | f380 | f381 | f382 | f383 | f384 | f385 | f386 | f387 | f388 | f389 | f390 | f391 | f392 | f393 | f394 | f395 | f396 | f397 | f398 | f399 | f400 | f401 | f402 | f403 | f404 | f405 | f406 | f407 | f408 | f409 | f410 | f411 | f412 | f413 | f414 | f415 | f416 | f417 | f418 | f419 | f420 | f421 | f422 | f423 | f424 | f425 | f426 | f427 | f428 | f429 | f430 | f431 | f432 | f433 | f434 | f435 | f436 | f437 | f438 | f439 | f440 | f441 | f442 | f443 | f444 | f445 | f446 | f447 | f448 | f449 | f450 | f451 | f452 | f453 | f454 | f455 | f456 | f457 | f458 | f459 | f460 | f461 | f462 | f463 | f464 | f465 | f466 | f467 | f468 | f469 | f470 | f471 | f472 | f473 | f474 | f475 | f476 | f477 | f478 | f479 | f480 | f481 | f482 | f483 | f484 | f485 | f486 | f487 | f488 | f489 | f490 | f491 | f492 | f493 | f494 | f495 | f496 | f497 | f498 | f499 | f500 | f501 | f502 | f503 | f504 | f505 | f506 | f507 | f508 | f509 | f510 | f511 | f512 | f513 | f514 | f515 | f516 | f517 | f518 | f519 | f520 | f521 | f522 | f523 | f524 | f525 | f526 | f527 | f528 | f529 | f530 | f531 | f532 | f533 | f534 | f535 | f536 | f537 | f538 | f539 | f540 | f541 | f542 | f543 | f544 | f545 | f546 | f547 | f548 | f549 | f550 | f551 | f552 | f553 | f554 | f555 | f556 | f557 | f558 | f559 | f560 | f561 | f562 | f563 | f564 | f565 | f566 | f567 | f568 | f569 | f570 | f571 | f572 | f573 | f574 | f575 | f576 | f577 | f578 | f579 | f580 | f581 | f582 | f583 | f584 | f585 | f586 | f587 | f588 | f589 | f590 | f591 | f592 | f593 | f594 | f595 | f596 | f597 | f598 | f599 | f600 | f601 | f602 | f603 | f604 | f605 | f606 | f607 | f608 | f609 | f610 | f611 | f612 | f613 | f614 | f615 | f616 | f617 | f618 | f619 | f620 | f621 | f622 | f623 | f624 | f625 | f626 | f627 | f628 | f629 | f630 | f631 | f632 | f633 | f634 | f635 | f636 | f637 | f638 | f639 | f640 | f641 | f642 | f643 | f644 | f645 | f646 | f647 | f648 | f649 | f650 | f651 | f652 | f653 | f654 | f655 | f656 | f657 | f658 | f659 | f660 | f661 | f662 | f663 | f664 | f665 | f666 | f667 | f668 | f669 | f670 | f671 | f672 | f673 | f674 | f675 | f676 | f677 | f678 | f679 | f680 | f681 | f682 | f683 | f684 | f685 | f686 | f687 | f688 | f689 | f690 | f691 | f692 | f693 | f694 | f695 | f696 | f697 | f698 | f699 | f700 | f701 | f702 | f703 | f704 | f705 | f706 | f707 | f708 | f709 | f710 | f711 | f712 | f713 | f714 | f715 | f716 | f717 | f718 | f719 | f720 | f721 | f722 | f723 | f724 | f725 | f726 | f727 | f728 | f729 | f730 | f731 | f732 | f733 | f734 | f735 | f736 | f737 | f738 | f739 | f740 | f741 | f742 | f743 | f744 | f745 | f746 | f747 | f748 | f749 | f750 | f751 | f752 | f753 | f754 | f755 | f756 | f757 | f758 | f759 | f760 | f761 | f762 | f763 | f764 | f765 | f766 | f767 | f768 | f769 | f770 | f771 | f772 | f773 | f774 | f775 | f776 | f777 | f778 | f779 | f780 | f781 | f782 | f783 | f784 | f785 | f786 | f787 | f788 | f789 | f790 | f791 | f792 | f793 | f794 | f795 | f796 | f797 | f798 | f799 | f800 | f801 | f802 | f803 | f804 | f805 | f806 | f807 | f808 | f809 | f810 | f811 | f812 | f813 | f814 | f815 | f816 | f817 | f818 | f819 | f820 | f821 | f822 | f823 | f824 | f825 | f826 | f827 | f828 | f829 | f830 | f831 | f832 | f833 | f834 | f835 | f836 | f837 | f838 | f839 | f840 | f841 | f842 | f843 | f844 | f845 | f846 | f847 | f848 | f849 | f850 | f851 | f852 | f853 | f854 | f855 | f856 | f857 | f858 | f859 | f860 | f861 | f862 | f863 | f864 | f865 | f866 | f867 | f868 | f869 | f870 | f871 | f872 | f873 | f874 | f875 | f876 | f877 | f878 | f879 | f880 | f881 | f882 | f883 | f884 | f885 | f886 | f887 | f888 | f889 | f890 | f891 | f892 | f893 | f894 | f895 | f896 | f897 | f898 | f899 | f900 | f901 | f902 | f903 | f904 | f905 | f906 | f907 | f908 | f909 | f910 | f911 | f912 | f913 | f914 | f915 | f916 | f917 | f918 | f919 | f920 | f921 | f922 | f923 | f924 | f925 | f926 | f927 | f928 | f929 | f930 | f931 | f932 | f933 | f934 | f935 | f936 | f937 | f938 | f939 | f940 | f941 | f942 | f943 | f944 | f945 | f946 | f947 | f948 | f949 | f950 | f951 | f952 | f953 | f954 | f955 | f956 | f957 | f958 | f959 | f960 | f961 | f962 | f963 | f964 | f965 | f966 | f967 | f968 | f969 | f970 | f971 | f972 | f973 | f974 | f975 | f976 | f977 | f978 | f979 | f980 | f981 | f982 | f983 | f984 | f985 | f986 | f987 | f988 | f989 | f990 | f991 | f992 | f993 | f994 | f995 | f996 | f997 | f998 | f999 | f1000 | f1001 | f1002 | f1003 | f1004 | f1005 | f1006 | f1007 | f1008 | f1009 | f1010 | f1011 | f1012 | f1013 | f1014 | f1015 | f1016 | f1017 | f1018 | f1019 | f1020 | f1021 | f1022 | f1023 | f1024 | f1025 | f1026 | f1027 | f1028 | f1029 | f1030 | f1031 | f1032 | f1033 | f1034 | f1035 | f1036 | f1037 | f1038 | f1039 | f1040 | f1041 | f1042 | f1043 | f1044 | f1045 | f1046 | f1047 | f1048 | f1049 | f1050 | f1051 | f1052 | f1053 | f1054 | f1055 | f1056 | f1057 | f1058 | f1059 | f1060 | f1061 | f1062 | f1063 | f1064 | f1065 | f1066 | f1067 | f1068 | f1069 | f1070 | f1071 | f1072 | f1073 | f1074 | f1075 | f1076 | f1077 | f1078 | f1079 | f1080 | f1081 | f1082 | f1083 | f1084 | f1085 | f1086 | f1087 | f1088 | f1089 | f1090 | f1091 | f1092 | f1093 | f1094 | f1095 | f1096 | f1097 | f1098 | f1099 | f1100 | f1101 | f1102 | f1103 | f1104 | f1105 | f1106 | f1107 | f1108 | f1109 | f1110 | f1111 | f1112 | f1113 | f1114 | f1115 | f1116 | f1117 | f1118 | f1119 | f1120 | f1121 | f1122 | f1123 | f1124 | f1125 | f1126 | f1127 | f1128 | f1129 | f1130 | f1131 | f1132 | f1133 | f1134 | f1135 | f1136 | f1137 | f1138 | f1139 | f1140 | f1141 | f1142 | f1143 | f1144 | f1145 | f1146 | f1147 | f1148 | f1149 | f1150 | f1151 | f1152 | f1153 | f1154 | f1155 | f1156 | f1157 | f1158 | f1159 | f1160 | f1161 | f1162 | f1163 | f1164 | f1165 | f1166 | f1167 | f1168 | f1169 | f1170 | f1171 | f1172 | f1173 | f1174 | f1175 | f1176 | f1177 | f1178 | f1179 | f1180 | f1181 | f1182 | f1183 | f1184 | f1185 | f1186 | f1187 | f1188 | f1189 | f1190 | f1191 | f1192 | f1193 | f1194 | f1195 | f1196 | f1197 | f1198 | f1199 | f1200 | f1201 | f1202 | f1203 | f1204 | f1205 | f1206 | f1207 | f1208 | f1209 | f1210 | f1211 | f1212 | f1213 | f1214 | f1215 | f1216 | f1217 | f1218 | f1219 | f1220 | f1221 | f1222 | f1223 | f1224 | f1225 | f1226 | f1227 | f1228 | f1229 | f1230 | f1231 | f1232 | f1233 | f1234 | f1235 | f1236 | f1237 | f1238 | f1239 | f1240 | f1241 | f1242 | f1243 | f1244 | f1245 | f1246 | f1247 | f1248 | f1249 | f1250 | f1251 | f1252 | f1253 | f1254 | f1255 | f1256 | f1257 | f1258 | f1259 | f1260 | f1261 | f1262 | f1263 | f1264 | f1265 | f1266 | f1267 | f1268 | f1269 | f1270 | f1271 | f1272 | f1273 | f1274 | f1275 | f1276 | f1277 | f1278 | f1279 | f1280 | f1281 | f1282 | f1283 | f1284 | f1285 | f1286 | f1287 | f1288 | f1289 | f1290 | f1291 | f1292 | f1293 | f1294 | f1295 | f1296 | f1297 | f1298 | f1299 | f1300 | f1301 | f1302 | f1303 | f1304 | f1305 | f1306 | f1307 | f1308 | f1309 | f1310 | f1311 | f1312 | f1313 | f1314 | f1315 | f1316 | f1317 | f1318 | f1319 | f1320 | f1321 | f1322 | f1323 | f1324 | f1325 | f1326 | f1327 | f1328 | f1329 | f1330 | f1331 | f1332 | f1333 | f1334 | f1335 | f1336 | f1337 | f1338 | f1339 | f1340 | f1341 | f1342 | f1343 | f1344 | f1345 | f1346 | f1347 | f1348 | f1349 | f1350 | f1351 | f1352 | f1353 | f1354 | f1355 | f1356 | f1357 | f1358 | f1359 | f1360 | f1361 | f1362 | f1363 | f1364 | f1365 | f1366 | f1367 | f1368 | f1369 | f1370 | f1371 | f1372 | f1373 | f1374 | f1375 | f1376 | f1377 | f1378 | f1379 | f1380 | f1381 | f1382 | f1383 | f1384 | f1385 | f1386 | f1387 | f1388 | f1389 | f1390 | f1391 | f1392 | f1393 | f1394 | f1395 | f1396 | f1397 | f1398 | f1399 | f1400 | f1401 | f1402 | f1403 | f1404 | f1405 | f1406 | f1407 | f1408 | f1409 | f1410 | f1411 | f1412 | f1413 | f1414 | f1415 | f1416 | f1417 | f1418 | f1419 | f1420 | f1421 | f1422 | f1423 | f1424 | f1425 | f1426 | f1427 | f1428 | f1429 | f1430 | f1431 | f1432 | f1433 | f1434 | f1435 | f1436 | f1437 | f1438 | f1439 | f1440 | f1441 | f1442 | f1443 | f1444 | f1445 | f1446 | f1447 | f1448 | f1449 | f1450 | f1451 | f1452 | f1453 | f1454 | f1455 | f1456 | f1457 | f1458 | f1459 | f1460 | f1461 | f1462 | f1463 | f1464 | f1465 | f1466 | f1467 | f1468 | f1469 | f1470 | f1471 | f1472 | f1473 | f1474 | f1475 | f1476 | f1477 | f1478 | f1479 | f1480 | f1481 | f1482 | f1483 | f1484 | f1485 | f1486 | f1487 | f1488 | f1489 | f1490 | f1491 | f1492 | f1493 | f1494 | f1495 | f1496 | f1497 | f1498 | f1499 | f1500 | f1501 | f1502 | f1503 | f1504 | f1505 | f1506 | f1507 | f1508 | f1509 | f1510 | f1511 | f1512 | f1513 | f1514 | f1515 | f1516 | f1517 | f1518 | f1519 | f1520 | f1521 | f1522 | f1523 | f1524 | f1525 | f1526 | f1527 | f1528 | f1529 | f1530 | f1531 | f1532 | f1533 | f1534 | f1535 | f1536 | f1537 | f1538 | f1539 | f1540 | f1541 | f1542 | f1543 | f1544 | f1545 | f1546 | f1547 | f1548 | f1549 | f1550 | f1551 | f1552 | f1553 | f1554 | f1555 | f1556 | f1557 | f1558 | f1559 | f1560 | f1561 | f1562 | f1563 | f1564 | f1565 | f1566 | f1567 | f1568 | f1569 | f1570 | f1571 | f1572 | f1573 | f1574 | f1575 | f1576 | f1577 | f1578 | f1579 | f1580 | f1581 | f1582 | f1583 | f1584 | f1585 | f1586 | f1587 | f1588 | f1589 | f1590 | f1591 | f1592 | f1593 | f1594 | f1595 | f1596 | f1597 | f1598 | f1599 | f1600 | f1601 | f1602 | f1603 | f1604 | f1605 | f1606 | f1607 | f1608 | f1609 | f1610 | f1611 | f1612 | f1613 | f1614 | f1615 | f1616 | f1617 | f1618 | f1619 | f1620 | f1621 | f1622 | f1623 | f1624 | f1625 | f1626 | f1627 | f1628 | f1629 | f1630 | f1631 | f1632 | f1633 | f1634 | f1635 | f1636 | f1637 | f1638 | f1639 | f1640 | f1641 | f1642 | f1643 | f1644 | f1645 | f1646 | f1647 | f1648 | f1649 | f1650 | f1651 | f1652 | f1653 | f1654 | f1655 | f1656 | f1657 | f1658 | f1659 | f1660 | f1661 | f1662 | f1663 | f1664 | f1665 | f1666 | f1667 | f1668 | f1669 | f1670 | f1671 | f1672 | f1673 | f1674 | f1675 | f1676 | f1677 | f1678 | f1679 | f1680 | f1681 | f1682 | f1683 | f1684 | f1685 | f1686 | f1687 | f1688 | f1689 | f1690 | f1691 | f1692 | f1693 | f1694 | f1695 | f1696 | f1697 | f1698 | f1699 | f1700 | f1701 | f1702 | f1703 | f1704 | f1705 | f1706 | f1707 | f1708 | f1709 | f1710 | f1711 | f1712 | f1713 | f1714 | f1715 | f1716 | f1717 | f1718 | f1719 | f1720 | f1721 | f1722 | f1723 | f1724 | f1725 | f1726 | f1727 | f1728 | f1729 | f1730 | f1731 | f1732 | f1733 | f1734 | f1735 | f1736 | f1737 | f1738 | f1739 | f1740 | f1741 | f1742 | f1743 | f1744 | f1745 | f1746 | f1747 | f1748 | f1749 | f1750 | f1751 | f1752 | f1753 | f1754 | f1755 | f1756 | f1757 | f1758 | f1759 | f1760 | f1761 | f1762 | f1763 | f1764 | f1765 | f1766 | f1767 | f1768 | f1769 | f1770 | f1771 | f1772 | f1773 | f1774 | f1775 | f1776 | f1777 | f1778 | f1779 | f1780 | f1781 | f1782 | f1783 | f1784 | f1785 | f1786 | f1787 | f1788 | f1789 | f1790 | f1791 | f1792 | f1793 | f1794 | f1795 | f1796 | f1797 | f1798 | f1799 | f1800 | f1801 | f1802 | f1803 | f1804 | f1805 | f1806 | f1807 | f1808 | f1809 | f1810 | f1811 | f1812 | f1813 | f1814 | f1815 | f1816 | f1817 | f1818 | f1819 | f1820 | f1821 | f1822 | f1823 | f1824 | f1825 | f1826 | f1827 | f1828 | f1829 | f1830 | f1831 | f1832 | f1833 | f1834 | f1835 | f1836 | f1837 | f1838 | f1839 | f1840 | f1841 | f1842 | f1843 | f1844 | f1845 | f1846 | f1847 | f1848 | f1849 | f1850 | f1851 | f1852 | f1853 | f1854 | f1855 | f1856 | f1857 | f1858 | f1859 | f1860 | f1861 | f1862 | f1863 | f1864 | f1865 | f1866 | f1867 | f1868 | f1869 | f1870 | f1871 | f1872 | f1873 | f1874 | f1875 | f1876 | f1877 | f1878 | f1879 | f1880 | f1881 | f1882 | f1883 | f1884 | f1885 | f1886 | f1887 | f1888 | f1889 | f1890 | f1891 | f1892 | f1893 | f1894 | f1895 | f1896 | f1897 | f1898 | f1899 | f1900 | f1901 | f1902 | f1903 | f1904 | f1905 | f1906 | f1907 | f1908 | f1909 | f1910 | f1911 | f1912 | f1913 | f1914 | f1915 | f1916 | f1917 | f1918 | f1919 | f1920 | f1921 | f1922 | f1923 | f1924 | f1925 | f1926 | f1927 | f1928 | f1929 | f1930 | f1931 | f1932 | f1933 | f1934 | f1935 | f1936 | f1937 | f1938 | f1939 | f1940 | f1941 | f1942 | f1943 | f1944 | f1945 | f1946 | f1947 | f1948 | f1949 | f1950 | f1951 | f1952 | f1953 | f1954 | f1955 | f1956 | f1957 | f1958 | f1959 | f1960 | f1961 | f1962 | f1963 | f1964 | f1965 | f1966 | f1967 | f1968 | f1969 | f1970 | f1971 | f1972 | f1973 | f1974 | f1975 | f1976 | f1977 | f1978 | f1979 | f1980 | f1981 | f1982 | f1983 | f1984 | f1985 | f1986 | f1987 | f1988 | f1989 | f1990 | f1991 | f1992 | f1993 | f1994 | f1995 | f1996 | f1997 | f1998 | f1999 | f2000 | f2001 | f2002 | f2003 | f2004 | f2005 | f2006 | f2007 | f2008 | f2009 | f2010 | f2011 | f2012 | f2013 | f2014 | f2015 | f2016 | f2017 | f2018 | f2019 | f2020 | f2021 | f2022 | f2023 | f2024 | f2025 | f2026 | f2027 | f2028 | f2029 | f2030 | f2031 | f2032 | f2033 | f2034 | f2035 | f2036 | f2037 | f2038 | f2039 | f2040 | f2041 | f2042 | f2043 | f2044 | f2045 | f2046 | f2047 | f2048 | f2049 | f2050 | f2051 | f2052 | f2053 | f2054 | f2055 | f2056 | f2057 | f2058 | f2059 | f2060 | f2061 | f2062 | f2063 | f2064 | f2065 | f2066 | f2067 | f2068 | f2069 | f2070 | f2071 | f2072 | f2073 | f2074 | f2075 | f2076 | f2077 | f2078 | f2079 | f2080 | f2081 | f2082 | f2083 | f2084 | f2085 | f2086 | f2087 | f2088 | f2089 | f2090 | f2091 | f2092 | f2093 | f2094 | f2095 | f2096 | f2097 | f2098 | f2099 | f2100 | f2101 | f2102 | f2103 | f2104 | f2105 | f2106 | f2107 | f2108 | f2109 | f2110 | f2111 | f2112 | f2113 | f2114 | f2115 | f2116 | f2117 | f2118 | f2119 | f2120 | f2121 | f2122 | f2123 | f2124 | f2125 | f2126 | f2127 | f2128 | f2129 | f2130 | f2131 | f2132 | f2133 | f2134 | f2135 | f2136 | f2137 | f2138 | f2139 | f2140 | f2141 | f2142 | f2143 | f2144 | f2145 | f2146 | f2147 | f2148 | f2149 | f2150 | f2151 | f2152 | f2153 | f2154 | f2155 | f2156 | f2157 | f2158 | f2159 | f2160 | f2161 | f2162 | f2163 | f2164 | f2165 | f2166 | f2167 | f2168 | f2169 | f2170 | f2171 | f2172 | f2173 | f2174 | f2175 | f2176 | f2177 | f2178 | f2179 | f2180 | f2181 | f2182 | f2183 | f2184 | f2185 | f2186 | f2187 | f2188 | f2189 | f2190 | f2191 | f2192 | f2193 | f2194 | f2195 | f2196 | f2197 | f2198 | f2199 | f2200 | f2201 | f2202 | f2203 | f2204 | f2205 | f2206 | f2207 | f2208 | f2209 | f2210 | f2211 | f2212 | f2213 | f2214 | f2215 | f2216 | f2217 | f2218 | f2219 | f2220 | f2221 | f2222 | f2223 | f2224 | f2225 | f2226 | f2227 | f2228 | f2229 | f2230 | f2231 | f2232 | f2233 | f2234 | f2235 | f2236 | f2237 | f2238 | f2239 | f2240 | f2241 | f2242 | f2243 | f2244 | f2245 | f2246 | f2247 | f2248 | f2249 | f2250 | f2251 | f2252 | f2253 | f2254 | f2255 | f2256 | f2257 | f2258 | f2259 | f2260 | f2261 | f2262 | f2263 | f2264 | f2265 | f2266 | f2267 | f2268 | f2269 | f2270 | f2271 | f2272 | f2273 | f2274 | f2275 | f2276 | f2277 | f2278 | f2279 | f2280 | f2281 | f2282 | f2283 | f2284 | f2285 | f2286 | f2287 | f2288 | f2289 | f2290 | f2291 | f2292 | f2293 | f2294 | f2295 | f2296 | f2297 | f2298 | f2299 | f2300 | f2301 | f2302 | f2303 | f2304 | f2305 | f2306 | f2307 | f2308 | f2309 | f2310 | f2311 | f2312 | f2313 | f2314 | f2315 | f2316 | f2317 | f2318 | f2319 | f2320 | f2321 | f2322 | f2323 | f2324 | f2325 | f2326 | f2327 | f2328 | f2329 | f2330 | f2331 | f2332 | f2333 | f2334 | f2335 | f2336 | f2337 | f2338 | f2339 | f2340 | f2341 | f2342 | f2343 | f2344 | f2345 | f2346 | f2347 | f2348 | f2349 | f2350 | f2351 | f2352 | f2353 | f2354 | f2355 | f2356 | f2357 | f2358 | f2359 | f2360 | f2361 | f2362 | f2363 | f2364 | f2365 | f2366 | f2367 | f2368 | f2369 | f2370 | f2371 | f2372 | f2373 | f2374 | f2375 | f2376 | f2377 | f2378 | f2379 | f2380 | f2381 | f2382 | f2383 | f2384 | f2385 | f2386 | f2387 | f2388 | f2389 | f2390 | f2391 | f2392 | f2393 | f2394 | f2395 | f2396 | f2397 | f2398 | f2399 | f2400 | f2401 | f2402 | f2403 | f2404 | f2405 | f2406 | f2407 | f2408 | f2409 | f2410 | f2411 | f2412 | f2413 | f2414 | f2415 | f2416 | f2417 | f2418 | f2419 | f2420 | f2421 | f2422 | f2423 | f2424 | f2425 | f2426 | f2427 | f2428 | f2429 | f2430 | f2431 | f2432 | f2433 | f2434 | f2435 | f2436 | f2437 | f2438 | f2439 | f2440 | f2441 | f2442 | f2443 | f2444 | f2445 | f2446 | f2447 | f2448 | f2449 | f2450 | f2451 | f2452 | f2453 | f2454 | f2455 | f2456 | f2457 | f2458 | f2459 | f2460 | f2461 | f2462 | f2463 | f2464 | f2465 | f2466 | f2467 | f2468 | f2469 | f2470 | f2471 | f2472 | f2473 | f2474 | f2475 | f2476 | f2477 | f2478 | f2479 | f2480 | f2481 | f2482 | f2483 | f2484 | f2485 | f2486 | f2487 | f2488 | f2489 | f2490 | f2491 | f2492 | f2493 | f2494 | f2495 | f2496 | f2497 | f2498 | f2499 | f2500 | f2501 | f2502 | f2503 | f2504 | f2505 | f2506 | f2507 | f2508 | f2509 | f2510 | f2511 | f2512 | f2513 | f2514 | f2515 | f2516 | f2517 | f2518 | f2519 | f2520 | f2521 | f2522 | f2523 | f2524 | f2525 | f2526 | f2527 | f2528 | f2529 | f2530 | f2531 | f2532 | f2533 | f2534 | f2535 | f2536 | f2537 | f2538 | f2539 | f2540 | f2541 | f2542 | f2543 | f2544 | f2545 | f2546 | f2547 | f2548 | f2549 | f2550 | f2551 | f2552 | f2553 | f2554 | f2555 | f2556 | f2557 | f2558 | f2559 | f2560 | f2561 | f2562 | f2563 | f2564 | f2565 | f2566 | f2567 | f2568 | f2569 | f2570 | f2571 | f2572 | f2573 | f2574 | f2575 | f2576 | f2577 | f2578 | f2579 | f2580 | f2581 | f2582 | f2583 | f2584 | f2585 | f2586 | f2587 | f2588 | f2589 | f2590 | f2591 | f2592 | f2593 | f2594 | f2595 | f2596 | f2597 | f2598 | f2599 | f2600 | f2601 | f2602 | f2603 | f2604 | f2605 | f2606 | f2607 | f2608 | f2609 | f2610 | f2611 | f2612 | f2613 | f2614 | f2615 | f2616 | f2617 | f2618 | f2619 | f2620 | f2621 | f2622 | f2623 | f2624 | f2625 | f2626 | f2627 | f2628 | f2629 | f2630 | f2631 | f2632 | f2633 | f2634 | f2635 | f2636 | f2637 | f2638 | f2639 | f2640 | f2641 | f2642 | f2643 | f2644 | f2645 | f2646 | f2647 | f2648 | f2649 | f2650 | f2651 | f2652 | f2653 | f2654 | f2655 | f2656 | f2657 | f2658 | f2659 | f2660 | f2661 | f2662 | f2663 | f2664 | f2665 | f2666 | f2667 | f2668 | f2669 | f2670 | f2671 | f2672 | f2673 | f2674 | f2675 | f2676 | f2677 | f2678 | f2679 | f2680 | f2681 | f2682 | f2683 | f2684 | f2685 | f2686 | f2687 | f2688 | f2689 | f2690 | f2691 | f2692 | f2693 | f2694 | f2695 | f2696 | f2697 | f2698 | f2699 | f2700 | f2701 | f2702 | f2703 | f2704 | f2705 | f2706 | f2707 | f2708 | f2709 | f2710 | f2711 | f2712 | f2713 | f2714 | f2715 | f2716 | f2717 | f2718 | f2719 | f2720 | f2721 | f2722 | f2723 | f2724 | f2725 | f2726 | f2727 | f2728 | f2729 | f2730 | f2731 | f2732 | f2733 | f2734 | f2735 | f2736 | f2737 | f2738 | f2739 | f2740 | f2741 | f2742 | f2743 | f2744 | f2745 | f2746 | f2747 | f2748 | f2749 | f2750 | f2751 | f2752 | f2753 | f2754 | f2755 | f2756 | f2757 | f2758 | f2759 | f2760 | f2761 | f2762 | f2763 | f2764 | f2765 | f2766 | f2767 | f2768 | f2769 | f2770 | f2771 | f2772 | f2773 | f2774 | f2775 | f2776 | f2777 | f2778 | f2779 | f2780 | f2781 | f2782 | f2783 | f2784 | f2785 | f2786 | f2787 | f2788 | f2789 | f2790 | f2791 | f2792 | f2793 | f2794 | f2795 | f2796 | f2797 | f2798 | f2799 | f2800 | f2801 | f2802 | f2803 | f2804 | f2805 | f2806 | f2807 | f2808 | f2809 | f2810 | f2811 | f2812 | f2813 | f2814 | f2815 | f2816 | f2817 | f2818 | f2819 | f2820 | f2821 | f2822 | f2823 | f2824 | f2825 | f2826 | f2827 | f2828 | f2829 | f2830 | f2831 | f2832 | f2833 | f2834 | f2835 | f2836 | f2837 | f2838 | f2839 | f2840 | f2841 | f2842 | f2843 | f2844 | f2845 | f2846 | f2847 | f2848 | f2849 | f2850 | f2851 | f2852 | f2853 | f2854 | f2855 | f2856 | f2857 | f2858 | f2859 | f2860 | f2861 | f2862 | f2863 | f2864 | f2865 | f2866 | f2867 | f2868 | f2869 | f2870 | f2871 | f2872 | f2873 | f2874 | f2875 | f2876 | f2877 | f2878 | f2879 | f2880 | f2881 | f2882 | f2883 | f2884 | f2885 | f2886 | f2887 | f2888 | f2889 | f2890 | f2891 | f2892 | f2893 | f2894 | f2895 | f2896 | f2897 | f2898 | f2899 | f2900 | f2901 | f2902 | f2903 | f2904 | f2905 | f2906 | f2907 | f2908 | f2909 | f2910 | f2911 | f2912 | f2913 | f2914 | f2915 | f2916 | f2917 | f2918 | f2919 | f2920 | f2921 | f2922 | f2923 | f2924 | f2925 | f2926 | f2927 | f2928 | f2929 | f2930 | f2931 | f2932 | f2933 | f2934 | f2935 | f2936 | f2937 | f2938 | f2939 | f2940 | f2941 | f2942 | f2943 | f2944 | f2945 | f2946 | f2947 | f2948 | f2949 | f2950 | f2951 | f2952 | f2953 | f2954 | f2955 | f2956 | f2957 | f2958 | f2959 | f2960 | f2961 | f2962 | f2963 | f2964 | f2965 | f2966 | f2967 | f2968 | f2969 | f2970 | f2971 | f2972 | f2973 | f2974 | f2975 | f2976 | f2977 | f2978 | f2979 | f2980 | f2981 | f2982 | f2983 | f2984 | f2985 | f2986 | f2987 | f2988 | f2989 | f2990 | f2991 | f2992 | f2993 | f2994 | f2995 | f2996 | f2997 | f2998 | f2999 | f3000 | f3001 | f3002 | f3003 | f3004 | f3005 | f3006 | f3007 | f3008 | f3009 | f3010 | f3011 | f3012 | f3013 | f3014 | f3015 | f3016 | f3017 | f3018 | f3019 | f3020 | f3021 | f3022 | f3023 | f3024 | f3025 | f3026 | f3027 | f3028 | f3029 | f3030 | f3031 | f3032 | f3033 | f3034 | f3035 | f3036 | f3037 | f3038 | f3039 | f3040 | f3041 | f3042 | f3043 | f3044 | f3045 | f3046 | f3047 | f3048 | f3049 | f3050 | f3051 | f3052 | f3053 | f3054 | f3055 | f3056 | f3057 | f3058 | f3059 | f3060 | f3061 | f3062 | f3063 | f3064 | f3065 | f3066 | f3067 | f3068 | f3069 | f3070 | f3071 | f3072 | f3073 | f3074 | f3075 | f3076 | f3077 | f3078 | f3079 | f3080 | f3081 | f3082 | f3083 | f3084 | f3085 | f3086 | f3087 | f3088 | f3089 | f3090 | f3091 | f3092 | f3093 | f3094 | f3095 | f3096 | f3097 | f3098 | f3099 | f3100 | f3101 | f3102 | f3103 | f3104 | f3105 | f3106 | f3107 | f3108 | f3109 | f3110 | f3111 | f3112 | f3113 | f3114 | f3115 | f3116 | f3117 | f3118 | f3119 | f3120 | f3121 | f3122 | f3123 | f3124 | f3125 | f3126 | f3127 | f3128 | f3129 | f3130 | f3131 | f3132 | f3133 | f3134 | f3135 | f3136 | f3137 | f3138 | f3139 | f3140 | f3141 | f3142 | f3143 | f3144 | f3145 | f3146 | f3147 | f3148 | f3149 | f3150 | f3151 | f3152 | f3153 | f3154 | f3155 | f3156 | f3157 | f3158 | f3159 | f3160 | f3161 | f3162 | f3163 | f3164 | f3165 | f3166 | f3167 | f3168 | f3169 | f3170 | f3171 | f3172 | f3173 | f3174 | f3175 | f3176 | f3177 | f3178 | f3179 | f3180 | f3181 | f3182 | f3183 | f3184 | f3185 | f3186 | f3187 | f3188 | f3189 | f3190 | f3191 | f3192 | f3193 | f3194 | f3195 | f3196 | f3197 | f3198 | f3199 | f3200 | f3201 | f3202 | f3203 | f3204 | f3205 | f3206 | f3207 | f3208 | f3209 | f3210 | f3211 | f3212 | f3213 | f3214 | f3215 | f3216 | f3217 | f3218 | f3219 | f3220 | f3221 | f3222 | f3223 | f3224 | f3225 | f3226 | f3227 | f3228 | f3229 | f3230 | f3231 | f3232 | f3233 | f3234 | f3235 | f3236 | f3237 | f3238 | f3239 | f3240 | f3241 | f3242 | f3243 | f3244 | f3245 | f3246 | f3247 | f3248 | f3249 | f3250 | f3251 | f3252 | f3253 | f3254 | f3255 | f3256 | f3257 | f3258 | f3259 | f3260 | f3261 | f3262 | f3263 | f3264 | f3265 | f3266 | f3267 | f3268 | f3269 | f3270 | f3271 | f3272 | f3273 | f3274 | f3275 | f3276 | f3277 | f3278 | f3279 | f3280 | f3281 | f3282 | f3283 | f3284 | f3285 | f3286 | f3287 | f3288 | f3289 | f3290 | f3291 | f3292 | f3293 | f3294 | f3295 | f3296 | f3297 | f3298 | f3299 | f3300 | f3301 | f3302 | f3303 | f3304 | f3305 | f3306 | f3307 | f3308 | f3309 | f3310 | f3311 | f3312 | f3313 | f3314 | f3315 | f3316 | f3317 | f3318 | f3319 | f3320 | f3321 | f3322 | f3323 | f3324 | f3325 | f3326 | f3327 | f3328 | f3329 | f3330 | f3331 | f3332 | f3333 | f3334 | f3335 | f3336 | f3337 | f3338 | f3339 | f3340 | f3341 | f3342 | f3343 | f3344 | f3345 | f3346 | f3347 | f3348 | f3349 | f3350 | f3351 | f3352 | f3353 | f3354 | f3355 | f3356 | f3357 | f3358 | f3359 | f3360 | f3361 | f3362 | f3363 | f3364 | f3365 | f3366 | f3367 | f3368 | f3369 | f3370 | f3371 | f3372 | f3373 | f3374 | f3375 | f3376 | f3377 | f3378 | f3379 | f3380 | f3381 | f3382 | f3383 | f3384 | f3385 | f3386 | f3387 | f3388 | f3389 | f3390 | f3391 | f3392 | f3393 | f3394 | f3395 | f3396 | f3397 | f3398 | f3399 | f3400 | f3401 | f3402 | f3403 | f3404 | f3405 | f3406 | f3407 | f3408 | f3409 | f3410 | f3411 | f3412 | f3413 | f3414 | f3415 | f3416 | f3417 | f3418 | f3419 | f3420 | f3421 | f3422 | f3423 | f3424 | f3425 | f3426 | f3427 | f3428 | f3429 | f3430 | f3431 | f3432 | f3433 | f3434 | f3435 | f3436 | f3437 | f3438 | f3439 | f3440 | f3441 | f3442 | f3443 | f3444 | f3445 | f3446 | f3447 | f3448 | f3449 | f3450 | f3451 | f3452 | f3453 | f3454 | f3455 | f3456
Voorbeeld dorp | -168 | 0.474 | 0.411 | 0.38 | 0.365 | 0.373 | 0.388 | 0.538 | 0.794 | 0.797 | 0.66 | 0.584 | 0.543 | 0.509 | 0.501 | 0.494 | 0.541 | 0.58 | 0.761 | 0.67 | 0.612 | 0.585 | 0.685 | 0.688 | 0.678 | 0.511 | 0.43 | 0.392 | 0.37 | 0.36 | 0.401 | 0.499 | 0.669 | 0.732 | 0.606 | 0.52 | 0.431 | 0.468 | 0.456 | 0.446 | 0.441 | 0.521 | 0.732 | 0.816 | 0.616 | 0.527 | 0.666 | 0.659 | 0.638 | 0.548 | 0.424 | 0.369 | 0.385 | 0.358 | 0.398 | 0.513 | 0.754 | 0.763 | 0.647 | 0.531 | 0.482 | 0.494 | 0.469 | 0.48 | 0.48 | 0.552 | 0.78 | 0.723 | 0.654 | 0.61 | 0.667 | 0.681 | 0.807 | 0.581 | 0.448 | 0.397 | 0.374 | 0.385 | 0.414 | 0.539 | 0.836 | 0.849 | 0.665 | 0.552 | 0.521 | 0.547 | 0.523 | 0.508 | 0.482 | 0.47 | 0.74 | 0.843 | 0.711 | 0.618 | 0.733 | 0.765 | 0.75 | 0.592 | 0.453 | 0.414 | 0.417 | 0.419 | 0.431 | 0.548 | 0.758 | 0.846 | 0.668 | 0.58 | 0.593 | 0.585 | 0.519 | 0.505 | 0.487 | 0.511 | 0.759 | 0.894 | 0.791 | 0.677 | 0.745 | 0.734 | 0.727 | 0.624 | 0.498 | 0.444 | 0.422 | 0.413 | 0.426 | 0.485 | 0.741 | 0.928 | 0.792 | 0.706 | 0.678 | 0.649 | 0.64 | 0.582 | 0.54 | 0.601 | 0.836 | 1 | 0.835 | 0.741 | 0.756 | 0.698 | 0.707 | 0.53 | 0.468 | 0.411 | 0.376 | 0.363 | 0.369 | 0.432 | 0.623 | 0.636 | 0.594 | 0.565 | 0.591 | 0.659 | 0.577 | 0.506 | 0.537 | 0.592 | 0.772 | 0.735 | 0.562 | 0.636 | 0.691 | 0.69 | 0.674
Voorbeeld flat | -168 | 0.602 | 0.543 | 0.515 | 0.496 | 0.49 | 0.496 | 0.504 | 0.55 | 0.618 | 0.709 | 0.696 | 0.678 | 0.675 | 0.666 | 0.636 | 0.627 | 0.702 | 0.778 | 0.79 | 0.78 | 0.797 | 0.781 | 0.757 | 0.712 | 0.622 | 0.549 | 0.523 | 0.506 | 0.5 | 0.505 | 0.511 | 0.55 | 0.607 | 0.643 | 0.696 | 0.736 | 0.77 | 0.727 | 0.672 | 0.675 | 0.743 | 0.864 | 0.881 | 0.856 | 0.823 | 0.775 | 0.756 | 0.684 | 0.602 | 0.545 | 0.511 | 0.509 | 0.504 | 0.501 | 0.518 | 0.574 | 0.709 | 0.778 | 0.819 | 0.787 | 0.825 | 0.778 | 0.787 | 0.778 | 0.84 | 0.935 | 0.943 | 0.892 | 0.883 | 0.834 | 0.753 | 0.681 | 0.589 | 0.518 | 0.506 | 0.502 | 0.498 | 0.502 | 0.53 | 0.614 | 0.725 | 0.735 | 0.742 | 0.767 | 0.768 | 0.763 | 0.721 | 0.715 | 0.76 | 0.98 | 0.989 | 1 | 0.933 | 0.891 | 0.822 | 0.73 | 0.622 | 0.543 | 0.534 | 0.531 | 0.522 | 0.535 | 0.544 | 0.632 | 0.74 | 0.778 | 0.772 | 0.697 | 0.722 | 0.69 | 0.694 | 0.697 | 0.737 | 0.935 | 0.928 | 0.936 | 0.894 | 0.861 | 0.784 | 0.698 | 0.631 | 0.564 | 0.52 | 0.511 | 0.514 | 0.506 | 0.537 | 0.591 | 0.691 | 0.762 | 0.808 | 0.803 | 0.851 | 0.756 | 0.732 | 0.707 | 0.77 | 0.969 | 0.954 | 0.996 | 0.925 | 0.883 | 0.819 | 0.725 | 0.645 | 0.552 | 0.499 | 0.498 | 0.489 | 0.49 | 0.495 | 0.535 | 0.611 | 0.682 | 0.742 | 0.756 | 0.763 | 0.738 | 0.702 | 0.721 | 0.782 | 0.904 | 0.89 | 0.905 | 0.847 | 0.813 | 0.762 | 0.703
Voorbeeld stad | -168 | 0.472 | 0.341 | 0.336 | 0.308 | 0.285 | 0.29 | 0.344 | 0.466 | 0.442 | 0.401 | 0.418 | 0.43 | 0.472 | 0.48 | 0.459 | 0.462 | 0.471 | 0.669 | 0.824 | 0.813 | 0.806 | 0.749 | 0.622 | 0.666 | 0.514 | 0.376 | 0.331 | 0.316 | 0.28 | 0.292 | 0.337 | 0.499 | 0.49 | 0.432 | 0.455 | 0.418 | 0.463 | 0.419 | 0.376 | 0.413 | 0.473 | 0.698 | 0.771 | 0.817 | 0.766 | 0.706 | 0.652 | 0.748 | 0.556 | 0.356 | 0.329 | 0.312 | 0.288 | 0.306 | 0.339 | 0.481 | 0.476 | 0.482 | 0.454 | 0.4 | 0.495 | 0.435 | 0.426 | 0.447 | 0.554 | 0.689 | 0.833 | 0.883 | 0.791 | 0.677 | 0.603 | 0.659 | 0.524 | 0.354 | 0.326 | 0.293 | 0.286 | 0.304 | 0.351 | 0.461 | 0.454 | 0.431 | 0.473 | 0.469 | 0.478 | 0.491 | 0.439 | 0.441 | 0.501 | 0.689 | 0.803 | 0.799 | 0.772 | 0.707 | 0.599 | 0.662 | 0.541 | 0.381 | 0.319 | 0.285 | 0.27 | 0.307 | 0.367 | 0.466 | 0.45 | 0.431 | 0.457 | 0.447 | 0.48 | 0.47 | 0.436 | 0.474 | 0.572 | 0.743 | 0.787 | 0.762 | 0.769 | 0.726 | 0.655 | 0.754 | 0.633 | 0.441 | 0.329 | 0.335 | 0.288 | 0.275 | 0.282 | 0.36 | 0.496 | 0.558 | 0.688 | 0.687 | 0.63 | 0.636 | 0.587 | 0.638 | 0.731 | 0.902 | 0.91 | 0.929 | 0.824 | 0.7 | 0.657 | 0.662 | 0.613 | 0.475 | 0.399 | 0.343 | 0.301 | 0.281 | 0.286 | 0.296 | 0.411 | 0.521 | 0.622 | 0.704 | 0.674 | 0.68 | 0.688 | 0.559 | 0.557 | 0.875 | 1 | 0.975 | 0.909 | 0.764 | 0.682 | 0.637
Voorbeeld woning met koken | -168 | 0.343 | 0.192 | 0.18 | 0.18 | 0.191 | 0.211 | 0.255 | 0.559 | 0.648 | 0.648 | 0.592 | 0.496 | 0.494 | 0.443 | 0.407 | 0.56 | 0.679 | 0.916 | 0.953 | 0.881 | 0.803 | 0.879 | 0.744 | 0.427 | 0.319 | 0.212 | 0.202 | 0.183 | 0.185 | 0.201 | 0.293 | 0.585 | 0.718 | 0.719 | 0.622 | 0.536 | 0.516 | 0.584 | 0.547 | 0.59 | 0.746 | 0.888 | 0.964 | 0.902 | 0.888 | 0.82 | 0.644 | 0.432 | 0.316 | 0.201 | 0.183 | 0.181 | 0.191 | 0.223 | 0.327 | 0.59 | 0.761 | 0.685 | 0.591 | 0.537 | 0.519 | 0.475 | 0.494 | 0.574 | 0.763 | 0.962 | 0.902 | 0.986 | 0.925 | 0.939 | 0.676 | 0.44 | 0.317 | 0.193 | 0.176 | 0.176 | 0.174 | 0.201 | 0.293 | 0.523 | 0.668 | 0.592 | 0.544 | 0.624 | 0.509 | 0.572 | 0.631 | 0.606 | 0.769 | 1 | 0.988 | 0.979 | 0.919 | 0.872 | 0.748 | 0.489 | 0.334 | 0.179 | 0.171 | 0.17 | 0.165 | 0.196 | 0.314 | 0.452 | 0.704 | 0.622 | 0.651 | 0.593 | 0.599 | 0.478 | 0.467 | 0.54 | 0.712 | 0.887 | 0.964 | 0.906 | 0.951 | 0.895 | 0.71 | 0.433 | 0.329 | 0.225 | 0.213 | 0.185 | 0.172 | 0.183 | 0.212 | 0.366 | 0.691 | 0.852 | 0.795 | 0.772 | 0.705 | 0.648 | 0.727 | 0.689 | 0.852 | 0.958 | 0.922 | 0.953 | 0.907 | 0.832 | 0.673 | 0.478 | 0.356 | 0.233 | 0.209 | 0.198 | 0.193 | 0.193 | 0.231 | 0.362 | 0.601 | 0.749 | 0.738 | 0.663 | 0.655 | 0.636 | 0.668 | 0.663 | 0.791 | 0.891 | 0.935 | 0.849 | 0.803 | 0.815 | 0.729 | 0.48
Voorbeeld woning all electric | -168 | 0.264 | 0.131 | 0.144 | 0.147 | 0.199 | 0.328 | 0.574 | 0.879 | 0.888 | 0.746 | 0.626 | 0.57 | 0.661 | 0.595 | 0.552 | 0.721 | 0.847 | 0.974 | 0.975 | 0.896 | 0.759 | 0.757 | 0.568 | 0.368 | 0.274 | 0.18 | 0.145 | 0.126 | 0.188 | 0.345 | 0.64 | 0.863 | 0.848 | 0.754 | 0.604 | 0.559 | 0.523 | 0.617 | 0.626 | 0.696 | 0.768 | 0.874 | 0.946 | 0.789 | 0.786 | 0.605 | 0.528 | 0.356 | 0.251 | 0.146 | 0.135 | 0.144 | 0.141 | 0.319 | 0.576 | 0.857 | 0.858 | 0.655 | 0.599 | 0.595 | 0.553 | 0.477 | 0.634 | 0.695 | 0.831 | 0.853 | 0.893 | 0.795 | 0.771 | 0.714 | 0.51 | 0.368 | 0.251 | 0.134 | 0.143 | 0.14 | 0.176 | 0.322 | 0.529 | 0.804 | 0.821 | 0.75 | 0.734 | 0.609 | 0.525 | 0.689 | 0.712 | 0.745 | 0.824 | 0.924 | 0.922 | 0.814 | 0.788 | 0.724 | 0.535 | 0.348 | 0.232 | 0.116 | 0.123 | 0.171 | 0.166 | 0.265 | 0.675 | 0.843 | 0.967 | 0.737 | 0.704 | 0.638 | 0.679 | 0.578 | 0.639 | 0.691 | 0.84 | 0.906 | 1 | 0.898 | 0.866 | 0.749 | 0.518 | 0.349 | 0.247 | 0.146 | 0.157 | 0.166 | 0.204 | 0.331 | 0.549 | 0.744 | 0.896 | 0.915 | 0.862 | 0.696 | 0.693 | 0.708 | 0.733 | 0.7 | 0.827 | 0.899 | 0.835 | 0.825 | 0.749 | 0.72 | 0.507 | 0.376 | 0.264 | 0.151 | 0.161 | 0.156 | 0.2 | 0.332 | 0.602 | 0.748 | 0.976 | 0.885 | 0.759 | 0.694 | 0.779 | 0.658 | 0.732 | 0.756 | 0.942 | 0.916 | 0.986 | 0.902 | 0.821 | 0.722 | 0.534 | 0.384
Voorbeeld landelijk | -168 | 0.46 | 0.409 | 0.391 | 0.365 | 0.375 | 0.393 | 0.441 | 0.695 | 0.73 | 0.762 | 0.746 | 0.744 | 0.703 | 0.699 | 0.679 | 0.646 | 0.713 | 0.78 | 0.819 | 0.932 | 0.938 | 0.793 | 0.725 | 0.615 | 0.514 | 0.413 | 0.391 | 0.382 | 0.375 | 0.418 | 0.476 | 0.683 | 0.711 | 0.656 | 0.648 | 0.687 | 0.702 | 0.679 | 0.692 | 0.681 | 0.687 | 0.784 | 0.826 | 1 | 0.962 | 0.853 | 0.739 | 0.661 | 0.539 | 0.436 | 0.397 | 0.387 | 0.392 | 0.417 | 0.458 | 0.647 | 0.674 | 0.715 | 0.696 | 0.653 | 0.695 | 0.718 | 0.68 | 0.697 | 0.729 | 0.797 | 0.844 | 0.972 | 0.956 | 0.862 | 0.748 | 0.64 | 0.503 | 0.416 | 0.394 | 0.378 | 0.374 | 0.412 | 0.482 | 0.712 | 0.708 | 0.689 | 0.642 | 0.65 | 0.684 | 0.731 | 0.734 | 0.697 | 0.731 | 0.837 | 0.858 | 0.976 | 0.939 | 0.851 | 0.761 | 0.642 | 0.522 | 0.434 | 0.399 | 0.384 | 0.375 | 0.39 | 0.462 | 0.692 | 0.732 | 0.684 | 0.699 | 0.698 | 0.736 | 0.711 | 0.703 | 0.701 | 0.709 | 0.813 | 0.845 | 0.946 | 0.93 | 0.806 | 0.708 | 0.671 | 0.544 | 0.479 | 0.434 | 0.395 | 0.384 | 0.396 | 0.413 | 0.56 | 0.797 | 0.842 | 0.82 | 0.844 | 0.859 | 0.807 | 0.749 | 0.707 | 0.689 | 0.801 | 0.82 | 0.95 | 0.873 | 0.766 | 0.745 | 0.689 | 0.548 | 0.484 | 0.442 | 0.394 | 0.391 | 0.396 | 0.394 | 0.423 | 0.508 | 0.61 | 0.604 | 0.69 | 0.713 | 0.729 | 0.714 | 0.596 | 0.603 | 0.706 | 0.759 | 0.867 | 0.909 | 0.805 | 0.759 | 0.575
Voorbeeld industrie | -168 | 0.052 | 0.052 | 0.052 | 0.052 | 0.051 | 0.075 | 0.187 | 0.57 | 0.911 | 0.957 | 0.955 | 0.89 | 0.857 | 0.912 | 0.945 | 0.916 | 0.581 | 0.388 | 0.374 | 0.374 | 0.398 | 0.254 | 0.146 | 0.132 | 0.13 | 0.141 | 0.082 | 0.063 | 0.055 | 0.07 | 0.276 | 0.608 | 0.909 | 0.893 | 0.933 | 0.941 | 0.884 | 0.898 | 0.921 | 1 | 0.746 | 0.516 | 0.393 | 0.456 | 0.467 | 0.306 | 0.16 | 0.146 | 0.139 | 0.147 | 0.063 | 0.053 | 0.052 | 0.078 | 0.223 | 0.455 | 0.731 | 0.839 | 0.842 | 0.804 | 0.82 | 0.945 | 0.958 | 0.943 | 0.752 | 0.486 | 0.398 | 0.387 | 0.372 | 0.332 | 0.208 | 0.163 | 0.162 | 0.153 | 0.085 | 0.079 | 0.086 | 0.111 | 0.286 | 0.618 | 0.884 | 0.814 | 0.921 | 0.892 | 0.898 | 0.924 | 0.908 | 0.896 | 0.48 | 0.352 | 0.295 | 0.307 | 0.289 | 0.281 | 0.116 | 0.095 | 0.093 | 0.071 | 0.072 | 0.072 | 0.07 | 0.088 | 0.261 | 0.536 | 0.591 | 0.649 | 0.59 | 0.618 | 0.633 | 0.592 | 0.599 | 0.576 | 0.239 | 0.131 | 0.112 | 0.099 | 0.103 | 0.112 | 0.093 | 0.088 | 0.086 | 0.087 | 0.085 | 0.084 | 0.087 | 0.084 | 0.085 | 0.068 | 0.069 | 0.072 | 0.079 | 0.08 | 0.078 | 0.076 | 0.077 | 0.076 | 0.075 | 0.071 | 0.069 | 0.068 | 0.078 | 0.08 | 0.079 | 0.078 | 0.05 | 0.051 | 0.051 | 0.05 | 0.05 | 0.052 | 0.051 | 0.038 | 0.036 | 0.031 | 0.035 | 0.034 | 0.051 | 0.066 | 0.032 | 0.052 | 0.043 | 0.036 | 0.034 | 0.034 | 0.04 | 0.05 | 0.052 | 0.049
Voorbeeld winkel | -168 | 0.024 | 0.024 | 0.024 | 0.166 | 0.327 | 0.327 | 0.551 | 0.889 | 0.839 | 0.853 | 0.894 | 0.736 | 0.745 | 0.516 | 0.303 | 0.314 | 0.33 | 0.303 | 0.364 | 0.427 | 0.444 | 0.319 | 0.034 | 0.024 | 0.024 | 0.024 | 0.024 | 0.244 | 0.327 | 0.327 | 0.687 | 0.889 | 0.855 | 0.89 | 0.895 | 0.878 | 0.913 | 0.756 | 0.907 | 0.913 | 0.911 | 0.933 | 0.944 | 0.901 | 0.835 | 0.502 | 0.034 | 0.024 | 0.024 | 0.024 | 0.024 | 0.183 | 0.327 | 0.327 | 0.443 | 0.9 | 0.867 | 0.908 | 0.908 | 0.966 | 0.907 | 0.788 | 0.766 | 0.756 | 0.784 | 0.772 | 0.818 | 0.745 | 0.746 | 0.474 | 0.034 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.227 | 0.327 | 0.327 | 0.708 | 0.875 | 1 | 0.85 | 0.758 | 0.759 | 0.752 | 0.791 | 0.788 | 0.788 | 0.789 | 0.816 | 0.875 | 0.939 | 0.484 | 0.037 | 0.024 | 0.024 | 0.024 | 0.026 | 0.024 | 0.275 | 0.319 | 0.474 | 0.888 | 0.855 | 0.877 | 0.928 | 0.884 | 0.888 | 0.889 | 0.957 | 0.893 | 0.875 | 0.926 | 0.919 | 0.697 | 0.414 | 0.321 | 0.042 | 0.027 | 0.024 | 0.024 | 0.043 | 0.25 | 0.457 | 0.47 | 0.452 | 0.628 | 0.941 | 0.882 | 0.886 | 0.883 | 0.912 | 0.906 | 0.919 | 0.908 | 0.924 | 0.922 | 0.884 | 0.89 | 0.529 | 0.32 | 0.039 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024 | 0.024
Voorbeeld school | -168 | 0.279 | 0.281 | 0.264 | 0.267 | 0.266 | 0.259 | 0.302 | 0.365 | 0.743 | 0.942 | 0.953 | 0.938 | 0.927 | 0.818 | 0.93 | 0.787 | 0.562 | 0.424 | 0.309 | 0.364 | 0.396 | 0.413 | 0.387 | 0.3 | 0.27 | 0.276 | 0.268 | 0.258 | 0.252 | 0.249 | 0.275 | 0.38 | 0.801 | 0.947 | 0.918 | 0.945 | 0.848 | 0.826 | 0.853 | 0.753 | 0.637 | 0.53 | 0.453 | 0.495 | 0.47 | 0.447 | 0.478 | 0.315 | 0.279 | 0.257 | 0.242 | 0.251 | 0.246 | 0.254 | 0.268 | 0.329 | 0.753 | 0.873 | 0.915 | 0.852 | 0.868 | 0.746 | 0.759 | 0.696 | 0.528 | 0.452 | 0.369 | 0.39 | 0.403 | 0.368 | 0.346 | 0.318 | 0.255 | 0.261 | 0.248 | 0.243 | 0.249 | 0.247 | 0.284 | 0.336 | 0.765 | 0.96 | 1 | 0.893 | 0.954 | 0.822 | 0.88 | 0.774 | 0.525 | 0.424 | 0.387 | 0.51 | 0.432 | 0.407 | 0.365 | 0.344 | 0.256 | 0.279 | 0.258 | 0.236 | 0.249 | 0.249 | 0.277 | 0.371 | 0.753 | 0.874 | 0.896 | 0.851 | 0.89 | 0.75 | 0.815 | 0.675 | 0.489 | 0.406 | 0.372 | 0.536 | 0.516 | 0.51 | 0.548 | 0.449 | 0.281 | 0.303 | 0.266 | 0.256 | 0.249 | 0.245 | 0.255 | 0.254 | 0.281 | 0.298 | 0.307 | 0.306 | 0.309 | 0.296 | 0.302 | 0.265 | 0.272 | 0.277 | 0.303 | 0.371 | 0.352 | 0.354 | 0.346 | 0.304 | 0.295 | 0.288 | 0.285 | 0.278 | 0.265 | 0.266 | 0.272 | 0.259 | 0.282 | 0.307 | 0.311 | 0.284 | 0.289 | 0.338 | 0.328 | 0.265 | 0.279 | 0.29 | 0.356 | 0.394 | 0.42 | 0.374 | 0.352 | 0.304
Voorbeeld min-max-belasting | 16 | 0.25 | 0.25 | 1 | 1 | 0.25 | 0.25 | 1 | 1 | 0.25 | 0.25 | 1 | 1 | 0.25 | 0.25 | 1 | 1
Voorbeeld min-max-opwekking | 16 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
Voorbeeld uren van een dag | -24 | 0.56 | 0.41 | 0.4 | 0.37 | 0.35 | 0.34 | 0.41 | 0.56 | 0.53 | 0.48 | 0.5 | 0.52 | 0.56 | 0.58 | 0.55 | 0.56 | 0.59 | 0.8 | 1 | 0.97 | 0.96 | 0.9 | 0.74 | 0.71
Voorbeeld halfuren van een dag | -48 | 0.56 | 0.5 | 0.41 | 0.4 | 0.39 | 0.38 | 0.37 | 0.36 | 0.35 | 0.34 | 0.33 | 0.38 | 0.41 | 0.5 | 0.56 | 0.55 | 0.53 | 0.51 | 0.48 | 0.49 | 0.5 | 0.51 | 0.52 | 0.54 | 0.56 | 0.57 | 0.58 | 0.56 | 0.55 | 0.55 | 0.56 | 0.58 | 0.59 | 0.72 | 0.8 | 0.95 | 1 | 0.98 | 0.97 | 0.96 | 0.95 | 0.92 | 0.9 | 0.8 | 0.74 | 0.72 | 0.7 | 0.65
Voorbeeld kwartieren van dag | -96 | 0.56 | 0.53 | 0.5 | 0.44 | 0.42 | 0.41 | 0.4 | 0.39 | 0.39 | 0.38 | 0.38 | 0.37 | 0.37 | 0.36 | 0.36 | 0.35 | 0.35 | 0.34 | 0.34 | 0.33 | 0.32 | 0.35 | 0.38 | 0.39 | 0.41 | 0.45 | 0.5 | 0.53 | 0.56 | 0.56 | 0.55 | 0.54 | 0.53 | 0.52 | 0.51 | 0.5 | 0.48 | 0.48 | 0.49 | 0.49 | 0.5 | 0.5 | 0.51 | 0.51 | 0.52 | 0.53 | 0.54 | 0.55 | 0.56 | 0.56 | 0.57 | 0.57 | 0.58 | 0.57 | 0.56 | 0.55 | 0.55 | 0.55 | 0.54 | 0.55 | 0.56 | 0.57 | 0.58 | 0.59 | 0.6 | 0.65 | 0.72 | 0.77 | 0.8 | 0.86 | 0.95 | 0.98 | 1 | 0.99 | 0.98 | 0.97 | 0.97 | 0.96 | 0.96 | 0.95 | 0.94 | 0.93 | 0.92 | 0.91 | 0.9 | 0.86 | 0.8 | 0.77 | 0.74 | 0.73 | 0.72 | 0.71 | 0.7 | 0.68 | 0.65 | 0.61
Voorbeeld vijf minuten van een dag | -289 | 0.56 | 0.55 | 0.54 | 0.53 | 0.52 | 0.51 | 0.5 | 0.48 | 0.46 | 0.44 | 0.43 | 0.42 | 0.42 | 0.42 | 0.41 | 0.41 | 0.41 | 0.41 | 0.4 | 0.4 | 0.4 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.39 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.38 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.36 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.33 | 0.33 | 0.33 | 0.32 | 0.33 | 0.34 | 0.35 | 0.36 | 0.37 | 0.38 | 0.38 | 0.39 | 0.39 | 0.4 | 0.41 | 0.41 | 0.42 | 0.43 | 0.45 | 0.47 | 0.48 | 0.5 | 0.51 | 0.52 | 0.53 | 0.54 | 0.55 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.55 | 0.55 | 0.55 | 0.54 | 0.54 | 0.54 | 0.53 | 0.53 | 0.53 | 0.52 | 0.52 | 0.52 | 0.51 | 0.51 | 0.51 | 0.5 | 0.5 | 0.5 | 0.49 | 0.48 | 0.48 | 0.48 | 0.48 | 0.48 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.52 | 0.52 | 0.52 | 0.53 | 0.53 | 0.53 | 0.54 | 0.54 | 0.54 | 0.55 | 0.55 | 0.55 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.58 | 0.59 | 0.58 | 0.57 | 0.57 | 0.57 | 0.56 | 0.56 | 0.56 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.55 | 0.54 | 0.54 | 0.54 | 0.55 | 0.55 | 0.55 | 0.56 | 0.56 | 0.56 | 0.57 | 0.57 | 0.57 | 0.58 | 0.58 | 0.58 | 0.59 | 0.59 | 0.59 | 0.6 | 0.61 | 0.63 | 0.65 | 0.67 | 0.69 | 0.72 | 0.73 | 0.75 | 0.77 | 0.78 | 0.79 | 0.8 | 0.82 | 0.84 | 0.86 | 0.88 | 0.91 | 0.95 | 0.96 | 0.97 | 0.98 | 0.99 | 0.99 | 1 | 1 | 1 | 0.99 | 0.99 | 0.99 | 0.98 | 0.98 | 0.98 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.97 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.96 | 0.95 | 0.95 | 0.95 | 0.94 | 0.94 | 0.94 | 0.93 | 0.93 | 0.93 | 0.92 | 0.92 | 0.92 | 0.91 | 0.91 | 0.91 | 0.9 | 0.89 | 0.87 | 0.86 | 0.84 | 0.82 | 0.8 | 0.79 | 0.78 | 0.77 | 0.76 | 0.75 | 0.74 | 0.74 | 0.73 | 0.73 | 0.73 | 0.72 | 0.72 | 0.72 | 0.71 | 0.71 | 0.71 | 0.7 | 0.7 | 0.7 | 0.69 | 0.68 | 0.67 | 0.66 | 0.65 | 0.64 | 0.63 | 0.61 | 0.61 | 0.6
Voorbeeld uren van dagsoort | -72 | 0.47 | 0.41 | 0.38 | 0.36 | 0.37 | 0.39 | 0.54 | 0.79 | 0.8 | 0.66 | 0.58 | 0.54 | 0.51 | 0.5 | 0.49 | 0.54 | 0.58 | 0.76 | 0.67 | 0.61 | 0.58 | 0.68 | 0.69 | 0.68 | 0.62 | 0.5 | 0.44 | 0.42 | 0.41 | 0.43 | 0.49 | 0.74 | 0.93 | 0.79 | 0.71 | 0.68 | 0.65 | 0.64 | 0.58 | 0.54 | 0.6 | 0.84 | 1 | 0.85 | 0.74 | 0.76 | 0.7 | 0.71 | 0.53 | 0.47 | 0.41 | 0.38 | 0.36 | 0.37 | 0.43 | 0.62 | 0.64 | 0.59 | 0.57 | 0.59 | 0.66 | 0.58 | 0.51 | 0.54 | 0.59 | 0.77 | 0.74 | 0.56 | 0.64 | 0.69 | 0.69 | 0.67
Laadpaal | -288 | 0.242 | 0.217 | 0.193 | 0.173 | 0.153 | 0.133 | 0.117 | 0.105 | 0.095 | 0.084 | 0.073 | 0.066 | 0.06 | 0.055 | 0.052 | 0.051 | 0.053 | 0.062 | 0.074 | 0.09 | 0.121 | 0.163 | 0.212 | 0.276 | 0.347 | 0.436 | 0.52 | 0.602 | 0.645 | 0.702 | 0.737 | 0.77 | 0.77 | 0.762 | 0.745 | 0.725 | 0.704 | 0.672 | 0.633 | 0.612 | 0.581 | 0.564 | 0.544 | 0.543 | 0.543 | 0.547 | 0.544 | 0.551 | 0.548 | 0.55 | 0.54 | 0.549 | 0.546 | 0.541 | 0.539 | 0.543 | 0.542 | 0.546 | 0.563 | 0.581 | 0.605 | 0.651 | 0.697 | 0.748 | 0.802 | 0.857 | 0.898 | 0.927 | 0.946 | 0.96 | 0.947 | 0.933 | 0.91 | 0.886 | 0.858 | 0.826 | 0.792 | 0.756 | 0.726 | 0.688 | 0.657 | 0.625 | 0.597 | 0.576 | 0.559 | 0.541 | 0.515 | 0.495 | 0.479 | 0.452 | 0.424 | 0.394 | 0.36 | 0.331 | 0.301 | 0.339 | 0.312 | 0.291 | 0.268 | 0.247 | 0.233 | 0.209 | 0.193 | 0.174 | 0.156 | 0.145 | 0.134 | 0.117 | 0.115 | 0.104 | 0.088 | 0.086 | 0.083 | 0.074 | 0.075 | 0.075 | 0.079 | 0.082 | 0.086 | 0.1 | 0.121 | 0.146 | 0.195 | 0.213 | 0.259 | 0.306 | 0.344 | 0.38 | 0.406 | 0.463 | 0.52 | 0.56 | 0.583 | 0.645 | 0.652 | 0.706 | 0.725 | 0.73 | 0.758 | 0.765 | 0.779 | 0.797 | 0.812 | 0.825 | 0.828 | 0.833 | 0.85 | 0.837 | 0.842 | 0.83 | 0.827 | 0.804 | 0.814 | 0.798 | 0.802 | 0.799 | 0.81 | 0.808 | 0.816 | 0.827 | 0.844 | 0.863 | 0.858 | 0.852 | 0.845 | 0.842 | 0.803 | 0.785 | 0.763 | 0.726 | 0.679 | 0.655 | 0.633 | 0.614 | 0.594 | 0.576 | 0.541 | 0.54 | 0.514 | 0.499 | 0.489 | 0.481 | 0.475 | 0.463 | 0.445 | 0.455 | 0.449 | 0.423 | 0.409 | 0.383 | 0.362 | 0.229 | 0.206 | 0.184 | 0.172 | 0.157 | 0.145 | 0.144 | 0.145 | 0.134 | 0.126 | 0.121 | 0.112 | 0.105 | 0.101 | 0.1 | 0.089 | 0.081 | 0.079 | 0.078 | 0.08 | 0.086 | 0.088 | 0.088 | 0.101 | 0.118 | 0.136 | 0.159 | 0.161 | 0.237 | 0.254 | 0.337 | 0.453 | 0.517 | 0.593 | 0.673 | 0.72 | 0.815 | 0.839 | 0.894 | 0.945 | 0.941 | 0.936 | 0.945 | 0.96 | 0.951 | 0.98 | 0.999 | 1.013 | 1.012 | 0.999 | 0.991 | 0.969 | 0.965 | 0.947 | 0.933 | 0.918 | 0.905 | 0.887 | 0.886 | 0.882 | 0.866 | 0.878 | 0.879 | 0.865 | 0.86 | 0.866 | 0.869 | 0.873 | 0.86 | 0.838 | 0.802 | 0.788 | 0.788 | 0.77 | 0.73 | 0.707 | 0.699 | 0.669 | 0.658 | 0.641 | 0.631 | 0.619 | 0.589 | 0.589 | 0.566 | 0.558 | 0.531 | 0.499 | 0.467 | 0.443 | 0.407 | 0.378 | 0.345 | 0.311 | 0.279 | 0.254 | 0.272
E1A | -3456 | 0.455 | 0.428 | 0.403 | 0.38 | 0.36 | 0.344 | 0.33 | 0.319 | 0.311 | 0.302 | 0.294 | 0.287 | 0.283 | 0.281 | 0.279 | 0.279 | 0.277 | 0.276 | 0.275 | 0.277 | 0.282 | 0.288 | 0.297 | 0.312 | 0.33 | 0.351 | 0.374 | 0.4 | 0.427 | 0.454 | 0.477 | 0.494 | 0.505 | 0.513 | 0.517 | 0.522 | 0.526 | 0.53 | 0.529 | 0.526 | 0.52 | 0.511 | 0.501 | 0.493 | 0.487 | 0.484 | 0.486 | 0.49 | 0.494 | 0.493 | 0.486 | 0.478 | 0.473 | 0.47 | 0.47 | 0.47 | 0.471 | 0.474 | 0.479 | 0.486 | 0.491 | 0.497 | 0.506 | 0.519 | 0.537 | 0.564 | 0.607 | 0.671 | 0.747 | 0.822 | 0.875 | 0.897 | 0.898 | 0.885 | 0.872 | 0.855 | 0.84 | 0.825 | 0.815 | 0.802 | 0.785 | 0.763 | 0.741 | 0.724 | 0.712 | 0.701 | 0.688 | 0.67 | 0.652 | 0.632 | 0.611 | 0.592 | 0.571 | 0.55 | 0.522 | 0.494 | 0.487 | 0.466 | 0.443 | 0.418 | 0.393 | 0.37 | 0.351 | 0.336 | 0.326 | 0.315 | 0.304 | 0.295 | 0.29 | 0.288 | 0.284 | 0.283 | 0.282 | 0.282 | 0.281 | 0.281 | 0.283 | 0.287 | 0.29 | 0.294 | 0.299 | 0.305 | 0.314 | 0.325 | 0.343 | 0.366 | 0.394 | 0.42 | 0.448 | 0.48 | 0.513 | 0.545 | 0.574 | 0.601 | 0.62 | 0.627 | 0.627 | 0.626 | 0.631 | 0.638 | 0.641 | 0.643 | 0.644 | 0.649 | 0.655 | 0.657 | 0.655 | 0.649 | 0.638 | 0.627 | 0.62 | 0.615 | 0.613 | 0.61 | 0.609 | 0.608 | 0.607 | 0.61 | 0.614 | 0.621 | 0.629 | 0.646 | 0.676 | 0.725 | 0.79 | 0.853 | 0.902 | 0.92 | 0.916 | 0.898 | 0.877 | 0.857 | 0.835 | 0.816 | 0.803 | 0.791 | 0.778 | 0.756 | 0.732 | 0.705 | 0.686 | 0.672 | 0.661 | 0.648 | 0.635 | 0.625 | 0.614 | 0.597 | 0.576 | 0.554 | 0.532 | 0.524 | 0.479 | 0.456 | 0.43 | 0.408 | 0.388 | 0.371 | 0.354 | 0.338 | 0.326 | 0.317 | 0.308 | 0.3 | 0.294 | 0.29 | 0.285 | 0.282 | 0.278 | 0.277 | 0.276 | 0.276 | 0.277 | 0.279 | 0.282 | 0.287 | 0.292 | 0.298 | 0.303 | 0.31 | 0.319 | 0.334 | 0.351 | 0.374 | 0.399 | 0.432 | 0.467 | 0.501 | 0.532 | 0.555 | 0.576 | 0.593 | 0.61 | 0.62 | 0.628 | 0.63 | 0.632 | 0.633 | 0.639 | 0.643 | 0.652 | 0.66 | 0.668 | 0.669 | 0.66 | 0.651 | 0.642 | 0.638 | 0.631 | 0.629 | 0.627 | 0.626 | 0.619 | 0.614 | 0.612 | 0.617 | 0.627 | 0.647 | 0.682 | 0.732 | 0.799 | 0.873 | 0.937 | 0.964 | 0.959 | 0.937 | 0.917 | 0.896 | 0.881 | 0.868 | 0.863 | 0.85 | 0.838 | 0.815 | 0.792 | 0.762 | 0.739 | 0.722 | 0.708 | 0.69 | 0.666 | 0.641 | 0.611 | 0.583 | 0.553 | 0.523 | 0.491 | 0.46 | 0.449 | 0.422 | 0.399 | 0.378 | 0.36 | 0.344 | 0.332 | 0.323 | 0.314 | 0.305 | 0.298 | 0.292 | 0.288 | 0.285 | 0.283 | 0.281 | 0.278 | 0.277 | 0.277 | 0.28 | 0.284 | 0.291 | 0.302 | 0.317 | 0.334 | 0.354 | 0.375 | 0.399 | 0.426 | 0.452 | 0.474 | 0.488 | 0.496 | 0.497 | 0.497 | 0.499 | 0.501 | 0.502 | 0.499 | 0.494 | 0.485 | 0.474 | 0.463 | 0.454 | 0.448 | 0.446 | 0.445 | 0.444 | 0.445 | 0.446 | 0.442 | 0.435 | 0.427 | 0.422 | 0.421 | 0.419 | 0.419 | 0.42 | 0.426 | 0.432 | 0.438 | 0.444 | 0.452 | 0.464 | 0.48 | 0.505 | 0.539 | 0.588 | 0.649 | 0.717 | 0.774 | 0.812 | 0.833 | 0.841 | 0.842 | 0.833 | 0.821 | 0.807 | 0.799 | 0.787 | 0.772 | 0.75 | 0.728 | 0.711 | 0.699 | 0.688 | 0.675 | 0.657 | 0.64 | 0.62 | 0.6 | 0.582 | 0.563 | 0.542 | 0.516 | 0.489 | 0.488 | 0.46 | 0.433 | 0.409 | 0.388 | 0.369 | 0.35 | 0.337 | 0.327 | 0.32 | 0.31 | 0.301 | 0.295 | 0.289 | 0.285 | 0.282 | 0.281 | 0.28 | 0.278 | 0.278 | 0.279 | 0.284 | 0.291 | 0.297 | 0.303 | 0.308 | 0.317 | 0.328 | 0.348 | 0.37 | 0.397 | 0.423 | 0.457 | 0.489 | 0.518 | 0.541 | 0.559 | 0.577 | 0.59 | 0.599 | 0.594 | 0.587 | 0.581 | 0.575 | 0.568 | 0.568 | 0.575 | 0.584 | 0.59 | 0.593 | 0.592 | 0.582 | 0.568 | 0.554 | 0.545 | 0.543 | 0.547 | 0.547 | 0.545 | 0.541 | 0.539 | 0.536 | 0.538 | 0.543 | 0.552 | 0.567 | 0.59 | 0.623 | 0.672 | 0.73 | 0.792 | 0.831 | 0.849 | 0.85 | 0.846 | 0.838 | 0.823 | 0.808 | 0.795 | 0.778 | 0.761 | 0.738 | 0.715 | 0.689 | 0.668 | 0.654 | 0.646 | 0.636 | 0.622 | 0.607 | 0.59 | 0.576 | 0.558 | 0.543 | 0.522 | 0.501 | 0.477 | 0.453 | 0.43 | 0.406 | 0.387 | 0.368 | 0.352 | 0.339 | 0.328 | 0.319 | 0.31 | 0.302 | 0.295 | 0.29 | 0.284 | 0.282 | 0.279 | 0.278 | 0.275 | 0.275 | 0.276 | 0.278 | 0.282 | 0.288 | 0.294 | 0.3 | 0.306 | 0.315 | 0.326 | 0.343 | 0.361 | 0.387 | 0.414 | 0.444 | 0.475 | 0.505 | 0.529 | 0.542 | 0.552 | 0.568 | 0.585 | 0.6 | 0.602 | 0.597 | 0.594 | 0.592 | 0.596 | 0.602 | 0.612 | 0.617 | 0.614 | 0.61 | 0.6 | 0.592 | 0.587 | 0.581 | 0.574 | 0.569 | 0.57 | 0.569 | 0.566 | 0.561 | 0.562 | 0.564 | 0.57 | 0.582 | 0.608 | 0.649 | 0.703 | 0.767 | 0.823 | 0.862 | 0.878 | 0.885 | 0.881 | 0.869 | 0.855 | 0.843 | 0.839 | 0.828 | 0.814 | 0.787 | 0.763 | 0.738 | 0.718 | 0.701 | 0.684 | 0.666 | 0.647 | 0.624 | 0.599 | 0.571 | 0.541 | 0.511 | 0.481 | 0.451 | 0.436 | 0.411 | 0.388 | 0.368 | 0.351 | 0.335 | 0.322 | 0.312 | 0.303 | 0.294 | 0.285 | 0.279 | 0.274 | 0.272 | 0.269 | 0.268 | 0.267 | 0.267 | 0.268 | 0.27 | 0.274 | 0.281 | 0.29 | 0.303 | 0.32 | 0.338 | 0.357 | 0.378 | 0.4 | 0.421 | 0.439 | 0.45 | 0.455 | 0.455 | 0.455 | 0.456 | 0.457 | 0.456 | 0.451 | 0.443 | 0.434 | 0.424 | 0.415 | 0.406 | 0.398 | 0.394 | 0.393 | 0.394 | 0.396 | 0.395 | 0.391 | 0.383 | 0.376 | 0.373 | 0.37 | 0.369 | 0.369 | 0.371 | 0.376 | 0.38 | 0.385 | 0.389 | 0.396 | 0.406 | 0.42 | 0.443 | 0.479 | 0.528 | 0.585 | 0.641 | 0.688 | 0.717 | 0.733 | 0.739 | 0.746 | 0.753 | 0.758 | 0.759 | 0.76 | 0.755 | 0.744 | 0.727 | 0.709 | 0.695 | 0.683 | 0.672 | 0.659 | 0.643 | 0.625 | 0.604 | 0.582 | 0.562 | 0.542 | 0.521 | 0.496 | 0.47 | 0.474 | 0.45 | 0.425 | 0.401 | 0.38 | 0.362 | 0.346 | 0.334 | 0.321 | 0.309 | 0.298 | 0.29 | 0.285 | 0.281 | 0.277 | 0.275 | 0.272 | 0.271 | 0.27 | 0.271 | 0.273 | 0.275 | 0.28 | 0.287 | 0.295 | 0.302 | 0.311 | 0.324 | 0.343 | 0.364 | 0.388 | 0.411 | 0.435 | 0.46 | 0.483 | 0.501 | 0.515 | 0.528 | 0.537 | 0.538 | 0.537 | 0.536 | 0.531 | 0.521 | 0.513 | 0.511 | 0.517 | 0.522 | 0.529 | 0.53 | 0.527 | 0.517 | 0.51 | 0.504 | 0.502 | 0.502 | 0.502 | 0.503 | 0.503 | 0.503 | 0.504 | 0.504 | 0.505 | 0.507 | 0.514 | 0.525 | 0.548 | 0.583 | 0.635 | 0.69 | 0.743 | 0.772 | 0.788 | 0.792 | 0.798 | 0.799 | 0.798 | 0.794 | 0.791 | 0.778 | 0.762 | 0.738 | 0.713 | 0.685 | 0.665 | 0.652 | 0.64 | 0.624 | 0.609 | 0.596 | 0.582 | 0.564 | 0.545 | 0.524 | 0.504 | 0.48 | 0.455 | 0.43 | 0.407 | 0.389 | 0.373 | 0.36 | 0.344 | 0.335 | 0.323 | 0.313 | 0.301 | 0.299 | 0.29 | 0.285 | 0.28 | 0.276 | 0.272 | 0.27 | 0.269 | 0.269 | 0.268 | 0.269 | 0.272 | 0.279 | 0.284 | 0.289 | 0.295 | 0.305 | 0.316 | 0.33 | 0.347 | 0.368 | 0.392 | 0.418 | 0.444 | 0.466 | 0.482 | 0.497 | 0.512 | 0.528 | 0.538 | 0.55 | 0.554 | 0.557 | 0.555 | 0.55 | 0.549 | 0.554 | 0.563 | 0.571 | 0.572 | 0.569 | 0.563 | 0.553 | 0.543 | 0.529 | 0.519 | 0.514 | 0.514 | 0.517 | 0.518 | 0.516 | 0.513 | 0.512 | 0.516 | 0.529 | 0.55 | 0.584 | 0.631 | 0.69 | 0.744 | 0.778 | 0.79 | 0.791 | 0.796 | 0.797 | 0.796 | 0.795 | 0.8 | 0.796 | 0.789 | 0.77 | 0.749 | 0.723 | 0.706 | 0.694 | 0.685 | 0.669 | 0.651 | 0.628 | 0.601 | 0.57 | 0.539 | 0.51 | 0.482 | 0.453 | 0.411 | 0.387 | 0.367 | 0.349 | 0.333 | 0.318 | 0.307 | 0.296 | 0.288 | 0.279 | 0.271 | 0.264 | 0.259 | 0.256 | 0.253 | 0.251 | 0.25 | 0.25 | 0.25 | 0.252 | 0.256 | 0.26 | 0.267 | 0.277 | 0.29 | 0.304 | 0.318 | 0.333 | 0.35 | 0.367 | 0.384 | 0.396 | 0.405 | 0.41 | 0.414 | 0.416 | 0.416 | 0.414 | 0.409 | 0.4 | 0.389 | 0.376 | 0.366 | 0.358 | 0.351 | 0.345 | 0.34 | 0.341 | 0.341 | 0.339 | 0.332 | 0.323 | 0.312 | 0.304 | 0.298 | 0.296 | 0.295 | 0.294 | 0.296 | 0.298 | 0.3 | 0.301 | 0.305 | 0.313 | 0.325 | 0.345 | 0.375 | 0.419 | 0.473 | 0.529 | 0.574 | 0.599 | 0.607 | 0.606 | 0.603 | 0.598 | 0.595 | 0.593 | 0.596 | 0.6 | 0.603 | 0.605 | 0.607 | 0.613 | 0.618 | 0.621 | 0.616 | 0.604 | 0.588 | 0.572 | 0.553 | 0.536 | 0.519 | 0.499 | 0.475 | 0.446 | 0.442 | 0.417 | 0.393 | 0.372 | 0.356 | 0.339 | 0.324 | 0.309 | 0.299 | 0.291 | 0.283 | 0.276 | 0.27 | 0.263 | 0.259 | 0.255 | 0.254 | 0.253 | 0.253 | 0.255 | 0.257 | 0.261 | 0.265 | 0.271 | 0.275 | 0.278 | 0.283 | 0.29 | 0.304 | 0.321 | 0.344 | 0.367 | 0.39 | 0.411 | 0.434 | 0.451 | 0.464 | 0.474 | 0.478 | 0.478 | 0.473 | 0.469 | 0.463 | 0.457 | 0.452 | 0.449 | 0.45 | 0.455 | 0.458 | 0.454 | 0.444 | 0.432 | 0.421 | 0.414 | 0.406 | 0.399 | 0.392 | 0.388 | 0.383 | 0.378 | 0.375 | 0.377 | 0.381 | 0.384 | 0.387 | 0.396 | 0.414 | 0.444 | 0.485 | 0.535 | 0.58 | 0.611 | 0.624 | 0.625 | 0.62 | 0.616 | 0.611 | 0.61 | 0.609 | 0.608 | 0.613 | 0.616 | 0.619 | 0.617 | 0.614 | 0.612 | 0.607 | 0.599 | 0.588 | 0.574 | 0.558 | 0.54 | 0.524 | 0.506 | 0.484 | 0.458 | 0.432 | 0.41 | 0.39 | 0.37 | 0.351 | 0.335 | 0.32 | 0.307 | 0.293 | 0.284 | 0.277 | 0.272 | 0.269 | 0.265 | 0.26 | 0.256 | 0.253 | 0.252 | 0.25 | 0.251 | 0.25 | 0.251 | 0.253 | 0.256 | 0.259 | 0.262 | 0.265 | 0.274 | 0.284 | 0.3 | 0.317 | 0.337 | 0.359 | 0.383 | 0.408 | 0.426 | 0.442 | 0.456 | 0.468 | 0.476 | 0.479 | 0.48 | 0.48 | 0.474 | 0.465 | 0.459 | 0.458 | 0.46 | 0.461 | 0.461 | 0.458 | 0.449 | 0.441 | 0.428 | 0.415 | 0.4 | 0.388 | 0.381 | 0.376 | 0.375 | 0.373 | 0.373 | 0.372 | 0.371 | 0.376 | 0.387 | 0.412 | 0.447 | 0.497 | 0.551 | 0.601 | 0.632 | 0.644 | 0.643 | 0.635 | 0.625 | 0.621 | 0.624 | 0.633 | 0.637 | 0.644 | 0.647 | 0.648 | 0.644 | 0.64 | 0.633 | 0.623 | 0.609 | 0.591 | 0.57 | 0.549 | 0.529 | 0.504 | 0.475 | 0.446 | 0.422 | 0.412 | 0.387 | 0.367 | 0.348 | 0.331 | 0.315 | 0.304 | 0.295 | 0.286 | 0.278 | 0.271 | 0.265 | 0.259 | 0.256 | 0.253 | 0.251 | 0.249 | 0.248 | 0.249 | 0.251 | 0.253 | 0.256 | 0.261 | 0.268 | 0.276 | 0.285 | 0.295 | 0.306 | 0.32 | 0.335 | 0.351 | 0.362 | 0.368 | 0.371 | 0.374 | 0.376 | 0.376 | 0.374 | 0.368 | 0.36 | 0.349 | 0.338 | 0.327 | 0.318 | 0.311 | 0.308 | 0.307 | 0.308 | 0.307 | 0.305 | 0.299 | 0.291 | 0.284 | 0.278 | 0.273 | 0.269 | 0.267 | 0.265 | 0.266 | 0.268 | 0.27 | 0.273 | 0.278 | 0.287 | 0.299 | 0.318 | 0.347 | 0.389 | 0.44 | 0.494 | 0.536 | 0.559 | 0.568 | 0.567 | 0.563 | 0.555 | 0.55 | 0.548 | 0.553 | 0.557 | 0.557 | 0.549 | 0.541 | 0.54 | 0.545 | 0.553 | 0.559 | 0.561 | 0.561 | 0.552 | 0.54 | 0.527 | 0.513 | 0.496 | 0.473 | 0.443 | 0.419 | 0.398 | 0.387 | 0.367 | 0.35 | 0.336 | 0.324 | 0.311 | 0.299 | 0.289 | 0.279 | 0.271 | 0.266 | 0.263 | 0.258 | 0.254 | 0.251 | 0.25 | 0.248 | 0.249 | 0.251 | 0.255 | 0.257 | 0.259 | 0.261 | 0.262 | 0.267 | 0.272 | 0.282 | 0.293 | 0.31 | 0.328 | 0.349 | 0.368 | 0.381 | 0.394 | 0.404 | 0.418 | 0.427 | 0.43 | 0.426 | 0.415 | 0.401 | 0.393 | 0.393 | 0.397 | 0.399 | 0.4 | 0.4 | 0.403 | 0.399 | 0.391 | 0.377 | 0.363 | 0.354 | 0.348 | 0.344 | 0.34 | 0.335 | 0.333 | 0.329 | 0.327 | 0.327 | 0.333 | 0.341 | 0.354 | 0.372 | 0.402 | 0.441 | 0.486 | 0.525 | 0.551 | 0.566 | 0.568 | 0.57 | 0.564 | 0.558 | 0.554 | 0.557 | 0.561 | 0.557 | 0.547 | 0.537 | 0.531 | 0.533 | 0.539 | 0.549 | 0.555 | 0.556 | 0.549 | 0.537 | 0.527 | 0.518 | 0.509 | 0.489 | 0.463 | 0.434 | 0.411 | 0.39 | 0.37 | 0.352 | 0.338 | 0.325 | 0.313 | 0.301 | 0.293 | 0.287 | 0.278 | 0.272 | 0.264 | 0.259 | 0.256 | 0.253 | 0.25 | 0.246 | 0.246 | 0.246 | 0.245 | 0.244 | 0.244 | 0.247 | 0.251 | 0.255 | 0.259 | 0.263 | 0.271 | 0.283 | 0.299 | 0.318 | 0.341 | 0.365 | 0.384 | 0.397 | 0.407 | 0.417 | 0.427 | 0.432 | 0.432 | 0.427 | 0.42 | 0.418 | 0.419 | 0.42 | 0.418 | 0.417 | 0.419 | 0.415 | 0.405 | 0.391 | 0.381 | 0.373 | 0.369 | 0.365 | 0.362 | 0.361 | 0.36 | 0.358 | 0.354 | 0.354 | 0.358 | 0.363 | 0.376 | 0.396 | 0.428 | 0.467 | 0.517 | 0.561 | 0.593 | 0.604 | 0.604 | 0.603 | 0.603 | 0.598 | 0.594 | 0.593 | 0.596 | 0.598 | 0.591 | 0.58 | 0.566 | 0.562 | 0.566 | 0.572 | 0.573 | 0.567 | 0.554 | 0.536 | 0.517 | 0.497 | 0.474 | 0.448 | 0.421 | 0.417 | 0.392 | 0.37 | 0.351 | 0.335 | 0.321 | 0.308 | 0.296 | 0.286 | 0.278 | 0.272 | 0.266 | 0.262 | 0.259 | 0.256 | 0.253 | 0.25 | 0.249 | 0.248 | 0.249 | 0.25 | 0.251 | 0.255 | 0.258 | 0.265 | 0.273 | 0.283 | 0.294 | 0.307 | 0.32 | 0.333 | 0.343 | 0.349 | 0.353 | 0.354 | 0.357 | 0.356 | 0.353 | 0.347 | 0.339 | 0.33 | 0.319 | 0.307 | 0.299 | 0.292 | 0.288 | 0.286 | 0.289 | 0.292 | 0.292 | 0.287 | 0.279 | 0.271 | 0.265 | 0.261 | 0.259 | 0.257 | 0.257 | 0.259 | 0.261 | 0.263 | 0.266 | 0.271 | 0.279 | 0.29 | 0.307 | 0.333 | 0.37 | 0.416 | 0.465 | 0.505 | 0.527 | 0.534 | 0.534 | 0.53 | 0.524 | 0.521 | 0.518 | 0.521 | 0.523 | 0.523 | 0.518 | 0.511 | 0.506 | 0.505 | 0.506 | 0.509 | 0.513 | 0.518 | 0.521 | 0.519 | 0.517 | 0.509 | 0.497 | 0.476 | 0.449 | 0.431 | 0.407 | 0.387 | 0.368 | 0.351 | 0.333 | 0.318 | 0.305 | 0.296 | 0.288 | 0.279 | 0.27 | 0.263 | 0.258 | 0.253 | 0.25 | 0.248 | 0.248 | 0.247 | 0.247 | 0.247 | 0.248 | 0.249 | 0.25 | 0.25 | 0.249 | 0.251 | 0.254 | 0.264 | 0.277 | 0.294 | 0.311 | 0.327 | 0.343 | 0.358 | 0.375 | 0.388 | 0.399 | 0.404 | 0.407 | 0.407 | 0.405 | 0.395 | 0.392 | 0.389 | 0.39 | 0.392 | 0.392 | 0.393 | 0.39 | 0.387 | 0.378 | 0.368 | 0.359 | 0.349 | 0.34 | 0.333 | 0.33 | 0.327 | 0.323 | 0.32 | 0.319 | 0.32 | 0.323 | 0.328 | 0.337 | 0.353 | 0.375 | 0.407 | 0.445 | 0.484 | 0.511 | 0.525 | 0.529 | 0.527 | 0.521 | 0.514 | 0.509 | 0.512 | 0.514 | 0.517 | 0.511 | 0.504 | 0.498 | 0.493 | 0.494 | 0.494 | 0.499 | 0.501 | 0.506 | 0.505 | 0.503 | 0.497 | 0.487 | 0.47 | 0.451 | 0.427 | 0.407 | 0.386 | 0.37 | 0.354 | 0.339 | 0.323 | 0.31 | 0.3 | 0.292 | 0.285 | 0.278 | 0.27 | 0.265 | 0.26 | 0.256 | 0.252 | 0.248 | 0.246 | 0.244 | 0.243 | 0.242 | 0.242 | 0.242 | 0.241 | 0.24 | 0.24 | 0.242 | 0.247 | 0.256 | 0.266 | 0.28 | 0.297 | 0.316 | 0.335 | 0.351 | 0.367 | 0.379 | 0.388 | 0.395 | 0.399 | 0.4 | 0.397 | 0.397 | 0.398 | 0.395 | 0.389 | 0.385 | 0.387 | 0.387 | 0.383 | 0.38 | 0.373 | 0.37 | 0.364 | 0.361 | 0.355 | 0.349 | 0.345 | 0.344 | 0.341 | 0.339 | 0.335 | 0.335 | 0.337 | 0.343 | 0.359 | 0.387 | 0.428 | 0.473 | 0.514 | 0.54 | 0.551 | 0.553 | 0.548 | 0.541 | 0.536 | 0.539 | 0.547 | 0.554 | 0.557 | 0.551 | 0.543 | 0.536 | 0.531 | 0.53 | 0.527 | 0.529 | 0.532 | 0.535 | 0.529 | 0.516 | 0.495 | 0.473 | 0.448 | 0.419 | 0.412 | 0.388 | 0.366 | 0.349 | 0.333 | 0.319 | 0.307 | 0.297 | 0.288 | 0.279 | 0.273 | 0.268 | 0.264 | 0.26 | 0.257 | 0.256 | 0.255 | 0.254 | 0.253 | 0.252 | 0.253 | 0.255 | 0.259 | 0.262 | 0.267 | 0.273 | 0.279 | 0.287 | 0.297 | 0.308 | 0.318 | 0.328 | 0.335 | 0.341 | 0.346 | 0.349 | 0.348 | 0.345 | 0.34 | 0.334 | 0.327 | 0.319 | 0.31 | 0.303 | 0.298 | 0.293 | 0.291 | 0.291 | 0.292 | 0.29 | 0.285 | 0.278 | 0.272 | 0.267 | 0.264 | 0.261 | 0.26 | 0.259 | 0.263 | 0.265 | 0.268 | 0.269 | 0.273 | 0.279 | 0.289 | 0.304 | 0.328 | 0.362 | 0.406 | 0.453 | 0.492 | 0.515 | 0.522 | 0.52 | 0.518 | 0.514 | 0.51 | 0.508 | 0.511 | 0.513 | 0.513 | 0.507 | 0.499 | 0.496 | 0.497 | 0.501 | 0.504 | 0.507 | 0.513 | 0.516 | 0.514 | 0.509 | 0.5 | 0.488 | 0.468 | 0.446 | 0.44 | 0.419 | 0.397 | 0.376 | 0.358 | 0.342 | 0.328 | 0.313 | 0.302 | 0.293 | 0.287 | 0.279 | 0.273 | 0.267 | 0.264 | 0.262 | 0.262 | 0.263 | 0.263 | 0.263 | 0.263 | 0.263 | 0.262 | 0.263 | 0.264 | 0.264 | 0.262 | 0.265 | 0.274 | 0.284 | 0.297 | 0.309 | 0.325 | 0.341 | 0.356 | 0.371 | 0.384 | 0.395 | 0.401 | 0.4 | 0.397 | 0.391 | 0.386 | 0.381 | 0.379 | 0.379 | 0.379 | 0.381 | 0.386 | 0.386 | 0.381 | 0.374 | 0.366 | 0.357 | 0.349 | 0.342 | 0.337 | 0.332 | 0.328 | 0.325 | 0.323 | 0.323 | 0.325 | 0.329 | 0.335 | 0.344 | 0.359 | 0.383 | 0.413 | 0.45 | 0.483 | 0.505 | 0.516 | 0.519 | 0.518 | 0.511 | 0.504 | 0.5 | 0.502 | 0.505 | 0.506 | 0.502 | 0.495 | 0.491 | 0.489 | 0.49 | 0.49 | 0.493 | 0.497 | 0.502 | 0.501 | 0.496 | 0.487 | 0.475 | 0.459 | 0.44 | 0.419 | 0.398 | 0.379 | 0.363 | 0.349 | 0.336 | 0.322 | 0.31 | 0.3 | 0.293 | 0.285 | 0.28 | 0.275 | 0.272 | 0.268 | 0.265 | 0.261 | 0.258 | 0.255 | 0.252 | 0.251 | 0.25 | 0.249 | 0.248 | 0.249 | 0.249 | 0.249 | 0.251 | 0.255 | 0.262 | 0.27 | 0.283 | 0.297 | 0.313 | 0.332 | 0.347 | 0.361 | 0.37 | 0.378 | 0.383 | 0.387 | 0.388 | 0.386 | 0.381 | 0.376 | 0.374 | 0.374 | 0.373 | 0.373 | 0.372 | 0.373 | 0.368 | 0.359 | 0.349 | 0.339 | 0.333 | 0.329 | 0.328 | 0.329 | 0.328 | 0.328 | 0.323 | 0.322 | 0.32 | 0.326 | 0.335 | 0.356 | 0.38 | 0.413 | 0.449 | 0.484 | 0.508 | 0.518 | 0.52 | 0.518 | 0.515 | 0.514 | 0.516 | 0.522 | 0.524 | 0.525 | 0.522 | 0.519 | 0.516 | 0.514 | 0.516 | 0.519 | 0.522 | 0.524 | 0.523 | 0.516 | 0.505 | 0.489 | 0.469 | 0.447 | 0.422 | 0.414 | 0.391 | 0.371 | 0.353 | 0.337 | 0.323 | 0.312 | 0.302 | 0.294 | 0.287 | 0.28 | 0.276 | 0.272 | 0.269 | 0.266 | 0.264 | 0.263 | 0.262 | 0.261 | 0.26 | 0.261 | 0.263 | 0.265 | 0.269 | 0.275 | 0.283 | 0.291 | 0.301 | 0.31 | 0.321 | 0.332 | 0.341 | 0.349 | 0.356 | 0.36 | 0.362 | 0.361 | 0.359 | 0.355 | 0.349 | 0.341 | 0.332 | 0.323 | 0.315 | 0.308 | 0.305 | 0.304 | 0.304 | 0.305 | 0.302 | 0.297 | 0.29 | 0.283 | 0.278 | 0.274 | 0.272 | 0.271 | 0.273 | 0.275 | 0.277 | 0.278 | 0.281 | 0.286 | 0.294 | 0.305 | 0.321 | 0.346 | 0.383 | 0.427 | 0.472 | 0.511 | 0.534 | 0.545 | 0.544 | 0.542 | 0.539 | 0.537 | 0.534 | 0.536 | 0.538 | 0.54 | 0.537 | 0.534 | 0.537 | 0.544 | 0.554 | 0.558 | 0.555 | 0.548 | 0.538 | 0.526 | 0.515 | 0.503 | 0.488 | 0.467 | 0.444 | 0.428 | 0.408 | 0.386 | 0.368 | 0.352 | 0.34 | 0.328 | 0.316 | 0.304 | 0.294 | 0.287 | 0.282 | 0.278 | 0.273 | 0.268 | 0.264 | 0.264 | 0.265 | 0.265 | 0.264 | 0.265 | 0.267 | 0.268 | 0.27 | 0.271 | 0.273 | 0.274 | 0.276 | 0.284 | 0.296 | 0.312 | 0.326 | 0.341 | 0.355 | 0.37 | 0.382 | 0.392 | 0.399 | 0.404 | 0.405 | 0.404 | 0.4 | 0.395 | 0.389 | 0.383 | 0.381 | 0.381 | 0.383 | 0.384 | 0.384 | 0.379 | 0.37 | 0.361 | 0.356 | 0.351 | 0.345 | 0.34 | 0.337 | 0.338 | 0.336 | 0.336 | 0.337 | 0.341 | 0.344 | 0.35 | 0.36 | 0.381 | 0.406 | 0.438 | 0.472 | 0.505 | 0.527 | 0.536 | 0.539 | 0.538 | 0.535 | 0.531 | 0.528 | 0.529 | 0.531 | 0.532 | 0.529 | 0.526 | 0.526 | 0.531 | 0.539 | 0.543 | 0.539 | 0.532 | 0.524 | 0.517 | 0.509 | 0.497 | 0.481 | 0.462 | 0.441 | 0.42 | 0.401 | 0.383 | 0.367 | 0.352 | 0.338 | 0.324 | 0.31 | 0.299 | 0.291 | 0.284 | 0.279 | 0.273 | 0.269 | 0.265 | 0.262 | 0.26 | 0.259 | 0.257 | 0.255 | 0.254 | 0.254 | 0.254 | 0.255 | 0.257 | 0.257 | 0.257 | 0.259 | 0.264 | 0.273 | 0.285 | 0.3 | 0.315 | 0.333 | 0.346 | 0.359 | 0.37 | 0.378 | 0.386 | 0.392 | 0.399 | 0.403 | 0.404 | 0.403 | 0.402 | 0.4 | 0.398 | 0.394 | 0.391 | 0.388 | 0.385 | 0.381 | 0.374 | 0.367 | 0.362 | 0.355 | 0.35 | 0.344 | 0.344 | 0.344 | 0.344 | 0.342 | 0.343 | 0.346 | 0.352 | 0.363 | 0.38 | 0.406 | 0.441 | 0.477 | 0.512 | 0.539 | 0.554 | 0.554 | 0.548 | 0.546 | 0.548 | 0.551 | 0.555 | 0.558 | 0.562 | 0.558 | 0.557 | 0.557 | 0.566 | 0.572 | 0.573 | 0.566 | 0.556 | 0.544 | 0.528 | 0.508 | 0.488 | 0.468 | 0.447 | 0.424 | 0.392 | 0.369 | 0.348 | 0.329 | 0.314 | 0.3 | 0.288 | 0.277 | 0.268 | 0.26 | 0.254 | 0.249 | 0.245 | 0.242 | 0.24 | 0.238 | 0.237 | 0.236 | 0.235 | 0.236 | 0.237 | 0.241 | 0.246 | 0.254 | 0.266 | 0.281 | 0.299 | 0.319 | 0.341 | 0.36 | 0.376 | 0.386 | 0.391 | 0.393 | 0.394 | 0.395 | 0.396 | 0.392 | 0.385 | 0.375 | 0.364 | 0.354 | 0.343 | 0.334 | 0.324 | 0.318 | 0.317 | 0.318 | 0.317 | 0.315 | 0.309 | 0.302 | 0.295 | 0.289 | 0.284 | 0.282 | 0.281 | 0.284 | 0.288 | 0.291 | 0.294 | 0.298 | 0.305 | 0.316 | 0.33 | 0.35 | 0.379 | 0.42 | 0.47 | 0.521 | 0.561 | 0.582 | 0.587 | 0.586 | 0.583 | 0.579 | 0.575 | 0.577 | 0.589 | 0.601 | 0.608 | 0.607 | 0.603 | 0.598 | 0.591 | 0.582 | 0.573 | 0.56 | 0.547 | 0.531 | 0.513 | 0.498 | 0.482 | 0.466 | 0.445 | 0.421 | 0.401 | 0.378 | 0.358 | 0.341 | 0.324 | 0.308 | 0.295 | 0.284 | 0.275 | 0.267 | 0.261 | 0.256 | 0.25 | 0.246 | 0.243 | 0.241 | 0.241 | 0.241 | 0.241 | 0.241 | 0.243 | 0.243 | 0.245 | 0.248 | 0.251 | 0.254 | 0.257 | 0.265 | 0.279 | 0.299 | 0.32 | 0.341 | 0.36 | 0.38 | 0.397 | 0.414 | 0.425 | 0.433 | 0.436 | 0.435 | 0.428 | 0.42 | 0.411 | 0.406 | 0.402 | 0.401 | 0.401 | 0.403 | 0.402 | 0.401 | 0.396 | 0.392 | 0.385 | 0.377 | 0.37 | 0.361 | 0.356 | 0.355 | 0.358 | 0.359 | 0.357 | 0.355 | 0.354 | 0.358 | 0.364 | 0.376 | 0.394 | 0.42 | 0.455 | 0.495 | 0.532 | 0.562 | 0.577 | 0.58 | 0.571 | 0.565 | 0.559 | 0.559 | 0.564 | 0.575 | 0.586 | 0.589 | 0.585 | 0.574 | 0.561 | 0.549 | 0.538 | 0.528 | 0.517 | 0.506 | 0.495 | 0.482 | 0.47 | 0.455 | 0.436 | 0.415 | 0.396 | 0.379 | 0.362 | 0.345 | 0.33 | 0.317 | 0.306 | 0.293 | 0.282 | 0.273 | 0.266 | 0.26 | 0.253 | 0.248 | 0.244 | 0.242 | 0.24 | 0.239 | 0.236 | 0.235 | 0.234 | 0.234 | 0.234 | 0.237 | 0.239 | 0.241 | 0.244 | 0.25 | 0.259 | 0.272 | 0.287 | 0.306 | 0.327 | 0.349 | 0.368 | 0.387 | 0.402 | 0.413 | 0.425 | 0.436 | 0.442 | 0.441 | 0.436 | 0.431 | 0.431 | 0.43 | 0.431 | 0.434 | 0.437 | 0.439 | 0.434 | 0.428 | 0.419 | 0.411 | 0.405 | 0.397 | 0.39 | 0.383 | 0.379 | 0.379 | 0.377 | 0.376 | 0.374 | 0.378 | 0.382 | 0.394 | 0.416 | 0.45 | 0.494 | 0.542 | 0.586 | 0.613 | 0.623 | 0.619 | 0.613 | 0.607 | 0.608 | 0.613 | 0.626 | 0.64 | 0.651 | 0.65 | 0.644 | 0.63 | 0.617 | 0.602 | 0.588 | 0.573 | 0.558 | 0.541 | 0.517 | 0.491 | 0.464 | 0.442 | 0.42 | 0.394 | 0.417 | 0.391 | 0.367 | 0.348 | 0.33 | 0.314 | 0.301 | 0.29 | 0.282 | 0.273 | 0.267 | 0.26 | 0.255 | 0.251 | 0.247 | 0.247 | 0.246 | 0.245 | 0.245 | 0.246 | 0.249 | 0.253 | 0.26 | 0.27 | 0.283 | 0.298 | 0.316 | 0.338 | 0.362 | 0.388 | 0.412 | 0.431 | 0.444 | 0.45 | 0.453 | 0.456 | 0.456 | 0.455 | 0.451 | 0.446 | 0.439 | 0.431 | 0.423 | 0.413 | 0.405 | 0.398 | 0.396 | 0.398 | 0.4 | 0.397 | 0.39 | 0.381 | 0.375 | 0.37 | 0.366 | 0.362 | 0.361 | 0.362 | 0.365 | 0.369 | 0.372 | 0.375 | 0.381 | 0.391 | 0.407 | 0.429 | 0.462 | 0.51 | 0.566 | 0.624 | 0.669 | 0.695 | 0.706 | 0.709 | 0.714 | 0.717 | 0.72 | 0.72 | 0.723 | 0.717 | 0.704 | 0.683 | 0.664 | 0.648 | 0.637 | 0.627 | 0.616 | 0.601 | 0.584 | 0.566 | 0.548 | 0.532 | 0.515 | 0.497 | 0.475 | 0.451 | 0.434 | 0.408 | 0.385 | 0.363 | 0.344 | 0.329 | 0.315 | 0.304 | 0.294 | 0.284 | 0.275 | 0.268 | 0.263 | 0.259 | 0.256 | 0.253 | 0.251 | 0.25 | 0.25 | 0.251 | 0.251 | 0.254 | 0.257 | 0.263 | 0.266 | 0.269 | 0.273 | 0.284 | 0.301 | 0.319 | 0.344 | 0.37 | 0.399 | 0.427 | 0.454 | 0.48 | 0.5 | 0.516 | 0.524 | 0.524 | 0.516 | 0.507 | 0.5 | 0.495 | 0.494 | 0.496 | 0.499 | 0.502 | 0.505 | 0.507 | 0.505 | 0.493 | 0.478 | 0.468 | 0.463 | 0.461 | 0.455 | 0.451 | 0.449 | 0.449 | 0.453 | 0.454 | 0.453 | 0.452 | 0.459 | 0.474 | 0.497 | 0.531 | 0.577 | 0.63 | 0.678 | 0.709 | 0.724 | 0.726 | 0.729 | 0.727 | 0.728 | 0.723 | 0.726 | 0.714 | 0.701 | 0.68 | 0.659 | 0.637 | 0.619 | 0.608 | 0.598 | 0.585 | 0.571 | 0.558 | 0.544 | 0.531 | 0.515 | 0.499 | 0.479 | 0.457 | 0.435 | 0.413 | 0.391 | 0.369 | 0.349 | 0.333 | 0.321 | 0.305 | 0.294 | 0.285 | 0.275 | 0.267 | 0.262 | 0.258 | 0.254 | 0.25 | 0.248 | 0.247 | 0.245 | 0.244 | 0.245 | 0.247 | 0.249 | 0.253 | 0.257 | 0.262 | 0.268 | 0.276 | 0.288 | 0.304 | 0.321 | 0.344 | 0.369 | 0.4 | 0.43 | 0.458 | 0.477 | 0.492 | 0.503 | 0.511 | 0.519 | 0.521 | 0.524 | 0.525 | 0.526 | 0.523 | 0.522 | 0.523 | 0.526 | 0.53 | 0.526 | 0.528 | 0.523 | 0.519 | 0.507 | 0.501 | 0.493 | 0.489 | 0.487 | 0.486 | 0.484 | 0.482 | 0.486 | 0.494 | 0.504 | 0.518 | 0.54 | 0.577 | 0.63 | 0.689 | 0.741 | 0.771 | 0.779 | 0.772 | 0.766 | 0.764 | 0.763 | 0.762 | 0.758 | 0.752 | 0.739 | 0.719 | 0.695 | 0.672 | 0.655 | 0.641 | 0.625 | 0.611 | 0.594 | 0.575 | 0.553 | 0.531 | 0.506 | 0.48 | 0.453 | 0.427 | 0.433 | 0.407 | 0.383 | 0.362 | 0.344 | 0.329 | 0.316 | 0.306 | 0.297 | 0.289 | 0.281 | 0.275 | 0.271 | 0.269 | 0.267 | 0.266 | 0.264 | 0.262 | 0.261 | 0.263 | 0.268 | 0.274 | 0.283 | 0.296 | 0.312 | 0.332 | 0.353 | 0.377 | 0.406 | 0.434 | 0.461 | 0.478 | 0.487 | 0.49 | 0.491 | 0.492 | 0.493 | 0.493 | 0.488 | 0.483 | 0.474 | 0.465 | 0.455 | 0.448 | 0.442 | 0.44 | 0.441 | 0.446 | 0.451 | 0.452 | 0.449 | 0.443 | 0.438 | 0.435 | 0.433 | 0.434 | 0.435 | 0.439 | 0.445 | 0.453 | 0.46 | 0.468 | 0.48 | 0.494 | 0.515 | 0.547 | 0.597 | 0.666 | 0.745 | 0.818 | 0.865 | 0.88 | 0.871 | 0.852 | 0.833 | 0.815 | 0.802 | 0.789 | 0.781 | 0.767 | 0.752 | 0.729 | 0.709 | 0.692 | 0.679 | 0.667 | 0.655 | 0.64 | 0.623 | 0.605 | 0.584 | 0.566 | 0.546 | 0.526 | 0.498 | 0.47 | 0.467 | 0.444 | 0.422 | 0.403 | 0.381 | 0.361 | 0.34 | 0.326 | 0.315 | 0.305 | 0.295 | 0.286 | 0.28 | 0.276 | 0.272 | 0.269 | 0.266 | 0.265 | 0.265 | 0.265 | 0.267 | 0.27 | 0.275 | 0.282 | 0.289 | 0.298 | 0.308 | 0.321 | 0.339 | 0.359 | 0.384 | 0.412 | 0.446 | 0.476 | 0.503 | 0.524 | 0.543 | 0.558 | 0.569 | 0.574 | 0.572 | 0.568 | 0.566 | 0.564 | 0.564 | 0.564 | 0.572 | 0.58 | 0.589 | 0.59 | 0.584 | 0.576 | 0.566 | 0.559 | 0.552 | 0.551 | 0.55 | 0.55 | 0.553 | 0.557 | 0.562 | 0.567 | 0.575 | 0.586 | 0.601 | 0.625 | 0.665 | 0.719 | 0.786 | 0.856 | 0.909 | 0.923 | 0.907 | 0.879 | 0.854 | 0.831 | 0.81 | 0.795 | 0.786 | 0.773 | 0.757 | 0.734 | 0.709 | 0.685 | 0.663 | 0.647 | 0.632 | 0.62 | 0.607 | 0.594 | 0.577 | 0.559 | 0.538 | 0.519 | 0.5 | 0.478 | 0.453 | 0.429 | 0.408 | 0.391 | 0.373 | 0.357 | 0.341 | 0.329 | 0.317 | 0.308 | 0.298 | 0.292 | 0.287 | 0.283 | 0.277 | 0.272 | 0.268 | 0.266 | 0.265 | 0.265 | 0.264 | 0.265 | 0.266 | 0.27 | 0.277 | 0.285 | 0.291 | 0.298 | 0.308 | 0.326 | 0.346 | 0.373 | 0.4 | 0.431 | 0.463 | 0.495 | 0.519 | 0.535 | 0.546 | 0.558 | 0.565 | 0.573 | 0.577 | 0.579 | 0.58 | 0.58 | 0.585 | 0.59 | 0.597 | 0.601 | 0.607 | 0.606 | 0.605 | 0.599 | 0.595 | 0.591 | 0.586 | 0.58 | 0.58 | 0.58 | 0.585 | 0.586 | 0.589 | 0.595 | 0.607 | 0.635 | 0.675 | 0.736 | 0.808 | 0.882 | 0.93 | 0.939 | 0.918 | 0.888 | 0.867 | 0.85 | 0.837 | 0.825 | 0.821 | 0.814 | 0.806 | 0.781 | 0.755 | 0.722 | 0.699 | 0.683 | 0.671 | 0.656 | 0.634 | 0.61 | 0.585 | 0.556 | 0.526 | 0.492 | 0.462 | 0.434 | 0.468 | 0.437 | 0.411 | 0.39 | 0.37 | 0.353 | 0.337 | 0.325 | 0.315 | 0.306 | 0.298 | 0.29 | 0.285 | 0.281 | 0.279 | 0.278 | 0.276 | 0.275 | 0.274 | 0.276 | 0.28 | 0.286 | 0.294 | 0.305 | 0.32 | 0.337 | 0.355 | 0.376 | 0.402 | 0.43 | 0.459 | 0.483 | 0.504 | 0.521 | 0.536 | 0.547 | 0.555 | 0.559 | 0.561 | 0.56 | 0.557 | 0.554 | 0.549 | 0.544 | 0.54 | 0.54 | 0.542 | 0.546 | 0.55 | 0.551 | 0.546 | 0.537 | 0.532 | 0.528 | 0.527 | 0.526 | 0.528 | 0.529 | 0.534 | 0.539 | 0.547 | 0.555 | 0.567 | 0.581 | 0.605 | 0.641 | 0.691 | 0.752 | 0.817 | 0.875 | 0.913 | 0.923 | 0.916 | 0.899 | 0.882 | 0.864 | 0.847 | 0.832 | 0.824 | 0.813 | 0.796 | 0.774 | 0.755 | 0.738 | 0.726 | 0.714 | 0.701 | 0.683 | 0.665 | 0.645 | 0.623 | 0.605 | 0.586 | 0.566 | 0.54 | 0.508 | 0.494 | 0.472 | 0.446 | 0.422 | 0.397 | 0.377 | 0.358 | 0.344 | 0.331 | 0.318 | 0.307 | 0.298 | 0.291 | 0.287 | 0.284 | 0.282 | 0.28 | 0.279 | 0.278 | 0.278 | 0.281 | 0.284 | 0.289 | 0.298 | 0.308 | 0.316 | 0.322 | 0.334 | 0.351 | 0.373 | 0.397 | 0.421 | 0.452 | 0.482 | 0.516 | 0.546 | 0.574 | 0.595 | 0.611 | 0.622 | 0.628 | 0.631 | 0.63 | 0.63 | 0.629 | 0.635 | 0.639 | 0.649 | 0.651 | 0.652 | 0.643 | 0.637 | 0.634 | 0.636 | 0.635 | 0.631 | 0.628 | 0.627 | 0.629 | 0.632 | 0.64 | 0.649 | 0.658 | 0.667 | 0.678 | 0.701 | 0.74 | 0.793 | 0.852 | 0.904 | 0.942 | 0.955 | 0.949 | 0.926 | 0.901 | 0.874 | 0.853 | 0.833 | 0.821 | 0.808 | 0.793 | 0.77 | 0.749 | 0.73 | 0.715 | 0.703 | 0.694 | 0.681 | 0.667 | 0.649 | 0.633 | 0.618 | 0.605 | 0.587 | 0.566 | 0.523 | 0.498 | 0.472 | 0.447 | 0.423 | 0.401 | 0.381 | 0.362 | 0.345 | 0.331 | 0.319 | 0.31 | 0.303 | 0.297 | 0.291 | 0.285 | 0.282 | 0.281 | 0.279 | 0.278 | 0.277 | 0.278 | 0.279 | 0.282 | 0.288 | 0.294 | 0.3 | 0.307 | 0.315 | 0.327 | 0.342 | 0.36 | 0.382 | 0.411 | 0.447 | 0.485 | 0.519 | 0.549 | 0.573 | 0.598 | 0.618 | 0.633 | 0.641 | 0.646 | 0.647 | 0.649 | 0.649 | 0.656 | 0.663 | 0.677 | 0.69 | 0.699 | 0.692 | 0.68 | 0.669 | 0.666 | 0.665 | 0.66 | 0.653 | 0.652 | 0.655 | 0.659 | 0.66 | 0.665 | 0.674 | 0.693 | 0.72 | 0.762 | 0.816 | 0.885 | 0.948 | 0.992 | 1 | 0.985 | 0.957 | 0.932 | 0.909 | 0.896 | 0.881 | 0.875 | 0.862 | 0.848 | 0.821 | 0.794 | 0.771 | 0.751 | 0.737 | 0.722 | 0.705 | 0.682 | 0.655 | 0.624 | 0.595 | 0.565 | 0.536 | 0.505 | 0.476
E1B | -3456 | 0.453 | 0.428 | 0.403 | 0.381 | 0.361 | 0.345 | 0.331 | 0.32 | 0.312 | 0.303 | 0.294 | 0.287 | 0.283 | 0.281 | 0.278 | 0.277 | 0.275 | 0.274 | 0.273 | 0.275 | 0.279 | 0.285 | 0.293 | 0.308 | 0.327 | 0.349 | 0.373 | 0.399 | 0.425 | 0.451 | 0.473 | 0.49 | 0.502 | 0.51 | 0.514 | 0.518 | 0.519 | 0.521 | 0.516 | 0.509 | 0.498 | 0.485 | 0.471 | 0.459 | 0.45 | 0.443 | 0.443 | 0.445 | 0.447 | 0.444 | 0.437 | 0.429 | 0.424 | 0.422 | 0.424 | 0.426 | 0.43 | 0.435 | 0.445 | 0.456 | 0.465 | 0.474 | 0.486 | 0.502 | 0.522 | 0.55 | 0.594 | 0.655 | 0.73 | 0.803 | 0.856 | 0.878 | 0.88 | 0.869 | 0.858 | 0.842 | 0.826 | 0.812 | 0.801 | 0.789 | 0.772 | 0.749 | 0.727 | 0.707 | 0.69 | 0.675 | 0.661 | 0.644 | 0.628 | 0.609 | 0.59 | 0.574 | 0.558 | 0.542 | 0.517 | 0.491 | 0.483 | 0.465 | 0.444 | 0.418 | 0.393 | 0.368 | 0.349 | 0.335 | 0.324 | 0.314 | 0.302 | 0.293 | 0.289 | 0.287 | 0.283 | 0.281 | 0.28 | 0.281 | 0.28 | 0.281 | 0.283 | 0.286 | 0.289 | 0.293 | 0.298 | 0.304 | 0.312 | 0.323 | 0.341 | 0.364 | 0.392 | 0.417 | 0.443 | 0.473 | 0.503 | 0.534 | 0.561 | 0.586 | 0.603 | 0.606 | 0.603 | 0.596 | 0.597 | 0.602 | 0.602 | 0.602 | 0.602 | 0.605 | 0.608 | 0.608 | 0.606 | 0.601 | 0.592 | 0.58 | 0.573 | 0.568 | 0.569 | 0.566 | 0.568 | 0.571 | 0.575 | 0.582 | 0.589 | 0.6 | 0.609 | 0.627 | 0.656 | 0.706 | 0.774 | 0.84 | 0.889 | 0.906 | 0.9 | 0.881 | 0.859 | 0.84 | 0.817 | 0.799 | 0.787 | 0.778 | 0.766 | 0.744 | 0.72 | 0.692 | 0.673 | 0.661 | 0.65 | 0.638 | 0.624 | 0.616 | 0.605 | 0.589 | 0.568 | 0.547 | 0.527 | 0.518 | 0.474 | 0.451 | 0.426 | 0.405 | 0.386 | 0.368 | 0.351 | 0.334 | 0.322 | 0.315 | 0.306 | 0.298 | 0.292 | 0.288 | 0.283 | 0.279 | 0.276 | 0.275 | 0.274 | 0.274 | 0.275 | 0.277 | 0.281 | 0.286 | 0.291 | 0.296 | 0.3 | 0.308 | 0.315 | 0.33 | 0.346 | 0.369 | 0.393 | 0.425 | 0.458 | 0.49 | 0.518 | 0.536 | 0.553 | 0.567 | 0.584 | 0.592 | 0.596 | 0.594 | 0.592 | 0.587 | 0.59 | 0.592 | 0.601 | 0.61 | 0.619 | 0.621 | 0.611 | 0.603 | 0.596 | 0.595 | 0.591 | 0.59 | 0.594 | 0.598 | 0.594 | 0.591 | 0.592 | 0.601 | 0.615 | 0.638 | 0.676 | 0.727 | 0.796 | 0.872 | 0.936 | 0.959 | 0.949 | 0.925 | 0.906 | 0.887 | 0.873 | 0.861 | 0.856 | 0.843 | 0.831 | 0.806 | 0.783 | 0.753 | 0.73 | 0.712 | 0.697 | 0.679 | 0.654 | 0.628 | 0.598 | 0.572 | 0.544 | 0.518 | 0.486 | 0.457 | 0.446 | 0.42 | 0.398 | 0.378 | 0.361 | 0.345 | 0.333 | 0.324 | 0.315 | 0.306 | 0.298 | 0.291 | 0.286 | 0.284 | 0.281 | 0.278 | 0.275 | 0.273 | 0.273 | 0.275 | 0.279 | 0.286 | 0.296 | 0.312 | 0.33 | 0.351 | 0.372 | 0.396 | 0.424 | 0.449 | 0.47 | 0.482 | 0.489 | 0.489 | 0.485 | 0.483 | 0.481 | 0.476 | 0.466 | 0.455 | 0.441 | 0.425 | 0.409 | 0.395 | 0.386 | 0.38 | 0.376 | 0.372 | 0.37 | 0.369 | 0.365 | 0.358 | 0.35 | 0.346 | 0.347 | 0.347 | 0.35 | 0.354 | 0.364 | 0.376 | 0.386 | 0.397 | 0.409 | 0.425 | 0.445 | 0.473 | 0.51 | 0.56 | 0.622 | 0.692 | 0.751 | 0.789 | 0.812 | 0.823 | 0.826 | 0.818 | 0.805 | 0.791 | 0.783 | 0.772 | 0.757 | 0.735 | 0.712 | 0.691 | 0.674 | 0.659 | 0.646 | 0.631 | 0.615 | 0.596 | 0.578 | 0.564 | 0.55 | 0.533 | 0.51 | 0.484 | 0.486 | 0.459 | 0.432 | 0.409 | 0.386 | 0.366 | 0.347 | 0.334 | 0.325 | 0.318 | 0.309 | 0.3 | 0.294 | 0.287 | 0.283 | 0.28 | 0.278 | 0.277 | 0.275 | 0.274 | 0.276 | 0.281 | 0.287 | 0.294 | 0.3 | 0.304 | 0.313 | 0.324 | 0.345 | 0.367 | 0.393 | 0.416 | 0.448 | 0.477 | 0.501 | 0.517 | 0.53 | 0.546 | 0.555 | 0.558 | 0.545 | 0.531 | 0.519 | 0.508 | 0.497 | 0.494 | 0.502 | 0.509 | 0.512 | 0.512 | 0.51 | 0.5 | 0.487 | 0.472 | 0.464 | 0.463 | 0.472 | 0.477 | 0.477 | 0.476 | 0.479 | 0.481 | 0.488 | 0.496 | 0.51 | 0.528 | 0.556 | 0.592 | 0.645 | 0.708 | 0.775 | 0.814 | 0.831 | 0.831 | 0.829 | 0.823 | 0.809 | 0.793 | 0.779 | 0.76 | 0.743 | 0.719 | 0.697 | 0.671 | 0.651 | 0.638 | 0.633 | 0.623 | 0.61 | 0.595 | 0.577 | 0.563 | 0.547 | 0.534 | 0.515 | 0.495 | 0.473 | 0.45 | 0.428 | 0.405 | 0.385 | 0.365 | 0.349 | 0.335 | 0.324 | 0.315 | 0.306 | 0.297 | 0.29 | 0.286 | 0.28 | 0.278 | 0.274 | 0.274 | 0.27 | 0.269 | 0.27 | 0.272 | 0.276 | 0.282 | 0.288 | 0.295 | 0.3 | 0.309 | 0.32 | 0.337 | 0.353 | 0.378 | 0.402 | 0.429 | 0.455 | 0.48 | 0.498 | 0.507 | 0.509 | 0.52 | 0.535 | 0.547 | 0.543 | 0.531 | 0.525 | 0.52 | 0.523 | 0.526 | 0.534 | 0.537 | 0.535 | 0.532 | 0.524 | 0.517 | 0.514 | 0.513 | 0.508 | 0.506 | 0.512 | 0.517 | 0.519 | 0.518 | 0.524 | 0.531 | 0.541 | 0.557 | 0.586 | 0.63 | 0.688 | 0.755 | 0.813 | 0.852 | 0.866 | 0.873 | 0.871 | 0.86 | 0.846 | 0.833 | 0.829 | 0.818 | 0.803 | 0.776 | 0.751 | 0.727 | 0.706 | 0.689 | 0.672 | 0.653 | 0.635 | 0.612 | 0.587 | 0.56 | 0.532 | 0.504 | 0.475 | 0.446 | 0.433 | 0.409 | 0.388 | 0.369 | 0.352 | 0.337 | 0.324 | 0.313 | 0.304 | 0.294 | 0.285 | 0.278 | 0.273 | 0.27 | 0.267 | 0.266 | 0.265 | 0.264 | 0.265 | 0.267 | 0.27 | 0.276 | 0.285 | 0.299 | 0.316 | 0.336 | 0.355 | 0.375 | 0.396 | 0.415 | 0.43 | 0.437 | 0.438 | 0.434 | 0.428 | 0.422 | 0.416 | 0.407 | 0.395 | 0.38 | 0.363 | 0.347 | 0.332 | 0.317 | 0.305 | 0.296 | 0.293 | 0.29 | 0.289 | 0.285 | 0.281 | 0.272 | 0.265 | 0.263 | 0.263 | 0.265 | 0.268 | 0.273 | 0.282 | 0.291 | 0.3 | 0.309 | 0.321 | 0.336 | 0.354 | 0.381 | 0.42 | 0.474 | 0.535 | 0.595 | 0.647 | 0.682 | 0.705 | 0.716 | 0.728 | 0.737 | 0.744 | 0.746 | 0.749 | 0.744 | 0.732 | 0.713 | 0.694 | 0.677 | 0.66 | 0.645 | 0.633 | 0.618 | 0.601 | 0.581 | 0.56 | 0.542 | 0.527 | 0.511 | 0.489 | 0.465 | 0.474 | 0.452 | 0.427 | 0.404 | 0.382 | 0.364 | 0.348 | 0.336 | 0.323 | 0.311 | 0.3 | 0.292 | 0.286 | 0.281 | 0.276 | 0.273 | 0.271 | 0.27 | 0.269 | 0.269 | 0.271 | 0.273 | 0.276 | 0.284 | 0.292 | 0.299 | 0.307 | 0.32 | 0.338 | 0.356 | 0.376 | 0.393 | 0.411 | 0.429 | 0.445 | 0.454 | 0.461 | 0.468 | 0.472 | 0.468 | 0.461 | 0.453 | 0.438 | 0.421 | 0.408 | 0.405 | 0.409 | 0.414 | 0.421 | 0.42 | 0.415 | 0.403 | 0.396 | 0.391 | 0.392 | 0.395 | 0.401 | 0.405 | 0.41 | 0.414 | 0.419 | 0.424 | 0.431 | 0.439 | 0.453 | 0.469 | 0.498 | 0.538 | 0.596 | 0.657 | 0.715 | 0.748 | 0.769 | 0.776 | 0.784 | 0.786 | 0.785 | 0.78 | 0.777 | 0.763 | 0.748 | 0.725 | 0.7 | 0.67 | 0.651 | 0.639 | 0.628 | 0.611 | 0.596 | 0.585 | 0.572 | 0.554 | 0.535 | 0.515 | 0.497 | 0.474 | 0.45 | 0.427 | 0.405 | 0.388 | 0.374 | 0.361 | 0.345 | 0.336 | 0.324 | 0.314 | 0.3 | 0.298 | 0.289 | 0.284 | 0.278 | 0.274 | 0.269 | 0.268 | 0.267 | 0.266 | 0.264 | 0.264 | 0.267 | 0.274 | 0.28 | 0.285 | 0.29 | 0.299 | 0.31 | 0.321 | 0.336 | 0.353 | 0.371 | 0.39 | 0.41 | 0.426 | 0.434 | 0.442 | 0.447 | 0.457 | 0.463 | 0.47 | 0.47 | 0.467 | 0.46 | 0.45 | 0.445 | 0.446 | 0.455 | 0.463 | 0.464 | 0.461 | 0.455 | 0.446 | 0.437 | 0.425 | 0.415 | 0.413 | 0.417 | 0.426 | 0.432 | 0.435 | 0.436 | 0.441 | 0.452 | 0.471 | 0.497 | 0.537 | 0.589 | 0.654 | 0.715 | 0.752 | 0.766 | 0.77 | 0.781 | 0.785 | 0.786 | 0.784 | 0.791 | 0.788 | 0.781 | 0.762 | 0.742 | 0.714 | 0.696 | 0.684 | 0.675 | 0.659 | 0.641 | 0.619 | 0.593 | 0.561 | 0.531 | 0.503 | 0.477 | 0.45 | 0.404 | 0.382 | 0.363 | 0.346 | 0.332 | 0.318 | 0.307 | 0.296 | 0.287 | 0.279 | 0.27 | 0.262 | 0.256 | 0.252 | 0.25 | 0.248 | 0.246 | 0.246 | 0.246 | 0.248 | 0.251 | 0.255 | 0.261 | 0.271 | 0.286 | 0.3 | 0.314 | 0.329 | 0.345 | 0.36 | 0.374 | 0.381 | 0.384 | 0.382 | 0.379 | 0.373 | 0.366 | 0.356 | 0.343 | 0.325 | 0.305 | 0.283 | 0.266 | 0.25 | 0.237 | 0.225 | 0.215 | 0.21 | 0.205 | 0.201 | 0.191 | 0.181 | 0.168 | 0.159 | 0.153 | 0.152 | 0.155 | 0.156 | 0.162 | 0.166 | 0.171 | 0.176 | 0.183 | 0.196 | 0.213 | 0.238 | 0.271 | 0.319 | 0.378 | 0.441 | 0.493 | 0.526 | 0.544 | 0.553 | 0.558 | 0.561 | 0.563 | 0.567 | 0.574 | 0.581 | 0.587 | 0.591 | 0.592 | 0.594 | 0.595 | 0.595 | 0.59 | 0.58 | 0.565 | 0.549 | 0.532 | 0.518 | 0.505 | 0.487 | 0.465 | 0.439 | 0.436 | 0.411 | 0.388 | 0.368 | 0.353 | 0.337 | 0.323 | 0.307 | 0.297 | 0.288 | 0.281 | 0.274 | 0.268 | 0.261 | 0.256 | 0.252 | 0.25 | 0.25 | 0.25 | 0.252 | 0.254 | 0.258 | 0.262 | 0.269 | 0.273 | 0.275 | 0.278 | 0.284 | 0.296 | 0.311 | 0.331 | 0.349 | 0.367 | 0.381 | 0.395 | 0.404 | 0.409 | 0.412 | 0.408 | 0.398 | 0.385 | 0.371 | 0.358 | 0.345 | 0.336 | 0.327 | 0.324 | 0.324 | 0.322 | 0.314 | 0.301 | 0.286 | 0.273 | 0.264 | 0.257 | 0.251 | 0.245 | 0.244 | 0.242 | 0.239 | 0.241 | 0.248 | 0.258 | 0.266 | 0.273 | 0.286 | 0.309 | 0.345 | 0.393 | 0.449 | 0.501 | 0.538 | 0.559 | 0.57 | 0.574 | 0.577 | 0.577 | 0.581 | 0.583 | 0.586 | 0.596 | 0.602 | 0.607 | 0.604 | 0.602 | 0.6 | 0.595 | 0.587 | 0.577 | 0.563 | 0.547 | 0.529 | 0.514 | 0.497 | 0.476 | 0.451 | 0.425 | 0.404 | 0.385 | 0.367 | 0.348 | 0.332 | 0.317 | 0.304 | 0.289 | 0.28 | 0.273 | 0.268 | 0.266 | 0.262 | 0.257 | 0.253 | 0.249 | 0.249 | 0.246 | 0.248 | 0.246 | 0.248 | 0.248 | 0.252 | 0.254 | 0.257 | 0.26 | 0.269 | 0.278 | 0.292 | 0.307 | 0.322 | 0.338 | 0.353 | 0.371 | 0.38 | 0.384 | 0.389 | 0.392 | 0.392 | 0.388 | 0.383 | 0.376 | 0.362 | 0.347 | 0.335 | 0.33 | 0.327 | 0.323 | 0.32 | 0.316 | 0.308 | 0.3 | 0.285 | 0.271 | 0.253 | 0.244 | 0.24 | 0.239 | 0.24 | 0.242 | 0.246 | 0.249 | 0.253 | 0.264 | 0.282 | 0.314 | 0.355 | 0.411 | 0.473 | 0.531 | 0.57 | 0.588 | 0.594 | 0.591 | 0.587 | 0.589 | 0.599 | 0.612 | 0.62 | 0.629 | 0.635 | 0.639 | 0.634 | 0.63 | 0.621 | 0.612 | 0.596 | 0.577 | 0.556 | 0.534 | 0.515 | 0.491 | 0.465 | 0.436 | 0.413 | 0.405 | 0.382 | 0.362 | 0.344 | 0.328 | 0.313 | 0.303 | 0.293 | 0.284 | 0.277 | 0.268 | 0.262 | 0.255 | 0.251 | 0.248 | 0.246 | 0.244 | 0.244 | 0.244 | 0.246 | 0.247 | 0.25 | 0.254 | 0.261 | 0.269 | 0.277 | 0.285 | 0.292 | 0.303 | 0.314 | 0.326 | 0.331 | 0.33 | 0.327 | 0.321 | 0.317 | 0.309 | 0.298 | 0.283 | 0.267 | 0.248 | 0.23 | 0.211 | 0.197 | 0.184 | 0.176 | 0.17 | 0.166 | 0.161 | 0.155 | 0.146 | 0.136 | 0.128 | 0.122 | 0.117 | 0.114 | 0.114 | 0.115 | 0.12 | 0.125 | 0.13 | 0.136 | 0.146 | 0.158 | 0.175 | 0.198 | 0.23 | 0.276 | 0.331 | 0.391 | 0.441 | 0.472 | 0.491 | 0.499 | 0.504 | 0.503 | 0.504 | 0.508 | 0.518 | 0.527 | 0.531 | 0.526 | 0.518 | 0.516 | 0.518 | 0.525 | 0.532 | 0.534 | 0.535 | 0.527 | 0.516 | 0.506 | 0.495 | 0.482 | 0.462 | 0.434 | 0.409 | 0.389 | 0.382 | 0.361 | 0.344 | 0.331 | 0.32 | 0.306 | 0.295 | 0.284 | 0.274 | 0.265 | 0.26 | 0.257 | 0.252 | 0.248 | 0.244 | 0.243 | 0.241 | 0.243 | 0.246 | 0.251 | 0.254 | 0.256 | 0.256 | 0.255 | 0.256 | 0.258 | 0.264 | 0.271 | 0.283 | 0.295 | 0.309 | 0.32 | 0.323 | 0.325 | 0.328 | 0.336 | 0.34 | 0.336 | 0.323 | 0.302 | 0.279 | 0.263 | 0.258 | 0.258 | 0.256 | 0.253 | 0.247 | 0.247 | 0.241 | 0.233 | 0.218 | 0.203 | 0.193 | 0.187 | 0.184 | 0.182 | 0.18 | 0.179 | 0.178 | 0.179 | 0.184 | 0.194 | 0.209 | 0.228 | 0.253 | 0.289 | 0.335 | 0.386 | 0.431 | 0.464 | 0.487 | 0.499 | 0.51 | 0.513 | 0.514 | 0.514 | 0.521 | 0.531 | 0.529 | 0.522 | 0.514 | 0.512 | 0.516 | 0.526 | 0.539 | 0.546 | 0.546 | 0.537 | 0.524 | 0.514 | 0.507 | 0.502 | 0.482 | 0.456 | 0.428 | 0.406 | 0.386 | 0.366 | 0.347 | 0.333 | 0.321 | 0.31 | 0.298 | 0.289 | 0.284 | 0.275 | 0.268 | 0.26 | 0.255 | 0.251 | 0.248 | 0.244 | 0.24 | 0.239 | 0.238 | 0.238 | 0.236 | 0.236 | 0.239 | 0.242 | 0.245 | 0.245 | 0.245 | 0.249 | 0.256 | 0.266 | 0.277 | 0.292 | 0.308 | 0.319 | 0.324 | 0.325 | 0.327 | 0.33 | 0.33 | 0.322 | 0.31 | 0.295 | 0.289 | 0.287 | 0.285 | 0.277 | 0.271 | 0.269 | 0.264 | 0.253 | 0.237 | 0.227 | 0.219 | 0.217 | 0.215 | 0.215 | 0.217 | 0.22 | 0.221 | 0.221 | 0.226 | 0.235 | 0.245 | 0.263 | 0.289 | 0.326 | 0.37 | 0.428 | 0.484 | 0.524 | 0.539 | 0.543 | 0.55 | 0.559 | 0.561 | 0.561 | 0.564 | 0.571 | 0.577 | 0.572 | 0.562 | 0.548 | 0.544 | 0.551 | 0.557 | 0.557 | 0.549 | 0.534 | 0.517 | 0.498 | 0.48 | 0.46 | 0.436 | 0.411 | 0.408 | 0.384 | 0.363 | 0.346 | 0.33 | 0.316 | 0.303 | 0.291 | 0.281 | 0.273 | 0.266 | 0.26 | 0.256 | 0.253 | 0.249 | 0.246 | 0.244 | 0.242 | 0.241 | 0.24 | 0.241 | 0.243 | 0.246 | 0.248 | 0.254 | 0.26 | 0.267 | 0.275 | 0.284 | 0.292 | 0.299 | 0.303 | 0.304 | 0.302 | 0.296 | 0.291 | 0.284 | 0.273 | 0.26 | 0.246 | 0.229 | 0.21 | 0.191 | 0.177 | 0.165 | 0.156 | 0.15 | 0.149 | 0.148 | 0.146 | 0.138 | 0.129 | 0.119 | 0.112 | 0.109 | 0.107 | 0.106 | 0.108 | 0.112 | 0.117 | 0.121 | 0.127 | 0.136 | 0.147 | 0.161 | 0.182 | 0.212 | 0.252 | 0.303 | 0.358 | 0.405 | 0.434 | 0.45 | 0.457 | 0.462 | 0.462 | 0.463 | 0.466 | 0.475 | 0.481 | 0.485 | 0.482 | 0.478 | 0.474 | 0.472 | 0.473 | 0.477 | 0.483 | 0.489 | 0.493 | 0.492 | 0.493 | 0.489 | 0.481 | 0.463 | 0.439 | 0.423 | 0.4 | 0.38 | 0.361 | 0.346 | 0.328 | 0.313 | 0.3 | 0.292 | 0.284 | 0.274 | 0.265 | 0.257 | 0.252 | 0.246 | 0.243 | 0.241 | 0.241 | 0.24 | 0.24 | 0.24 | 0.24 | 0.242 | 0.242 | 0.24 | 0.236 | 0.234 | 0.234 | 0.24 | 0.248 | 0.26 | 0.272 | 0.282 | 0.291 | 0.296 | 0.304 | 0.309 | 0.314 | 0.312 | 0.309 | 0.302 | 0.292 | 0.275 | 0.266 | 0.259 | 0.257 | 0.255 | 0.251 | 0.248 | 0.241 | 0.235 | 0.225 | 0.215 | 0.206 | 0.192 | 0.181 | 0.174 | 0.174 | 0.174 | 0.171 | 0.171 | 0.172 | 0.176 | 0.183 | 0.193 | 0.209 | 0.23 | 0.256 | 0.292 | 0.338 | 0.386 | 0.421 | 0.442 | 0.453 | 0.458 | 0.456 | 0.451 | 0.45 | 0.46 | 0.47 | 0.479 | 0.478 | 0.476 | 0.474 | 0.473 | 0.477 | 0.478 | 0.484 | 0.486 | 0.491 | 0.489 | 0.487 | 0.484 | 0.476 | 0.46 | 0.44 | 0.417 | 0.398 | 0.378 | 0.364 | 0.349 | 0.334 | 0.318 | 0.303 | 0.293 | 0.286 | 0.279 | 0.272 | 0.263 | 0.258 | 0.253 | 0.249 | 0.244 | 0.24 | 0.237 | 0.235 | 0.233 | 0.232 | 0.232 | 0.231 | 0.228 | 0.225 | 0.222 | 0.221 | 0.221 | 0.224 | 0.229 | 0.237 | 0.248 | 0.26 | 0.27 | 0.278 | 0.286 | 0.291 | 0.291 | 0.292 | 0.288 | 0.283 | 0.272 | 0.268 | 0.267 | 0.261 | 0.25 | 0.241 | 0.238 | 0.235 | 0.23 | 0.228 | 0.221 | 0.219 | 0.212 | 0.21 | 0.205 | 0.202 | 0.201 | 0.202 | 0.202 | 0.203 | 0.204 | 0.207 | 0.211 | 0.221 | 0.242 | 0.276 | 0.324 | 0.377 | 0.428 | 0.461 | 0.477 | 0.483 | 0.483 | 0.483 | 0.484 | 0.491 | 0.505 | 0.518 | 0.525 | 0.524 | 0.518 | 0.514 | 0.512 | 0.513 | 0.51 | 0.512 | 0.515 | 0.518 | 0.512 | 0.498 | 0.478 | 0.457 | 0.434 | 0.407 | 0.401 | 0.378 | 0.357 | 0.34 | 0.325 | 0.312 | 0.3 | 0.29 | 0.281 | 0.272 | 0.265 | 0.259 | 0.255 | 0.251 | 0.248 | 0.247 | 0.246 | 0.245 | 0.244 | 0.243 | 0.244 | 0.246 | 0.249 | 0.253 | 0.257 | 0.261 | 0.265 | 0.271 | 0.278 | 0.284 | 0.29 | 0.294 | 0.296 | 0.295 | 0.292 | 0.288 | 0.281 | 0.27 | 0.256 | 0.241 | 0.226 | 0.21 | 0.195 | 0.183 | 0.172 | 0.163 | 0.155 | 0.151 | 0.149 | 0.144 | 0.136 | 0.126 | 0.119 | 0.113 | 0.11 | 0.107 | 0.107 | 0.108 | 0.114 | 0.119 | 0.125 | 0.128 | 0.136 | 0.145 | 0.158 | 0.177 | 0.205 | 0.244 | 0.293 | 0.348 | 0.396 | 0.426 | 0.44 | 0.446 | 0.452 | 0.454 | 0.456 | 0.458 | 0.466 | 0.474 | 0.478 | 0.475 | 0.469 | 0.466 | 0.467 | 0.47 | 0.473 | 0.478 | 0.485 | 0.489 | 0.487 | 0.484 | 0.479 | 0.47 | 0.453 | 0.433 | 0.429 | 0.41 | 0.388 | 0.367 | 0.349 | 0.332 | 0.318 | 0.304 | 0.293 | 0.284 | 0.277 | 0.269 | 0.263 | 0.257 | 0.254 | 0.252 | 0.252 | 0.254 | 0.254 | 0.255 | 0.254 | 0.254 | 0.253 | 0.254 | 0.253 | 0.252 | 0.247 | 0.246 | 0.253 | 0.259 | 0.268 | 0.274 | 0.284 | 0.291 | 0.297 | 0.304 | 0.31 | 0.315 | 0.315 | 0.305 | 0.294 | 0.281 | 0.268 | 0.257 | 0.25 | 0.245 | 0.241 | 0.239 | 0.24 | 0.238 | 0.231 | 0.223 | 0.213 | 0.203 | 0.192 | 0.185 | 0.181 | 0.178 | 0.174 | 0.173 | 0.172 | 0.174 | 0.181 | 0.191 | 0.202 | 0.216 | 0.235 | 0.263 | 0.298 | 0.343 | 0.386 | 0.416 | 0.435 | 0.444 | 0.45 | 0.447 | 0.444 | 0.444 | 0.452 | 0.46 | 0.466 | 0.466 | 0.463 | 0.463 | 0.465 | 0.47 | 0.471 | 0.474 | 0.479 | 0.484 | 0.482 | 0.478 | 0.469 | 0.458 | 0.444 | 0.426 | 0.407 | 0.386 | 0.368 | 0.353 | 0.34 | 0.327 | 0.314 | 0.302 | 0.293 | 0.285 | 0.277 | 0.271 | 0.267 | 0.265 | 0.26 | 0.256 | 0.252 | 0.249 | 0.245 | 0.242 | 0.24 | 0.24 | 0.239 | 0.238 | 0.238 | 0.236 | 0.234 | 0.233 | 0.234 | 0.236 | 0.239 | 0.245 | 0.253 | 0.263 | 0.274 | 0.282 | 0.289 | 0.289 | 0.289 | 0.286 | 0.284 | 0.279 | 0.27 | 0.257 | 0.246 | 0.24 | 0.237 | 0.232 | 0.226 | 0.221 | 0.221 | 0.216 | 0.205 | 0.193 | 0.182 | 0.176 | 0.172 | 0.173 | 0.177 | 0.179 | 0.181 | 0.18 | 0.183 | 0.185 | 0.195 | 0.208 | 0.235 | 0.264 | 0.303 | 0.348 | 0.392 | 0.423 | 0.439 | 0.446 | 0.449 | 0.452 | 0.458 | 0.467 | 0.477 | 0.483 | 0.489 | 0.491 | 0.493 | 0.493 | 0.494 | 0.497 | 0.501 | 0.504 | 0.505 | 0.504 | 0.496 | 0.485 | 0.47 | 0.453 | 0.432 | 0.408 | 0.404 | 0.383 | 0.364 | 0.347 | 0.332 | 0.318 | 0.307 | 0.297 | 0.289 | 0.282 | 0.275 | 0.27 | 0.266 | 0.263 | 0.259 | 0.257 | 0.256 | 0.255 | 0.254 | 0.253 | 0.254 | 0.256 | 0.258 | 0.261 | 0.267 | 0.276 | 0.283 | 0.29 | 0.298 | 0.306 | 0.312 | 0.317 | 0.32 | 0.32 | 0.318 | 0.312 | 0.304 | 0.293 | 0.281 | 0.267 | 0.251 | 0.234 | 0.218 | 0.204 | 0.192 | 0.183 | 0.178 | 0.174 | 0.17 | 0.164 | 0.156 | 0.146 | 0.137 | 0.131 | 0.127 | 0.125 | 0.126 | 0.129 | 0.135 | 0.14 | 0.144 | 0.15 | 0.159 | 0.172 | 0.186 | 0.206 | 0.236 | 0.277 | 0.327 | 0.377 | 0.423 | 0.454 | 0.474 | 0.481 | 0.486 | 0.49 | 0.494 | 0.497 | 0.503 | 0.51 | 0.516 | 0.516 | 0.514 | 0.515 | 0.519 | 0.525 | 0.529 | 0.528 | 0.522 | 0.513 | 0.501 | 0.492 | 0.483 | 0.472 | 0.453 | 0.432 | 0.415 | 0.397 | 0.376 | 0.359 | 0.344 | 0.332 | 0.321 | 0.309 | 0.297 | 0.287 | 0.279 | 0.276 | 0.272 | 0.267 | 0.26 | 0.256 | 0.256 | 0.258 | 0.259 | 0.258 | 0.258 | 0.261 | 0.262 | 0.264 | 0.265 | 0.268 | 0.267 | 0.267 | 0.272 | 0.283 | 0.295 | 0.305 | 0.313 | 0.32 | 0.327 | 0.33 | 0.332 | 0.331 | 0.327 | 0.32 | 0.31 | 0.299 | 0.286 | 0.274 | 0.261 | 0.254 | 0.25 | 0.248 | 0.245 | 0.242 | 0.236 | 0.223 | 0.211 | 0.205 | 0.201 | 0.195 | 0.191 | 0.191 | 0.193 | 0.194 | 0.197 | 0.202 | 0.211 | 0.218 | 0.228 | 0.243 | 0.27 | 0.3 | 0.338 | 0.38 | 0.42 | 0.449 | 0.465 | 0.476 | 0.481 | 0.485 | 0.486 | 0.489 | 0.494 | 0.501 | 0.507 | 0.506 | 0.506 | 0.507 | 0.513 | 0.522 | 0.526 | 0.523 | 0.516 | 0.508 | 0.503 | 0.495 | 0.485 | 0.471 | 0.45 | 0.43 | 0.408 | 0.389 | 0.372 | 0.358 | 0.344 | 0.33 | 0.316 | 0.303 | 0.292 | 0.284 | 0.277 | 0.272 | 0.267 | 0.262 | 0.258 | 0.254 | 0.252 | 0.251 | 0.249 | 0.247 | 0.246 | 0.245 | 0.246 | 0.248 | 0.249 | 0.249 | 0.248 | 0.248 | 0.251 | 0.257 | 0.265 | 0.275 | 0.285 | 0.296 | 0.302 | 0.306 | 0.307 | 0.306 | 0.305 | 0.305 | 0.305 | 0.301 | 0.295 | 0.289 | 0.284 | 0.279 | 0.272 | 0.262 | 0.251 | 0.245 | 0.241 | 0.235 | 0.227 | 0.219 | 0.214 | 0.208 | 0.204 | 0.2 | 0.202 | 0.206 | 0.211 | 0.213 | 0.218 | 0.225 | 0.237 | 0.254 | 0.277 | 0.307 | 0.347 | 0.389 | 0.433 | 0.468 | 0.492 | 0.497 | 0.495 | 0.498 | 0.507 | 0.516 | 0.524 | 0.53 | 0.538 | 0.539 | 0.54 | 0.541 | 0.551 | 0.557 | 0.558 | 0.55 | 0.541 | 0.529 | 0.513 | 0.493 | 0.473 | 0.455 | 0.436 | 0.414 | 0.388 | 0.366 | 0.346 | 0.327 | 0.312 | 0.298 | 0.285 | 0.274 | 0.264 | 0.256 | 0.249 | 0.243 | 0.239 | 0.236 | 0.234 | 0.232 | 0.231 | 0.23 | 0.229 | 0.229 | 0.231 | 0.234 | 0.239 | 0.247 | 0.26 | 0.276 | 0.294 | 0.313 | 0.335 | 0.354 | 0.369 | 0.377 | 0.379 | 0.377 | 0.373 | 0.367 | 0.361 | 0.349 | 0.335 | 0.317 | 0.298 | 0.28 | 0.263 | 0.246 | 0.23 | 0.219 | 0.212 | 0.21 | 0.205 | 0.199 | 0.191 | 0.182 | 0.175 | 0.168 | 0.165 | 0.164 | 0.166 | 0.171 | 0.178 | 0.184 | 0.19 | 0.197 | 0.209 | 0.224 | 0.243 | 0.267 | 0.3 | 0.346 | 0.401 | 0.459 | 0.504 | 0.532 | 0.545 | 0.552 | 0.556 | 0.556 | 0.556 | 0.562 | 0.577 | 0.59 | 0.598 | 0.597 | 0.592 | 0.583 | 0.572 | 0.56 | 0.55 | 0.538 | 0.526 | 0.51 | 0.493 | 0.479 | 0.466 | 0.454 | 0.436 | 0.414 | 0.392 | 0.37 | 0.35 | 0.335 | 0.317 | 0.302 | 0.287 | 0.278 | 0.268 | 0.261 | 0.255 | 0.249 | 0.244 | 0.239 | 0.237 | 0.234 | 0.235 | 0.234 | 0.235 | 0.236 | 0.237 | 0.238 | 0.24 | 0.243 | 0.246 | 0.248 | 0.249 | 0.256 | 0.272 | 0.293 | 0.313 | 0.331 | 0.347 | 0.36 | 0.37 | 0.38 | 0.384 | 0.385 | 0.379 | 0.37 | 0.355 | 0.337 | 0.32 | 0.31 | 0.302 | 0.297 | 0.293 | 0.291 | 0.284 | 0.28 | 0.272 | 0.269 | 0.262 | 0.254 | 0.245 | 0.235 | 0.232 | 0.232 | 0.238 | 0.243 | 0.245 | 0.245 | 0.249 | 0.257 | 0.27 | 0.288 | 0.312 | 0.344 | 0.385 | 0.432 | 0.476 | 0.514 | 0.535 | 0.543 | 0.538 | 0.538 | 0.537 | 0.541 | 0.549 | 0.561 | 0.573 | 0.575 | 0.572 | 0.562 | 0.55 | 0.538 | 0.525 | 0.515 | 0.504 | 0.492 | 0.48 | 0.468 | 0.456 | 0.443 | 0.425 | 0.405 | 0.387 | 0.372 | 0.357 | 0.341 | 0.327 | 0.314 | 0.303 | 0.29 | 0.279 | 0.269 | 0.263 | 0.256 | 0.249 | 0.243 | 0.238 | 0.237 | 0.235 | 0.233 | 0.23 | 0.228 | 0.228 | 0.228 | 0.228 | 0.23 | 0.233 | 0.235 | 0.237 | 0.243 | 0.252 | 0.264 | 0.278 | 0.295 | 0.31 | 0.326 | 0.339 | 0.35 | 0.357 | 0.359 | 0.365 | 0.37 | 0.371 | 0.363 | 0.349 | 0.34 | 0.336 | 0.331 | 0.327 | 0.326 | 0.325 | 0.324 | 0.318 | 0.311 | 0.302 | 0.292 | 0.287 | 0.281 | 0.275 | 0.269 | 0.269 | 0.273 | 0.275 | 0.279 | 0.281 | 0.289 | 0.298 | 0.315 | 0.343 | 0.382 | 0.434 | 0.49 | 0.542 | 0.575 | 0.592 | 0.592 | 0.59 | 0.588 | 0.593 | 0.603 | 0.619 | 0.633 | 0.643 | 0.644 | 0.638 | 0.622 | 0.608 | 0.593 | 0.579 | 0.563 | 0.546 | 0.529 | 0.505 | 0.478 | 0.452 | 0.433 | 0.413 | 0.389 | 0.415 | 0.39 | 0.367 | 0.348 | 0.331 | 0.315 | 0.301 | 0.29 | 0.281 | 0.272 | 0.265 | 0.258 | 0.252 | 0.247 | 0.243 | 0.242 | 0.241 | 0.241 | 0.24 | 0.241 | 0.244 | 0.248 | 0.254 | 0.264 | 0.277 | 0.294 | 0.312 | 0.333 | 0.357 | 0.383 | 0.408 | 0.427 | 0.44 | 0.445 | 0.445 | 0.443 | 0.438 | 0.432 | 0.423 | 0.412 | 0.398 | 0.384 | 0.37 | 0.355 | 0.341 | 0.329 | 0.323 | 0.322 | 0.32 | 0.314 | 0.304 | 0.293 | 0.286 | 0.282 | 0.278 | 0.277 | 0.278 | 0.283 | 0.29 | 0.297 | 0.304 | 0.31 | 0.32 | 0.334 | 0.354 | 0.38 | 0.415 | 0.466 | 0.528 | 0.591 | 0.64 | 0.67 | 0.687 | 0.696 | 0.705 | 0.708 | 0.712 | 0.712 | 0.716 | 0.71 | 0.696 | 0.672 | 0.652 | 0.633 | 0.617 | 0.604 | 0.594 | 0.579 | 0.564 | 0.547 | 0.531 | 0.518 | 0.503 | 0.489 | 0.469 | 0.447 | 0.428 | 0.403 | 0.38 | 0.358 | 0.339 | 0.324 | 0.311 | 0.301 | 0.29 | 0.281 | 0.271 | 0.264 | 0.259 | 0.255 | 0.253 | 0.249 | 0.246 | 0.246 | 0.245 | 0.247 | 0.247 | 0.25 | 0.253 | 0.259 | 0.261 | 0.263 | 0.267 | 0.279 | 0.298 | 0.317 | 0.341 | 0.365 | 0.392 | 0.418 | 0.441 | 0.464 | 0.48 | 0.492 | 0.494 | 0.489 | 0.475 | 0.459 | 0.444 | 0.433 | 0.427 | 0.424 | 0.422 | 0.421 | 0.42 | 0.42 | 0.415 | 0.401 | 0.383 | 0.373 | 0.369 | 0.369 | 0.364 | 0.361 | 0.362 | 0.366 | 0.375 | 0.381 | 0.383 | 0.386 | 0.397 | 0.419 | 0.447 | 0.487 | 0.539 | 0.598 | 0.652 | 0.686 | 0.704 | 0.709 | 0.714 | 0.713 | 0.717 | 0.713 | 0.718 | 0.704 | 0.69 | 0.668 | 0.647 | 0.624 | 0.607 | 0.596 | 0.587 | 0.574 | 0.56 | 0.547 | 0.533 | 0.52 | 0.504 | 0.49 | 0.471 | 0.449 | 0.428 | 0.408 | 0.387 | 0.364 | 0.344 | 0.329 | 0.317 | 0.302 | 0.292 | 0.282 | 0.271 | 0.262 | 0.258 | 0.254 | 0.249 | 0.245 | 0.243 | 0.242 | 0.241 | 0.239 | 0.24 | 0.242 | 0.244 | 0.247 | 0.251 | 0.257 | 0.262 | 0.271 | 0.282 | 0.298 | 0.314 | 0.336 | 0.359 | 0.388 | 0.414 | 0.438 | 0.451 | 0.458 | 0.462 | 0.465 | 0.468 | 0.466 | 0.465 | 0.462 | 0.459 | 0.451 | 0.443 | 0.44 | 0.439 | 0.441 | 0.437 | 0.441 | 0.437 | 0.435 | 0.422 | 0.417 | 0.411 | 0.41 | 0.413 | 0.415 | 0.417 | 0.418 | 0.428 | 0.442 | 0.458 | 0.476 | 0.502 | 0.543 | 0.601 | 0.667 | 0.724 | 0.758 | 0.767 | 0.762 | 0.759 | 0.758 | 0.756 | 0.756 | 0.754 | 0.747 | 0.732 | 0.711 | 0.688 | 0.666 | 0.648 | 0.633 | 0.617 | 0.602 | 0.584 | 0.565 | 0.543 | 0.522 | 0.499 | 0.475 | 0.449 | 0.426 | 0.431 | 0.406 | 0.383 | 0.362 | 0.344 | 0.33 | 0.317 | 0.308 | 0.298 | 0.29 | 0.281 | 0.274 | 0.269 | 0.267 | 0.264 | 0.263 | 0.26 | 0.259 | 0.258 | 0.26 | 0.264 | 0.27 | 0.277 | 0.29 | 0.307 | 0.328 | 0.35 | 0.374 | 0.402 | 0.43 | 0.456 | 0.473 | 0.483 | 0.485 | 0.482 | 0.48 | 0.477 | 0.473 | 0.464 | 0.454 | 0.441 | 0.429 | 0.414 | 0.404 | 0.395 | 0.39 | 0.39 | 0.393 | 0.398 | 0.398 | 0.395 | 0.39 | 0.385 | 0.383 | 0.383 | 0.387 | 0.392 | 0.401 | 0.411 | 0.424 | 0.436 | 0.448 | 0.463 | 0.48 | 0.502 | 0.535 | 0.585 | 0.652 | 0.729 | 0.8 | 0.849 | 0.864 | 0.858 | 0.84 | 0.822 | 0.805 | 0.792 | 0.78 | 0.773 | 0.759 | 0.744 | 0.72 | 0.699 | 0.678 | 0.66 | 0.645 | 0.632 | 0.618 | 0.602 | 0.584 | 0.565 | 0.551 | 0.535 | 0.519 | 0.494 | 0.467 | 0.466 | 0.445 | 0.423 | 0.405 | 0.382 | 0.36 | 0.339 | 0.325 | 0.314 | 0.304 | 0.293 | 0.284 | 0.277 | 0.272 | 0.269 | 0.264 | 0.262 | 0.26 | 0.261 | 0.261 | 0.263 | 0.266 | 0.27 | 0.277 | 0.286 | 0.294 | 0.304 | 0.317 | 0.334 | 0.354 | 0.378 | 0.405 | 0.438 | 0.465 | 0.488 | 0.505 | 0.521 | 0.533 | 0.544 | 0.546 | 0.539 | 0.527 | 0.521 | 0.516 | 0.515 | 0.51 | 0.517 | 0.524 | 0.533 | 0.533 | 0.527 | 0.52 | 0.51 | 0.504 | 0.496 | 0.496 | 0.499 | 0.505 | 0.515 | 0.525 | 0.535 | 0.543 | 0.554 | 0.567 | 0.584 | 0.611 | 0.654 | 0.707 | 0.771 | 0.84 | 0.896 | 0.91 | 0.893 | 0.863 | 0.839 | 0.816 | 0.796 | 0.781 | 0.772 | 0.759 | 0.744 | 0.722 | 0.697 | 0.673 | 0.651 | 0.636 | 0.62 | 0.608 | 0.595 | 0.582 | 0.564 | 0.547 | 0.526 | 0.509 | 0.491 | 0.47 | 0.446 | 0.422 | 0.403 | 0.387 | 0.371 | 0.356 | 0.341 | 0.33 | 0.318 | 0.308 | 0.298 | 0.291 | 0.286 | 0.282 | 0.275 | 0.268 | 0.263 | 0.262 | 0.261 | 0.261 | 0.259 | 0.26 | 0.26 | 0.264 | 0.272 | 0.28 | 0.286 | 0.291 | 0.301 | 0.318 | 0.338 | 0.365 | 0.389 | 0.418 | 0.445 | 0.474 | 0.493 | 0.504 | 0.509 | 0.518 | 0.522 | 0.527 | 0.527 | 0.525 | 0.523 | 0.521 | 0.528 | 0.532 | 0.538 | 0.541 | 0.548 | 0.549 | 0.55 | 0.547 | 0.545 | 0.544 | 0.541 | 0.54 | 0.545 | 0.551 | 0.562 | 0.566 | 0.573 | 0.581 | 0.596 | 0.627 | 0.669 | 0.73 | 0.802 | 0.877 | 0.926 | 0.934 | 0.909 | 0.875 | 0.854 | 0.84 | 0.832 | 0.824 | 0.821 | 0.814 | 0.804 | 0.779 | 0.751 | 0.716 | 0.691 | 0.675 | 0.663 | 0.647 | 0.624 | 0.598 | 0.574 | 0.547 | 0.518 | 0.485 | 0.456 | 0.43 | 0.466 | 0.436 | 0.412 | 0.392 | 0.373 | 0.355 | 0.339 | 0.328 | 0.317 | 0.308 | 0.299 | 0.291 | 0.284 | 0.28 | 0.277 | 0.276 | 0.274 | 0.273 | 0.273 | 0.274 | 0.277 | 0.283 | 0.29 | 0.302 | 0.317 | 0.336 | 0.354 | 0.374 | 0.399 | 0.427 | 0.457 | 0.481 | 0.503 | 0.52 | 0.535 | 0.545 | 0.55 | 0.551 | 0.548 | 0.544 | 0.537 | 0.531 | 0.522 | 0.515 | 0.509 | 0.508 | 0.507 | 0.51 | 0.512 | 0.512 | 0.506 | 0.497 | 0.491 | 0.488 | 0.49 | 0.491 | 0.497 | 0.502 | 0.511 | 0.519 | 0.531 | 0.542 | 0.557 | 0.574 | 0.6 | 0.636 | 0.686 | 0.743 | 0.805 | 0.861 | 0.898 | 0.909 | 0.903 | 0.887 | 0.871 | 0.854 | 0.838 | 0.824 | 0.815 | 0.803 | 0.787 | 0.764 | 0.744 | 0.725 | 0.708 | 0.693 | 0.679 | 0.662 | 0.645 | 0.626 | 0.605 | 0.59 | 0.574 | 0.558 | 0.535 | 0.505 | 0.494 | 0.476 | 0.449 | 0.425 | 0.397 | 0.377 | 0.358 | 0.345 | 0.332 | 0.319 | 0.308 | 0.297 | 0.291 | 0.286 | 0.283 | 0.281 | 0.28 | 0.278 | 0.278 | 0.279 | 0.282 | 0.284 | 0.289 | 0.298 | 0.309 | 0.317 | 0.322 | 0.333 | 0.35 | 0.371 | 0.395 | 0.418 | 0.45 | 0.481 | 0.513 | 0.54 | 0.565 | 0.583 | 0.596 | 0.605 | 0.609 | 0.609 | 0.604 | 0.598 | 0.594 | 0.598 | 0.601 | 0.608 | 0.607 | 0.608 | 0.597 | 0.589 | 0.586 | 0.59 | 0.588 | 0.585 | 0.584 | 0.588 | 0.595 | 0.601 | 0.613 | 0.626 | 0.64 | 0.652 | 0.664 | 0.686 | 0.724 | 0.776 | 0.835 | 0.886 | 0.926 | 0.941 | 0.937 | 0.913 | 0.888 | 0.861 | 0.841 | 0.82 | 0.808 | 0.794 | 0.779 | 0.757 | 0.735 | 0.717 | 0.703 | 0.692 | 0.685 | 0.674 | 0.66 | 0.641 | 0.622 | 0.608 | 0.597 | 0.58 | 0.56 | 0.519 | 0.497 | 0.473 | 0.448 | 0.424 | 0.403 | 0.384 | 0.364 | 0.346 | 0.332 | 0.32 | 0.31 | 0.302 | 0.296 | 0.289 | 0.283 | 0.281 | 0.28 | 0.278 | 0.276 | 0.275 | 0.276 | 0.277 | 0.28 | 0.287 | 0.293 | 0.299 | 0.305 | 0.312 | 0.324 | 0.338 | 0.356 | 0.378 | 0.407 | 0.441 | 0.476 | 0.506 | 0.534 | 0.554 | 0.575 | 0.592 | 0.604 | 0.611 | 0.613 | 0.61 | 0.608 | 0.606 | 0.611 | 0.616 | 0.63 | 0.645 | 0.657 | 0.65 | 0.637 | 0.627 | 0.627 | 0.63 | 0.626 | 0.62 | 0.623 | 0.632 | 0.644 | 0.647 | 0.657 | 0.669 | 0.692 | 0.719 | 0.761 | 0.814 | 0.883 | 0.948 | 0.993 | 1 | 0.98 | 0.947 | 0.92 | 0.9 | 0.888 | 0.875 | 0.869 | 0.855 | 0.84 | 0.812 | 0.786 | 0.763 | 0.742 | 0.727 | 0.712 | 0.695 | 0.671 | 0.643 | 0.612 | 0.585 | 0.557 | 0.53 | 0.502 | 0.476
E1C | -3456 | 0.452 | 0.423 | 0.396 | 0.374 | 0.354 | 0.338 | 0.324 | 0.314 | 0.306 | 0.298 | 0.292 | 0.287 | 0.283 | 0.282 | 0.282 | 0.284 | 0.283 | 0.282 | 0.282 | 0.285 | 0.291 | 0.299 | 0.31 | 0.324 | 0.34 | 0.358 | 0.379 | 0.405 | 0.434 | 0.463 | 0.489 | 0.508 | 0.517 | 0.522 | 0.524 | 0.531 | 0.535 | 0.536 | 0.528 | 0.517 | 0.504 | 0.487 | 0.469 | 0.453 | 0.439 | 0.429 | 0.426 | 0.428 | 0.43 | 0.428 | 0.422 | 0.414 | 0.409 | 0.409 | 0.413 | 0.415 | 0.418 | 0.425 | 0.434 | 0.445 | 0.456 | 0.471 | 0.491 | 0.514 | 0.54 | 0.576 | 0.632 | 0.707 | 0.793 | 0.874 | 0.933 | 0.955 | 0.949 | 0.927 | 0.909 | 0.89 | 0.874 | 0.858 | 0.847 | 0.835 | 0.818 | 0.797 | 0.776 | 0.77 | 0.772 | 0.773 | 0.761 | 0.739 | 0.719 | 0.696 | 0.67 | 0.639 | 0.606 | 0.57 | 0.533 | 0.498 | 0.493 | 0.464 | 0.437 | 0.413 | 0.388 | 0.37 | 0.354 | 0.34 | 0.328 | 0.316 | 0.307 | 0.3 | 0.294 | 0.291 | 0.289 | 0.288 | 0.287 | 0.285 | 0.285 | 0.284 | 0.285 | 0.288 | 0.293 | 0.299 | 0.304 | 0.311 | 0.32 | 0.334 | 0.352 | 0.374 | 0.4 | 0.431 | 0.466 | 0.504 | 0.539 | 0.574 | 0.603 | 0.624 | 0.629 | 0.624 | 0.619 | 0.615 | 0.613 | 0.607 | 0.598 | 0.589 | 0.584 | 0.586 | 0.593 | 0.597 | 0.592 | 0.581 | 0.569 | 0.567 | 0.568 | 0.571 | 0.573 | 0.579 | 0.587 | 0.591 | 0.593 | 0.599 | 0.61 | 0.626 | 0.646 | 0.674 | 0.717 | 0.77 | 0.83 | 0.89 | 0.94 | 0.964 | 0.963 | 0.945 | 0.925 | 0.905 | 0.882 | 0.861 | 0.843 | 0.824 | 0.806 | 0.785 | 0.764 | 0.738 | 0.717 | 0.701 | 0.689 | 0.672 | 0.658 | 0.646 | 0.633 | 0.615 | 0.594 | 0.568 | 0.54 | 0.534 | 0.487 | 0.464 | 0.437 | 0.412 | 0.391 | 0.374 | 0.359 | 0.345 | 0.333 | 0.322 | 0.313 | 0.305 | 0.298 | 0.294 | 0.292 | 0.29 | 0.287 | 0.284 | 0.282 | 0.282 | 0.284 | 0.287 | 0.289 | 0.293 | 0.298 | 0.305 | 0.311 | 0.32 | 0.331 | 0.346 | 0.366 | 0.391 | 0.42 | 0.455 | 0.492 | 0.53 | 0.563 | 0.589 | 0.604 | 0.608 | 0.608 | 0.605 | 0.604 | 0.6 | 0.599 | 0.598 | 0.603 | 0.603 | 0.605 | 0.606 | 0.607 | 0.606 | 0.601 | 0.595 | 0.587 | 0.582 | 0.582 | 0.584 | 0.584 | 0.583 | 0.582 | 0.588 | 0.598 | 0.61 | 0.623 | 0.646 | 0.684 | 0.738 | 0.802 | 0.873 | 0.941 | 0.981 | 0.988 | 0.969 | 0.944 | 0.92 | 0.9 | 0.884 | 0.875 | 0.865 | 0.855 | 0.836 | 0.813 | 0.786 | 0.763 | 0.747 | 0.734 | 0.716 | 0.696 | 0.673 | 0.644 | 0.612 | 0.573 | 0.534 | 0.497 | 0.463 | 0.451 | 0.421 | 0.396 | 0.372 | 0.353 | 0.338 | 0.327 | 0.316 | 0.308 | 0.302 | 0.298 | 0.294 | 0.291 | 0.289 | 0.289 | 0.289 | 0.29 | 0.289 | 0.29 | 0.294 | 0.3 | 0.309 | 0.319 | 0.333 | 0.348 | 0.364 | 0.383 | 0.407 | 0.435 | 0.463 | 0.487 | 0.504 | 0.51 | 0.508 | 0.501 | 0.496 | 0.493 | 0.488 | 0.478 | 0.463 | 0.442 | 0.423 | 0.404 | 0.386 | 0.37 | 0.359 | 0.355 | 0.354 | 0.354 | 0.351 | 0.347 | 0.34 | 0.333 | 0.329 | 0.328 | 0.329 | 0.332 | 0.337 | 0.347 | 0.358 | 0.372 | 0.387 | 0.405 | 0.429 | 0.458 | 0.496 | 0.547 | 0.613 | 0.689 | 0.767 | 0.832 | 0.872 | 0.889 | 0.89 | 0.888 | 0.876 | 0.861 | 0.844 | 0.835 | 0.823 | 0.808 | 0.787 | 0.768 | 0.763 | 0.765 | 0.764 | 0.751 | 0.729 | 0.707 | 0.684 | 0.659 | 0.63 | 0.598 | 0.564 | 0.529 | 0.495 | 0.488 | 0.459 | 0.43 | 0.407 | 0.389 | 0.373 | 0.357 | 0.343 | 0.332 | 0.322 | 0.312 | 0.303 | 0.299 | 0.294 | 0.292 | 0.292 | 0.29 | 0.288 | 0.286 | 0.288 | 0.291 | 0.295 | 0.301 | 0.308 | 0.315 | 0.321 | 0.329 | 0.34 | 0.357 | 0.379 | 0.408 | 0.441 | 0.476 | 0.507 | 0.535 | 0.558 | 0.571 | 0.572 | 0.571 | 0.565 | 0.557 | 0.544 | 0.535 | 0.523 | 0.507 | 0.493 | 0.489 | 0.491 | 0.498 | 0.503 | 0.502 | 0.49 | 0.475 | 0.466 | 0.465 | 0.465 | 0.466 | 0.466 | 0.472 | 0.48 | 0.487 | 0.493 | 0.503 | 0.524 | 0.545 | 0.573 | 0.603 | 0.65 | 0.704 | 0.768 | 0.831 | 0.876 | 0.898 | 0.9 | 0.893 | 0.878 | 0.859 | 0.842 | 0.834 | 0.823 | 0.808 | 0.785 | 0.759 | 0.733 | 0.711 | 0.692 | 0.678 | 0.664 | 0.651 | 0.637 | 0.623 | 0.605 | 0.586 | 0.56 | 0.535 | 0.509 | 0.482 | 0.454 | 0.427 | 0.406 | 0.389 | 0.374 | 0.359 | 0.348 | 0.338 | 0.33 | 0.322 | 0.315 | 0.308 | 0.301 | 0.297 | 0.295 | 0.293 | 0.292 | 0.291 | 0.292 | 0.295 | 0.298 | 0.302 | 0.305 | 0.312 | 0.319 | 0.327 | 0.335 | 0.346 | 0.363 | 0.384 | 0.411 | 0.44 | 0.471 | 0.499 | 0.521 | 0.539 | 0.543 | 0.549 | 0.549 | 0.55 | 0.547 | 0.542 | 0.533 | 0.522 | 0.511 | 0.507 | 0.51 | 0.514 | 0.515 | 0.508 | 0.497 | 0.486 | 0.477 | 0.473 | 0.466 | 0.464 | 0.465 | 0.467 | 0.47 | 0.474 | 0.481 | 0.49 | 0.502 | 0.52 | 0.547 | 0.585 | 0.639 | 0.702 | 0.772 | 0.839 | 0.884 | 0.909 | 0.914 | 0.91 | 0.893 | 0.877 | 0.865 | 0.859 | 0.846 | 0.834 | 0.81 | 0.788 | 0.762 | 0.744 | 0.727 | 0.712 | 0.694 | 0.675 | 0.653 | 0.627 | 0.595 | 0.56 | 0.524 | 0.489 | 0.458 | 0.437 | 0.409 | 0.382 | 0.359 | 0.34 | 0.325 | 0.313 | 0.304 | 0.296 | 0.289 | 0.284 | 0.28 | 0.278 | 0.276 | 0.275 | 0.275 | 0.275 | 0.274 | 0.275 | 0.279 | 0.286 | 0.295 | 0.306 | 0.319 | 0.333 | 0.348 | 0.363 | 0.385 | 0.409 | 0.432 | 0.448 | 0.453 | 0.447 | 0.436 | 0.426 | 0.417 | 0.406 | 0.393 | 0.377 | 0.36 | 0.34 | 0.32 | 0.3 | 0.28 | 0.264 | 0.251 | 0.244 | 0.241 | 0.24 | 0.236 | 0.229 | 0.221 | 0.215 | 0.211 | 0.208 | 0.207 | 0.21 | 0.218 | 0.228 | 0.239 | 0.251 | 0.266 | 0.285 | 0.31 | 0.341 | 0.383 | 0.439 | 0.508 | 0.583 | 0.653 | 0.71 | 0.746 | 0.763 | 0.766 | 0.773 | 0.778 | 0.782 | 0.779 | 0.781 | 0.778 | 0.769 | 0.755 | 0.742 | 0.74 | 0.741 | 0.74 | 0.728 | 0.706 | 0.685 | 0.663 | 0.639 | 0.61 | 0.579 | 0.545 | 0.51 | 0.476 | 0.467 | 0.439 | 0.41 | 0.387 | 0.366 | 0.352 | 0.338 | 0.326 | 0.314 | 0.302 | 0.293 | 0.285 | 0.283 | 0.28 | 0.28 | 0.279 | 0.277 | 0.275 | 0.274 | 0.275 | 0.279 | 0.285 | 0.292 | 0.299 | 0.306 | 0.313 | 0.322 | 0.336 | 0.352 | 0.373 | 0.394 | 0.415 | 0.433 | 0.451 | 0.468 | 0.477 | 0.482 | 0.478 | 0.469 | 0.453 | 0.44 | 0.431 | 0.426 | 0.414 | 0.402 | 0.388 | 0.384 | 0.378 | 0.377 | 0.376 | 0.374 | 0.372 | 0.366 | 0.363 | 0.362 | 0.361 | 0.361 | 0.364 | 0.369 | 0.377 | 0.389 | 0.401 | 0.414 | 0.426 | 0.447 | 0.475 | 0.511 | 0.563 | 0.625 | 0.695 | 0.755 | 0.794 | 0.812 | 0.819 | 0.828 | 0.832 | 0.832 | 0.828 | 0.826 | 0.813 | 0.794 | 0.765 | 0.74 | 0.716 | 0.697 | 0.68 | 0.666 | 0.651 | 0.636 | 0.62 | 0.603 | 0.586 | 0.566 | 0.542 | 0.516 | 0.489 | 0.462 | 0.435 | 0.41 | 0.386 | 0.366 | 0.35 | 0.338 | 0.33 | 0.319 | 0.308 | 0.301 | 0.299 | 0.292 | 0.288 | 0.285 | 0.284 | 0.28 | 0.277 | 0.276 | 0.278 | 0.281 | 0.285 | 0.29 | 0.294 | 0.298 | 0.304 | 0.31 | 0.321 | 0.333 | 0.35 | 0.365 | 0.383 | 0.404 | 0.426 | 0.444 | 0.454 | 0.462 | 0.469 | 0.475 | 0.475 | 0.469 | 0.461 | 0.452 | 0.445 | 0.434 | 0.425 | 0.418 | 0.417 | 0.416 | 0.413 | 0.409 | 0.401 | 0.394 | 0.382 | 0.374 | 0.365 | 0.366 | 0.366 | 0.372 | 0.373 | 0.381 | 0.389 | 0.398 | 0.407 | 0.421 | 0.445 | 0.482 | 0.53 | 0.591 | 0.659 | 0.723 | 0.77 | 0.797 | 0.805 | 0.805 | 0.802 | 0.804 | 0.807 | 0.813 | 0.809 | 0.802 | 0.781 | 0.761 | 0.739 | 0.724 | 0.712 | 0.701 | 0.687 | 0.669 | 0.643 | 0.617 | 0.587 | 0.555 | 0.52 | 0.485 | 0.453 | 0.418 | 0.392 | 0.367 | 0.346 | 0.327 | 0.312 | 0.3 | 0.29 | 0.282 | 0.275 | 0.27 | 0.267 | 0.265 | 0.264 | 0.261 | 0.26 | 0.258 | 0.259 | 0.26 | 0.265 | 0.27 | 0.275 | 0.283 | 0.294 | 0.306 | 0.317 | 0.328 | 0.34 | 0.354 | 0.368 | 0.381 | 0.385 | 0.384 | 0.379 | 0.376 | 0.365 | 0.351 | 0.331 | 0.313 | 0.292 | 0.27 | 0.246 | 0.222 | 0.198 | 0.179 | 0.161 | 0.148 | 0.141 | 0.137 | 0.128 | 0.114 | 0.099 | 0.088 | 0.078 | 0.071 | 0.065 | 0.061 | 0.062 | 0.065 | 0.071 | 0.079 | 0.09 | 0.104 | 0.122 | 0.146 | 0.181 | 0.232 | 0.299 | 0.374 | 0.447 | 0.508 | 0.547 | 0.563 | 0.565 | 0.567 | 0.572 | 0.578 | 0.583 | 0.594 | 0.607 | 0.619 | 0.628 | 0.636 | 0.655 | 0.675 | 0.684 | 0.678 | 0.661 | 0.644 | 0.624 | 0.602 | 0.576 | 0.55 | 0.519 | 0.489 | 0.456 | 0.45 | 0.425 | 0.399 | 0.375 | 0.355 | 0.337 | 0.322 | 0.309 | 0.3 | 0.292 | 0.285 | 0.276 | 0.271 | 0.267 | 0.265 | 0.264 | 0.263 | 0.262 | 0.262 | 0.264 | 0.267 | 0.27 | 0.273 | 0.277 | 0.281 | 0.287 | 0.293 | 0.3 | 0.31 | 0.325 | 0.343 | 0.357 | 0.371 | 0.384 | 0.4 | 0.408 | 0.408 | 0.399 | 0.389 | 0.376 | 0.361 | 0.344 | 0.324 | 0.304 | 0.283 | 0.267 | 0.256 | 0.254 | 0.253 | 0.247 | 0.233 | 0.219 | 0.208 | 0.198 | 0.188 | 0.18 | 0.175 | 0.171 | 0.169 | 0.168 | 0.169 | 0.173 | 0.179 | 0.192 | 0.211 | 0.235 | 0.269 | 0.315 | 0.374 | 0.441 | 0.503 | 0.551 | 0.576 | 0.58 | 0.58 | 0.587 | 0.596 | 0.604 | 0.611 | 0.621 | 0.627 | 0.633 | 0.637 | 0.64 | 0.636 | 0.631 | 0.626 | 0.618 | 0.606 | 0.591 | 0.575 | 0.558 | 0.541 | 0.52 | 0.496 | 0.468 | 0.443 | 0.418 | 0.394 | 0.371 | 0.353 | 0.336 | 0.322 | 0.309 | 0.299 | 0.291 | 0.284 | 0.279 | 0.274 | 0.27 | 0.267 | 0.264 | 0.262 | 0.261 | 0.261 | 0.261 | 0.262 | 0.263 | 0.266 | 0.27 | 0.273 | 0.277 | 0.281 | 0.285 | 0.293 | 0.304 | 0.317 | 0.33 | 0.346 | 0.364 | 0.382 | 0.395 | 0.405 | 0.411 | 0.409 | 0.4 | 0.384 | 0.368 | 0.352 | 0.333 | 0.312 | 0.293 | 0.279 | 0.273 | 0.272 | 0.264 | 0.251 | 0.229 | 0.211 | 0.198 | 0.189 | 0.182 | 0.17 | 0.162 | 0.158 | 0.159 | 0.161 | 0.167 | 0.173 | 0.184 | 0.196 | 0.216 | 0.253 | 0.302 | 0.369 | 0.437 | 0.503 | 0.548 | 0.577 | 0.588 | 0.595 | 0.6 | 0.61 | 0.618 | 0.63 | 0.643 | 0.656 | 0.663 | 0.664 | 0.662 | 0.659 | 0.652 | 0.645 | 0.633 | 0.618 | 0.598 | 0.579 | 0.556 | 0.527 | 0.493 | 0.463 | 0.436 | 0.419 | 0.393 | 0.37 | 0.349 | 0.329 | 0.313 | 0.301 | 0.292 | 0.285 | 0.278 | 0.273 | 0.27 | 0.268 | 0.266 | 0.264 | 0.263 | 0.261 | 0.261 | 0.262 | 0.265 | 0.27 | 0.275 | 0.28 | 0.285 | 0.289 | 0.294 | 0.301 | 0.308 | 0.315 | 0.32 | 0.325 | 0.324 | 0.32 | 0.312 | 0.301 | 0.29 | 0.278 | 0.264 | 0.244 | 0.222 | 0.199 | 0.175 | 0.151 | 0.128 | 0.108 | 0.094 | 0.083 | 0.078 | 0.074 | 0.069 | 0.059 | 0.047 | 0.035 | 0.027 | 0.02 | 0.016 | 0.013 | 0.011 | 0.013 | 0.017 | 0.025 | 0.035 | 0.05 | 0.069 | 0.093 | 0.127 | 0.177 | 0.241 | 0.313 | 0.385 | 0.443 | 0.479 | 0.491 | 0.494 | 0.497 | 0.501 | 0.507 | 0.516 | 0.531 | 0.546 | 0.555 | 0.558 | 0.561 | 0.577 | 0.6 | 0.62 | 0.627 | 0.627 | 0.623 | 0.612 | 0.596 | 0.575 | 0.551 | 0.522 | 0.49 | 0.455 | 0.437 | 0.414 | 0.392 | 0.375 | 0.358 | 0.344 | 0.329 | 0.318 | 0.306 | 0.297 | 0.29 | 0.285 | 0.282 | 0.278 | 0.275 | 0.271 | 0.269 | 0.268 | 0.268 | 0.267 | 0.267 | 0.266 | 0.266 | 0.266 | 0.266 | 0.267 | 0.269 | 0.27 | 0.272 | 0.275 | 0.284 | 0.292 | 0.301 | 0.31 | 0.316 | 0.324 | 0.32 | 0.312 | 0.296 | 0.284 | 0.27 | 0.255 | 0.234 | 0.216 | 0.2 | 0.187 | 0.175 | 0.172 | 0.171 | 0.169 | 0.158 | 0.14 | 0.125 | 0.11 | 0.104 | 0.099 | 0.1 | 0.098 | 0.097 | 0.101 | 0.107 | 0.114 | 0.121 | 0.133 | 0.147 | 0.169 | 0.2 | 0.243 | 0.299 | 0.362 | 0.426 | 0.464 | 0.487 | 0.494 | 0.501 | 0.504 | 0.507 | 0.516 | 0.531 | 0.546 | 0.556 | 0.558 | 0.556 | 0.552 | 0.555 | 0.557 | 0.561 | 0.566 | 0.569 | 0.568 | 0.559 | 0.547 | 0.533 | 0.516 | 0.494 | 0.468 | 0.441 | 0.415 | 0.392 | 0.373 | 0.358 | 0.342 | 0.327 | 0.315 | 0.306 | 0.298 | 0.29 | 0.283 | 0.278 | 0.273 | 0.27 | 0.268 | 0.267 | 0.266 | 0.265 | 0.266 | 0.267 | 0.268 | 0.267 | 0.265 | 0.263 | 0.264 | 0.264 | 0.261 | 0.259 | 0.259 | 0.265 | 0.274 | 0.287 | 0.3 | 0.313 | 0.322 | 0.322 | 0.323 | 0.316 | 0.309 | 0.297 | 0.284 | 0.268 | 0.253 | 0.237 | 0.22 | 0.204 | 0.199 | 0.199 | 0.197 | 0.183 | 0.17 | 0.155 | 0.145 | 0.134 | 0.127 | 0.121 | 0.12 | 0.118 | 0.12 | 0.12 | 0.124 | 0.131 | 0.14 | 0.155 | 0.176 | 0.211 | 0.26 | 0.318 | 0.378 | 0.43 | 0.471 | 0.502 | 0.521 | 0.534 | 0.537 | 0.542 | 0.547 | 0.559 | 0.573 | 0.585 | 0.587 | 0.588 | 0.585 | 0.59 | 0.594 | 0.602 | 0.607 | 0.605 | 0.595 | 0.578 | 0.558 | 0.532 | 0.503 | 0.47 | 0.438 | 0.43 | 0.404 | 0.38 | 0.358 | 0.34 | 0.326 | 0.313 | 0.303 | 0.295 | 0.289 | 0.284 | 0.279 | 0.276 | 0.273 | 0.271 | 0.269 | 0.267 | 0.267 | 0.268 | 0.27 | 0.271 | 0.272 | 0.275 | 0.276 | 0.277 | 0.279 | 0.284 | 0.292 | 0.299 | 0.305 | 0.309 | 0.309 | 0.305 | 0.296 | 0.283 | 0.273 | 0.26 | 0.244 | 0.221 | 0.198 | 0.177 | 0.157 | 0.135 | 0.117 | 0.101 | 0.089 | 0.077 | 0.073 | 0.069 | 0.064 | 0.053 | 0.042 | 0.032 | 0.024 | 0.019 | 0.015 | 0.014 | 0.016 | 0.021 | 0.026 | 0.033 | 0.042 | 0.056 | 0.072 | 0.094 | 0.123 | 0.169 | 0.224 | 0.288 | 0.351 | 0.405 | 0.438 | 0.453 | 0.457 | 0.463 | 0.467 | 0.475 | 0.482 | 0.497 | 0.51 | 0.522 | 0.527 | 0.53 | 0.543 | 0.558 | 0.572 | 0.575 | 0.578 | 0.584 | 0.588 | 0.584 | 0.573 | 0.553 | 0.528 | 0.498 | 0.464 | 0.444 | 0.417 | 0.397 | 0.377 | 0.358 | 0.341 | 0.325 | 0.313 | 0.303 | 0.295 | 0.29 | 0.282 | 0.277 | 0.271 | 0.268 | 0.267 | 0.265 | 0.265 | 0.265 | 0.265 | 0.265 | 0.264 | 0.263 | 0.26 | 0.256 | 0.253 | 0.253 | 0.254 | 0.256 | 0.261 | 0.266 | 0.273 | 0.279 | 0.287 | 0.295 | 0.305 | 0.309 | 0.302 | 0.288 | 0.276 | 0.264 | 0.252 | 0.232 | 0.221 | 0.205 | 0.194 | 0.182 | 0.179 | 0.177 | 0.172 | 0.164 | 0.149 | 0.134 | 0.123 | 0.12 | 0.12 | 0.115 | 0.112 | 0.11 | 0.111 | 0.113 | 0.119 | 0.13 | 0.14 | 0.152 | 0.168 | 0.196 | 0.235 | 0.282 | 0.333 | 0.38 | 0.417 | 0.44 | 0.454 | 0.465 | 0.475 | 0.484 | 0.492 | 0.501 | 0.508 | 0.513 | 0.513 | 0.512 | 0.51 | 0.509 | 0.508 | 0.51 | 0.517 | 0.526 | 0.536 | 0.538 | 0.532 | 0.518 | 0.503 | 0.486 | 0.467 | 0.445 | 0.42 | 0.397 | 0.377 | 0.36 | 0.345 | 0.333 | 0.322 | 0.312 | 0.304 | 0.297 | 0.29 | 0.285 | 0.281 | 0.278 | 0.275 | 0.273 | 0.272 | 0.27 | 0.268 | 0.266 | 0.264 | 0.263 | 0.26 | 0.255 | 0.25 | 0.246 | 0.244 | 0.244 | 0.245 | 0.247 | 0.251 | 0.258 | 0.267 | 0.274 | 0.281 | 0.286 | 0.288 | 0.285 | 0.276 | 0.267 | 0.255 | 0.241 | 0.227 | 0.21 | 0.194 | 0.181 | 0.176 | 0.176 | 0.172 | 0.16 | 0.147 | 0.134 | 0.127 | 0.119 | 0.118 | 0.115 | 0.112 | 0.108 | 0.107 | 0.109 | 0.109 | 0.114 | 0.123 | 0.141 | 0.161 | 0.191 | 0.229 | 0.279 | 0.331 | 0.38 | 0.418 | 0.446 | 0.462 | 0.472 | 0.476 | 0.482 | 0.494 | 0.513 | 0.528 | 0.537 | 0.538 | 0.541 | 0.544 | 0.545 | 0.546 | 0.547 | 0.554 | 0.563 | 0.57 | 0.565 | 0.551 | 0.53 | 0.505 | 0.475 | 0.441 | 0.433 | 0.408 | 0.383 | 0.363 | 0.346 | 0.331 | 0.319 | 0.309 | 0.302 | 0.296 | 0.291 | 0.288 | 0.285 | 0.282 | 0.279 | 0.278 | 0.276 | 0.275 | 0.275 | 0.276 | 0.278 | 0.28 | 0.282 | 0.285 | 0.286 | 0.288 | 0.289 | 0.292 | 0.296 | 0.299 | 0.299 | 0.298 | 0.296 | 0.291 | 0.282 | 0.27 | 0.256 | 0.24 | 0.222 | 0.204 | 0.186 | 0.164 | 0.142 | 0.12 | 0.102 | 0.087 | 0.077 | 0.071 | 0.064 | 0.056 | 0.047 | 0.038 | 0.029 | 0.021 | 0.016 | 0.013 | 0.013 | 0.015 | 0.021 | 0.028 | 0.034 | 0.043 | 0.056 | 0.073 | 0.094 | 0.122 | 0.162 | 0.213 | 0.27 | 0.328 | 0.379 | 0.413 | 0.431 | 0.436 | 0.443 | 0.451 | 0.459 | 0.47 | 0.484 | 0.499 | 0.509 | 0.515 | 0.518 | 0.532 | 0.55 | 0.565 | 0.571 | 0.575 | 0.579 | 0.582 | 0.577 | 0.566 | 0.548 | 0.525 | 0.497 | 0.469 | 0.458 | 0.435 | 0.413 | 0.392 | 0.376 | 0.362 | 0.348 | 0.334 | 0.324 | 0.317 | 0.31 | 0.305 | 0.299 | 0.294 | 0.291 | 0.289 | 0.289 | 0.289 | 0.288 | 0.287 | 0.286 | 0.286 | 0.285 | 0.284 | 0.283 | 0.28 | 0.276 | 0.276 | 0.277 | 0.278 | 0.28 | 0.284 | 0.292 | 0.301 | 0.309 | 0.314 | 0.31 | 0.303 | 0.291 | 0.276 | 0.26 | 0.242 | 0.225 | 0.207 | 0.193 | 0.183 | 0.174 | 0.169 | 0.167 | 0.16 | 0.149 | 0.135 | 0.125 | 0.116 | 0.112 | 0.108 | 0.106 | 0.103 | 0.105 | 0.11 | 0.117 | 0.125 | 0.132 | 0.14 | 0.15 | 0.169 | 0.202 | 0.24 | 0.285 | 0.33 | 0.374 | 0.405 | 0.426 | 0.44 | 0.452 | 0.461 | 0.47 | 0.48 | 0.493 | 0.508 | 0.519 | 0.523 | 0.52 | 0.52 | 0.52 | 0.524 | 0.526 | 0.53 | 0.535 | 0.54 | 0.541 | 0.536 | 0.524 | 0.507 | 0.487 | 0.465 | 0.442 | 0.42 | 0.402 | 0.383 | 0.367 | 0.352 | 0.339 | 0.326 | 0.317 | 0.31 | 0.305 | 0.3 | 0.295 | 0.291 | 0.288 | 0.285 | 0.283 | 0.281 | 0.28 | 0.279 | 0.28 | 0.279 | 0.276 | 0.274 | 0.273 | 0.27 | 0.266 | 0.261 | 0.259 | 0.26 | 0.262 | 0.268 | 0.274 | 0.278 | 0.281 | 0.286 | 0.287 | 0.286 | 0.278 | 0.267 | 0.249 | 0.232 | 0.217 | 0.203 | 0.189 | 0.171 | 0.159 | 0.152 | 0.15 | 0.146 | 0.136 | 0.123 | 0.111 | 0.103 | 0.097 | 0.092 | 0.09 | 0.088 | 0.091 | 0.094 | 0.098 | 0.1 | 0.102 | 0.109 | 0.123 | 0.145 | 0.177 | 0.215 | 0.259 | 0.304 | 0.349 | 0.385 | 0.412 | 0.431 | 0.444 | 0.453 | 0.461 | 0.474 | 0.492 | 0.51 | 0.522 | 0.526 | 0.526 | 0.53 | 0.536 | 0.544 | 0.549 | 0.555 | 0.563 | 0.567 | 0.562 | 0.549 | 0.528 | 0.504 | 0.475 | 0.448 | 0.429 | 0.404 | 0.381 | 0.362 | 0.344 | 0.33 | 0.319 | 0.311 | 0.304 | 0.298 | 0.293 | 0.289 | 0.287 | 0.284 | 0.282 | 0.281 | 0.279 | 0.279 | 0.278 | 0.279 | 0.28 | 0.282 | 0.285 | 0.29 | 0.297 | 0.304 | 0.312 | 0.319 | 0.327 | 0.333 | 0.338 | 0.339 | 0.336 | 0.33 | 0.321 | 0.31 | 0.296 | 0.28 | 0.262 | 0.24 | 0.217 | 0.192 | 0.169 | 0.147 | 0.128 | 0.113 | 0.102 | 0.094 | 0.087 | 0.08 | 0.072 | 0.062 | 0.052 | 0.045 | 0.04 | 0.038 | 0.039 | 0.043 | 0.047 | 0.053 | 0.06 | 0.07 | 0.083 | 0.101 | 0.126 | 0.158 | 0.201 | 0.254 | 0.315 | 0.378 | 0.434 | 0.472 | 0.49 | 0.497 | 0.503 | 0.512 | 0.52 | 0.527 | 0.536 | 0.548 | 0.559 | 0.566 | 0.57 | 0.585 | 0.606 | 0.625 | 0.631 | 0.624 | 0.613 | 0.6 | 0.587 | 0.57 | 0.548 | 0.52 | 0.492 | 0.464 | 0.452 | 0.429 | 0.407 | 0.387 | 0.37 | 0.356 | 0.342 | 0.329 | 0.319 | 0.31 | 0.304 | 0.298 | 0.293 | 0.289 | 0.286 | 0.283 | 0.282 | 0.282 | 0.282 | 0.281 | 0.281 | 0.281 | 0.282 | 0.285 | 0.287 | 0.29 | 0.292 | 0.295 | 0.299 | 0.305 | 0.312 | 0.32 | 0.328 | 0.337 | 0.343 | 0.346 | 0.342 | 0.335 | 0.326 | 0.313 | 0.3 | 0.281 | 0.263 | 0.242 | 0.225 | 0.211 | 0.201 | 0.195 | 0.19 | 0.182 | 0.173 | 0.16 | 0.15 | 0.142 | 0.134 | 0.128 | 0.124 | 0.125 | 0.129 | 0.133 | 0.137 | 0.142 | 0.152 | 0.166 | 0.185 | 0.209 | 0.242 | 0.283 | 0.329 | 0.376 | 0.423 | 0.461 | 0.484 | 0.495 | 0.506 | 0.516 | 0.525 | 0.531 | 0.539 | 0.549 | 0.559 | 0.565 | 0.567 | 0.567 | 0.572 | 0.576 | 0.58 | 0.575 | 0.567 | 0.557 | 0.548 | 0.535 | 0.518 | 0.499 | 0.481 | 0.461 | 0.444 | 0.423 | 0.404 | 0.385 | 0.368 | 0.354 | 0.338 | 0.326 | 0.314 | 0.308 | 0.301 | 0.296 | 0.29 | 0.287 | 0.285 | 0.283 | 0.282 | 0.279 | 0.278 | 0.278 | 0.278 | 0.277 | 0.275 | 0.276 | 0.279 | 0.282 | 0.282 | 0.282 | 0.285 | 0.29 | 0.294 | 0.302 | 0.31 | 0.318 | 0.321 | 0.326 | 0.329 | 0.327 | 0.32 | 0.306 | 0.295 | 0.284 | 0.272 | 0.253 | 0.23 | 0.212 | 0.203 | 0.197 | 0.195 | 0.188 | 0.177 | 0.161 | 0.15 | 0.141 | 0.136 | 0.127 | 0.122 | 0.118 | 0.119 | 0.122 | 0.125 | 0.13 | 0.138 | 0.15 | 0.167 | 0.186 | 0.218 | 0.263 | 0.317 | 0.368 | 0.414 | 0.452 | 0.477 | 0.493 | 0.504 | 0.519 | 0.53 | 0.541 | 0.556 | 0.572 | 0.586 | 0.589 | 0.59 | 0.593 | 0.6 | 0.605 | 0.605 | 0.6 | 0.589 | 0.576 | 0.559 | 0.54 | 0.518 | 0.492 | 0.465 | 0.438 | 0.393 | 0.367 | 0.344 | 0.326 | 0.31 | 0.297 | 0.287 | 0.28 | 0.273 | 0.268 | 0.264 | 0.26 | 0.258 | 0.256 | 0.254 | 0.253 | 0.252 | 0.251 | 0.251 | 0.253 | 0.256 | 0.259 | 0.265 | 0.274 | 0.284 | 0.298 | 0.313 | 0.335 | 0.357 | 0.377 | 0.389 | 0.395 | 0.393 | 0.386 | 0.378 | 0.369 | 0.359 | 0.343 | 0.323 | 0.298 | 0.272 | 0.248 | 0.224 | 0.201 | 0.182 | 0.166 | 0.157 | 0.149 | 0.143 | 0.135 | 0.124 | 0.112 | 0.102 | 0.093 | 0.087 | 0.084 | 0.085 | 0.091 | 0.098 | 0.107 | 0.116 | 0.13 | 0.147 | 0.17 | 0.197 | 0.234 | 0.282 | 0.343 | 0.409 | 0.475 | 0.53 | 0.565 | 0.579 | 0.58 | 0.579 | 0.582 | 0.587 | 0.596 | 0.61 | 0.621 | 0.63 | 0.632 | 0.633 | 0.635 | 0.638 | 0.636 | 0.627 | 0.611 | 0.596 | 0.579 | 0.561 | 0.539 | 0.514 | 0.487 | 0.459 | 0.43 | 0.415 | 0.392 | 0.371 | 0.351 | 0.335 | 0.321 | 0.308 | 0.298 | 0.289 | 0.281 | 0.276 | 0.271 | 0.266 | 0.263 | 0.26 | 0.259 | 0.258 | 0.257 | 0.256 | 0.256 | 0.256 | 0.257 | 0.259 | 0.262 | 0.266 | 0.273 | 0.279 | 0.288 | 0.299 | 0.314 | 0.33 | 0.345 | 0.359 | 0.375 | 0.388 | 0.397 | 0.395 | 0.39 | 0.381 | 0.365 | 0.346 | 0.326 | 0.307 | 0.286 | 0.266 | 0.25 | 0.24 | 0.233 | 0.228 | 0.22 | 0.213 | 0.197 | 0.184 | 0.173 | 0.171 | 0.17 | 0.17 | 0.174 | 0.18 | 0.184 | 0.188 | 0.195 | 0.205 | 0.218 | 0.235 | 0.258 | 0.289 | 0.33 | 0.384 | 0.436 | 0.484 | 0.524 | 0.555 | 0.569 | 0.571 | 0.571 | 0.574 | 0.58 | 0.59 | 0.603 | 0.617 | 0.624 | 0.622 | 0.605 | 0.587 | 0.569 | 0.562 | 0.551 | 0.543 | 0.533 | 0.525 | 0.513 | 0.496 | 0.475 | 0.454 | 0.431 | 0.41 | 0.39 | 0.368 | 0.348 | 0.329 | 0.319 | 0.307 | 0.296 | 0.286 | 0.279 | 0.274 | 0.268 | 0.263 | 0.26 | 0.258 | 0.255 | 0.253 | 0.252 | 0.252 | 0.251 | 0.249 | 0.248 | 0.25 | 0.254 | 0.257 | 0.26 | 0.264 | 0.27 | 0.28 | 0.291 | 0.302 | 0.319 | 0.338 | 0.357 | 0.371 | 0.381 | 0.386 | 0.39 | 0.386 | 0.374 | 0.359 | 0.343 | 0.328 | 0.307 | 0.288 | 0.274 | 0.267 | 0.261 | 0.258 | 0.254 | 0.244 | 0.231 | 0.22 | 0.212 | 0.204 | 0.195 | 0.189 | 0.188 | 0.188 | 0.19 | 0.193 | 0.198 | 0.207 | 0.219 | 0.237 | 0.264 | 0.302 | 0.349 | 0.405 | 0.461 | 0.515 | 0.554 | 0.576 | 0.585 | 0.589 | 0.596 | 0.604 | 0.613 | 0.632 | 0.651 | 0.665 | 0.661 | 0.659 | 0.649 | 0.634 | 0.614 | 0.602 | 0.592 | 0.581 | 0.563 | 0.541 | 0.515 | 0.486 | 0.456 | 0.426 | 0.393 | 0.411 | 0.384 | 0.359 | 0.339 | 0.32 | 0.306 | 0.294 | 0.285 | 0.278 | 0.272 | 0.268 | 0.265 | 0.262 | 0.26 | 0.258 | 0.258 | 0.256 | 0.256 | 0.257 | 0.26 | 0.264 | 0.269 | 0.277 | 0.288 | 0.299 | 0.311 | 0.328 | 0.352 | 0.379 | 0.405 | 0.426 | 0.443 | 0.453 | 0.455 | 0.455 | 0.453 | 0.447 | 0.438 | 0.425 | 0.407 | 0.387 | 0.365 | 0.344 | 0.322 | 0.303 | 0.286 | 0.274 | 0.267 | 0.263 | 0.258 | 0.249 | 0.238 | 0.228 | 0.22 | 0.214 | 0.209 | 0.208 | 0.211 | 0.218 | 0.228 | 0.239 | 0.253 | 0.27 | 0.294 | 0.325 | 0.365 | 0.417 | 0.484 | 0.556 | 0.626 | 0.681 | 0.713 | 0.725 | 0.727 | 0.733 | 0.735 | 0.738 | 0.737 | 0.741 | 0.735 | 0.724 | 0.705 | 0.689 | 0.683 | 0.684 | 0.683 | 0.672 | 0.652 | 0.633 | 0.612 | 0.59 | 0.565 | 0.54 | 0.511 | 0.481 | 0.45 | 0.439 | 0.414 | 0.39 | 0.37 | 0.351 | 0.335 | 0.321 | 0.308 | 0.298 | 0.288 | 0.283 | 0.278 | 0.272 | 0.268 | 0.265 | 0.264 | 0.263 | 0.263 | 0.263 | 0.263 | 0.263 | 0.264 | 0.268 | 0.274 | 0.279 | 0.284 | 0.289 | 0.298 | 0.311 | 0.329 | 0.353 | 0.384 | 0.415 | 0.444 | 0.471 | 0.489 | 0.501 | 0.506 | 0.504 | 0.487 | 0.467 | 0.445 | 0.432 | 0.416 | 0.402 | 0.392 | 0.385 | 0.382 | 0.379 | 0.375 | 0.367 | 0.357 | 0.344 | 0.333 | 0.324 | 0.321 | 0.321 | 0.324 | 0.326 | 0.33 | 0.338 | 0.347 | 0.359 | 0.373 | 0.393 | 0.417 | 0.45 | 0.5 | 0.558 | 0.621 | 0.678 | 0.72 | 0.744 | 0.755 | 0.762 | 0.759 | 0.754 | 0.746 | 0.746 | 0.738 | 0.727 | 0.707 | 0.687 | 0.664 | 0.645 | 0.629 | 0.618 | 0.605 | 0.591 | 0.578 | 0.567 | 0.555 | 0.536 | 0.516 | 0.493 | 0.47 | 0.444 | 0.42 | 0.397 | 0.375 | 0.355 | 0.338 | 0.324 | 0.308 | 0.297 | 0.289 | 0.282 | 0.276 | 0.272 | 0.269 | 0.266 | 0.262 | 0.26 | 0.258 | 0.258 | 0.257 | 0.258 | 0.26 | 0.262 | 0.268 | 0.272 | 0.278 | 0.283 | 0.292 | 0.305 | 0.322 | 0.34 | 0.364 | 0.391 | 0.419 | 0.444 | 0.466 | 0.483 | 0.497 | 0.502 | 0.495 | 0.484 | 0.47 | 0.457 | 0.44 | 0.427 | 0.418 | 0.415 | 0.412 | 0.412 | 0.407 | 0.399 | 0.388 | 0.377 | 0.367 | 0.359 | 0.355 | 0.351 | 0.351 | 0.351 | 0.359 | 0.365 | 0.375 | 0.384 | 0.4 | 0.418 | 0.445 | 0.483 | 0.536 | 0.6 | 0.664 | 0.72 | 0.76 | 0.778 | 0.778 | 0.776 | 0.775 | 0.778 | 0.773 | 0.768 | 0.763 | 0.753 | 0.733 | 0.706 | 0.682 | 0.666 | 0.653 | 0.639 | 0.627 | 0.612 | 0.596 | 0.572 | 0.546 | 0.515 | 0.482 | 0.451 | 0.422 | 0.432 | 0.404 | 0.378 | 0.356 | 0.336 | 0.321 | 0.308 | 0.299 | 0.291 | 0.284 | 0.28 | 0.278 | 0.277 | 0.276 | 0.275 | 0.276 | 0.274 | 0.272 | 0.272 | 0.275 | 0.281 | 0.288 | 0.298 | 0.312 | 0.327 | 0.343 | 0.362 | 0.388 | 0.419 | 0.449 | 0.473 | 0.488 | 0.495 | 0.495 | 0.491 | 0.488 | 0.484 | 0.477 | 0.462 | 0.446 | 0.428 | 0.412 | 0.396 | 0.381 | 0.368 | 0.36 | 0.357 | 0.358 | 0.36 | 0.361 | 0.357 | 0.355 | 0.354 | 0.357 | 0.362 | 0.367 | 0.372 | 0.38 | 0.393 | 0.405 | 0.42 | 0.437 | 0.462 | 0.487 | 0.519 | 0.561 | 0.624 | 0.703 | 0.789 | 0.866 | 0.915 | 0.927 | 0.911 | 0.883 | 0.86 | 0.84 | 0.823 | 0.807 | 0.798 | 0.785 | 0.769 | 0.749 | 0.732 | 0.727 | 0.727 | 0.727 | 0.716 | 0.697 | 0.68 | 0.659 | 0.634 | 0.603 | 0.572 | 0.538 | 0.505 | 0.471 | 0.462 | 0.435 | 0.411 | 0.392 | 0.374 | 0.358 | 0.342 | 0.328 | 0.315 | 0.304 | 0.297 | 0.291 | 0.289 | 0.286 | 0.284 | 0.282 | 0.28 | 0.279 | 0.277 | 0.278 | 0.279 | 0.282 | 0.287 | 0.294 | 0.3 | 0.309 | 0.318 | 0.334 | 0.353 | 0.376 | 0.4 | 0.43 | 0.465 | 0.499 | 0.525 | 0.545 | 0.557 | 0.558 | 0.549 | 0.541 | 0.534 | 0.531 | 0.521 | 0.512 | 0.502 | 0.502 | 0.506 | 0.508 | 0.512 | 0.514 | 0.512 | 0.502 | 0.495 | 0.496 | 0.503 | 0.512 | 0.515 | 0.516 | 0.519 | 0.526 | 0.537 | 0.551 | 0.574 | 0.595 | 0.62 | 0.647 | 0.69 | 0.753 | 0.827 | 0.901 | 0.951 | 0.965 | 0.949 | 0.922 | 0.894 | 0.867 | 0.845 | 0.828 | 0.82 | 0.807 | 0.788 | 0.762 | 0.735 | 0.712 | 0.692 | 0.674 | 0.66 | 0.648 | 0.636 | 0.623 | 0.608 | 0.589 | 0.566 | 0.543 | 0.519 | 0.493 | 0.468 | 0.444 | 0.419 | 0.395 | 0.376 | 0.358 | 0.341 | 0.326 | 0.314 | 0.307 | 0.3 | 0.295 | 0.29 | 0.285 | 0.284 | 0.283 | 0.281 | 0.278 | 0.275 | 0.275 | 0.277 | 0.28 | 0.284 | 0.287 | 0.292 | 0.299 | 0.306 | 0.318 | 0.332 | 0.349 | 0.369 | 0.395 | 0.426 | 0.461 | 0.493 | 0.521 | 0.543 | 0.557 | 0.565 | 0.563 | 0.558 | 0.552 | 0.549 | 0.546 | 0.542 | 0.532 | 0.524 | 0.525 | 0.531 | 0.535 | 0.538 | 0.536 | 0.535 | 0.532 | 0.533 | 0.534 | 0.536 | 0.536 | 0.539 | 0.542 | 0.549 | 0.559 | 0.574 | 0.588 | 0.609 | 0.641 | 0.687 | 0.751 | 0.825 | 0.896 | 0.942 | 0.954 | 0.943 | 0.921 | 0.9 | 0.875 | 0.847 | 0.822 | 0.814 | 0.809 | 0.805 | 0.781 | 0.757 | 0.732 | 0.713 | 0.701 | 0.687 | 0.674 | 0.656 | 0.636 | 0.608 | 0.576 | 0.542 | 0.506 | 0.471 | 0.44 | 0.467 | 0.433 | 0.405 | 0.379 | 0.357 | 0.341 | 0.326 | 0.315 | 0.305 | 0.298 | 0.293 | 0.289 | 0.286 | 0.285 | 0.283 | 0.284 | 0.282 | 0.281 | 0.28 | 0.282 | 0.288 | 0.295 | 0.305 | 0.316 | 0.328 | 0.343 | 0.36 | 0.384 | 0.411 | 0.439 | 0.467 | 0.491 | 0.511 | 0.526 | 0.54 | 0.552 | 0.562 | 0.566 | 0.564 | 0.557 | 0.548 | 0.539 | 0.526 | 0.511 | 0.498 | 0.489 | 0.486 | 0.489 | 0.492 | 0.493 | 0.489 | 0.485 | 0.483 | 0.484 | 0.486 | 0.488 | 0.49 | 0.495 | 0.505 | 0.515 | 0.527 | 0.543 | 0.563 | 0.583 | 0.611 | 0.65 | 0.709 | 0.781 | 0.854 | 0.917 | 0.955 | 0.965 | 0.953 | 0.931 | 0.91 | 0.889 | 0.868 | 0.852 | 0.845 | 0.834 | 0.819 | 0.799 | 0.78 | 0.772 | 0.772 | 0.771 | 0.76 | 0.739 | 0.719 | 0.697 | 0.672 | 0.645 | 0.616 | 0.583 | 0.55 | 0.51 | 0.488 | 0.455 | 0.431 | 0.408 | 0.39 | 0.371 | 0.354 | 0.339 | 0.326 | 0.313 | 0.304 | 0.297 | 0.293 | 0.289 | 0.286 | 0.286 | 0.284 | 0.281 | 0.278 | 0.278 | 0.281 | 0.284 | 0.29 | 0.297 | 0.306 | 0.316 | 0.325 | 0.34 | 0.357 | 0.379 | 0.403 | 0.429 | 0.459 | 0.49 | 0.524 | 0.561 | 0.594 | 0.617 | 0.625 | 0.623 | 0.618 | 0.612 | 0.606 | 0.604 | 0.599 | 0.597 | 0.596 | 0.604 | 0.608 | 0.606 | 0.603 | 0.605 | 0.609 | 0.61 | 0.618 | 0.623 | 0.626 | 0.627 | 0.633 | 0.64 | 0.651 | 0.664 | 0.68 | 0.691 | 0.708 | 0.742 | 0.791 | 0.847 | 0.903 | 0.954 | 0.991 | 0.998 | 0.985 | 0.959 | 0.936 | 0.909 | 0.884 | 0.866 | 0.856 | 0.844 | 0.828 | 0.807 | 0.785 | 0.764 | 0.747 | 0.731 | 0.715 | 0.697 | 0.682 | 0.667 | 0.658 | 0.643 | 0.624 | 0.602 | 0.579 | 0.527 | 0.495 | 0.465 | 0.439 | 0.414 | 0.392 | 0.37 | 0.354 | 0.338 | 0.326 | 0.316 | 0.309 | 0.304 | 0.3 | 0.297 | 0.292 | 0.288 | 0.285 | 0.284 | 0.283 | 0.283 | 0.285 | 0.286 | 0.289 | 0.292 | 0.297 | 0.304 | 0.312 | 0.325 | 0.339 | 0.355 | 0.371 | 0.394 | 0.426 | 0.465 | 0.51 | 0.553 | 0.587 | 0.612 | 0.63 | 0.642 | 0.647 | 0.643 | 0.638 | 0.634 | 0.632 | 0.627 | 0.629 | 0.633 | 0.644 | 0.648 | 0.648 | 0.641 | 0.635 | 0.629 | 0.627 | 0.625 | 0.63 | 0.635 | 0.639 | 0.64 | 0.639 | 0.647 | 0.656 | 0.669 | 0.686 | 0.717 | 0.766 | 0.825 | 0.891 | 0.947 | 0.987 | 1 | 1 | 0.982 | 0.964 | 0.934 | 0.914 | 0.895 | 0.888 | 0.876 | 0.865 | 0.84 | 0.814 | 0.788 | 0.771 | 0.758 | 0.744 | 0.727 | 0.708 | 0.684 | 0.655 | 0.62 | 0.585 | 0.547 | 0.51 | 0.472
E2A | -3456 | 0.616 | 0.604 | 0.591 | 0.579 | 0.566 | 0.555 | 0.547 | 0.542 | 0.538 | 0.533 | 0.529 | 0.526 | 0.523 | 0.518 | 0.514 | 0.511 | 0.51 | 0.508 | 0.509 | 0.512 | 0.52 | 0.53 | 0.544 | 0.563 | 0.588 | 0.617 | 0.653 | 0.695 | 0.737 | 0.782 | 0.83 | 0.881 | 0.92 | 0.943 | 0.954 | 0.96 | 0.96 | 0.954 | 0.945 | 0.938 | 0.928 | 0.915 | 0.903 | 0.894 | 0.891 | 0.888 | 0.885 | 0.88 | 0.871 | 0.858 | 0.846 | 0.84 | 0.838 | 0.839 | 0.84 | 0.84 | 0.84 | 0.839 | 0.843 | 0.844 | 0.844 | 0.845 | 0.854 | 0.869 | 0.887 | 0.906 | 0.931 | 0.954 | 0.975 | 0.988 | 0.999 | 1 | 0.997 | 0.991 | 0.988 | 0.987 | 0.982 | 0.975 | 0.965 | 0.951 | 0.93 | 0.905 | 0.88 | 0.857 | 0.836 | 0.816 | 0.799 | 0.779 | 0.756 | 0.734 | 0.715 | 0.702 | 0.69 | 0.676 | 0.658 | 0.644 | 0.643 | 0.63 | 0.616 | 0.603 | 0.594 | 0.584 | 0.575 | 0.566 | 0.559 | 0.553 | 0.547 | 0.542 | 0.537 | 0.532 | 0.528 | 0.524 | 0.522 | 0.521 | 0.52 | 0.521 | 0.526 | 0.533 | 0.542 | 0.555 | 0.571 | 0.596 | 0.621 | 0.652 | 0.679 | 0.704 | 0.731 | 0.766 | 0.795 | 0.81 | 0.816 | 0.827 | 0.837 | 0.847 | 0.849 | 0.848 | 0.845 | 0.837 | 0.831 | 0.827 | 0.826 | 0.826 | 0.824 | 0.819 | 0.812 | 0.804 | 0.798 | 0.794 | 0.791 | 0.787 | 0.782 | 0.778 | 0.776 | 0.776 | 0.776 | 0.779 | 0.779 | 0.779 | 0.783 | 0.792 | 0.802 | 0.816 | 0.838 | 0.864 | 0.89 | 0.913 | 0.931 | 0.944 | 0.951 | 0.956 | 0.955 | 0.949 | 0.939 | 0.932 | 0.923 | 0.912 | 0.894 | 0.874 | 0.854 | 0.836 | 0.815 | 0.797 | 0.78 | 0.763 | 0.747 | 0.73 | 0.717 | 0.701 | 0.688 | 0.672 | 0.656 | 0.637 | 0.619 | 0.608 | 0.594 | 0.581 | 0.568 | 0.558 | 0.549 | 0.541 | 0.536 | 0.53 | 0.526 | 0.523 | 0.519 | 0.513 | 0.507 | 0.504 | 0.504 | 0.502 | 0.502 | 0.502 | 0.507 | 0.513 | 0.524 | 0.537 | 0.553 | 0.576 | 0.6 | 0.628 | 0.651 | 0.671 | 0.687 | 0.702 | 0.709 | 0.706 | 0.697 | 0.69 | 0.689 | 0.692 | 0.696 | 0.698 | 0.698 | 0.697 | 0.697 | 0.698 | 0.697 | 0.692 | 0.69 | 0.691 | 0.693 | 0.693 | 0.695 | 0.698 | 0.697 | 0.69 | 0.681 | 0.673 | 0.667 | 0.665 | 0.666 | 0.67 | 0.671 | 0.671 | 0.675 | 0.685 | 0.695 | 0.71 | 0.735 | 0.768 | 0.804 | 0.833 | 0.859 | 0.88 | 0.898 | 0.909 | 0.913 | 0.91 | 0.906 | 0.896 | 0.885 | 0.872 | 0.857 | 0.84 | 0.82 | 0.8 | 0.782 | 0.766 | 0.753 | 0.735 | 0.717 | 0.696 | 0.677 | 0.66 | 0.645 | 0.628 | 0.611 | 0.597 | 0.597 | 0.586 | 0.576 | 0.565 | 0.557 | 0.551 | 0.545 | 0.54 | 0.536 | 0.532 | 0.528 | 0.525 | 0.522 | 0.517 | 0.512 | 0.51 | 0.509 | 0.506 | 0.505 | 0.507 | 0.516 | 0.528 | 0.543 | 0.563 | 0.589 | 0.619 | 0.654 | 0.691 | 0.731 | 0.771 | 0.814 | 0.857 | 0.89 | 0.912 | 0.923 | 0.929 | 0.926 | 0.918 | 0.906 | 0.896 | 0.884 | 0.872 | 0.861 | 0.855 | 0.851 | 0.849 | 0.847 | 0.841 | 0.83 | 0.815 | 0.802 | 0.795 | 0.794 | 0.794 | 0.793 | 0.79 | 0.79 | 0.79 | 0.793 | 0.792 | 0.79 | 0.789 | 0.796 | 0.807 | 0.822 | 0.836 | 0.852 | 0.866 | 0.878 | 0.887 | 0.902 | 0.917 | 0.931 | 0.941 | 0.95 | 0.956 | 0.955 | 0.948 | 0.938 | 0.924 | 0.905 | 0.884 | 0.861 | 0.838 | 0.818 | 0.797 | 0.779 | 0.76 | 0.739 | 0.716 | 0.696 | 0.684 | 0.672 | 0.656 | 0.637 | 0.622 | 0.631 | 0.62 | 0.606 | 0.594 | 0.583 | 0.575 | 0.567 | 0.559 | 0.553 | 0.547 | 0.542 | 0.538 | 0.533 | 0.527 | 0.522 | 0.521 | 0.519 | 0.516 | 0.514 | 0.515 | 0.519 | 0.527 | 0.539 | 0.556 | 0.574 | 0.598 | 0.624 | 0.654 | 0.681 | 0.706 | 0.726 | 0.75 | 0.766 | 0.779 | 0.786 | 0.794 | 0.801 | 0.8 | 0.796 | 0.79 | 0.783 | 0.777 | 0.776 | 0.776 | 0.775 | 0.769 | 0.766 | 0.76 | 0.754 | 0.745 | 0.736 | 0.727 | 0.719 | 0.715 | 0.708 | 0.702 | 0.697 | 0.697 | 0.702 | 0.705 | 0.706 | 0.705 | 0.709 | 0.714 | 0.72 | 0.727 | 0.742 | 0.762 | 0.784 | 0.801 | 0.821 | 0.845 | 0.873 | 0.896 | 0.91 | 0.917 | 0.915 | 0.906 | 0.891 | 0.877 | 0.861 | 0.842 | 0.821 | 0.8 | 0.784 | 0.77 | 0.759 | 0.745 | 0.729 | 0.71 | 0.695 | 0.677 | 0.658 | 0.637 | 0.617 | 0.603 | 0.588 | 0.577 | 0.567 | 0.559 | 0.55 | 0.541 | 0.534 | 0.53 | 0.529 | 0.527 | 0.522 | 0.515 | 0.508 | 0.501 | 0.495 | 0.495 | 0.496 | 0.494 | 0.493 | 0.494 | 0.499 | 0.506 | 0.517 | 0.528 | 0.543 | 0.561 | 0.58 | 0.599 | 0.619 | 0.639 | 0.655 | 0.666 | 0.673 | 0.672 | 0.67 | 0.665 | 0.666 | 0.664 | 0.664 | 0.659 | 0.656 | 0.652 | 0.652 | 0.653 | 0.651 | 0.648 | 0.643 | 0.64 | 0.642 | 0.64 | 0.636 | 0.628 | 0.624 | 0.621 | 0.617 | 0.61 | 0.606 | 0.604 | 0.607 | 0.611 | 0.614 | 0.619 | 0.621 | 0.628 | 0.633 | 0.645 | 0.668 | 0.695 | 0.721 | 0.742 | 0.77 | 0.803 | 0.838 | 0.862 | 0.878 | 0.881 | 0.878 | 0.867 | 0.856 | 0.842 | 0.831 | 0.816 | 0.798 | 0.777 | 0.761 | 0.749 | 0.738 | 0.722 | 0.704 | 0.681 | 0.661 | 0.641 | 0.622 | 0.604 | 0.587 | 0.576 | 0.568 | 0.557 | 0.544 | 0.533 | 0.527 | 0.521 | 0.514 | 0.509 | 0.506 | 0.502 | 0.497 | 0.494 | 0.494 | 0.49 | 0.484 | 0.48 | 0.479 | 0.477 | 0.475 | 0.477 | 0.484 | 0.497 | 0.512 | 0.533 | 0.558 | 0.588 | 0.62 | 0.652 | 0.684 | 0.714 | 0.749 | 0.785 | 0.815 | 0.834 | 0.842 | 0.846 | 0.843 | 0.837 | 0.825 | 0.814 | 0.803 | 0.794 | 0.786 | 0.781 | 0.778 | 0.778 | 0.778 | 0.775 | 0.767 | 0.754 | 0.74 | 0.732 | 0.73 | 0.731 | 0.73 | 0.73 | 0.728 | 0.73 | 0.73 | 0.729 | 0.725 | 0.723 | 0.725 | 0.733 | 0.745 | 0.757 | 0.771 | 0.782 | 0.792 | 0.797 | 0.805 | 0.812 | 0.822 | 0.832 | 0.847 | 0.864 | 0.881 | 0.887 | 0.884 | 0.873 | 0.858 | 0.842 | 0.821 | 0.801 | 0.781 | 0.759 | 0.739 | 0.718 | 0.698 | 0.679 | 0.662 | 0.65 | 0.638 | 0.624 | 0.605 | 0.59 | 0.598 | 0.589 | 0.578 | 0.564 | 0.555 | 0.545 | 0.536 | 0.528 | 0.522 | 0.516 | 0.508 | 0.503 | 0.499 | 0.494 | 0.487 | 0.484 | 0.481 | 0.48 | 0.478 | 0.482 | 0.486 | 0.493 | 0.501 | 0.513 | 0.531 | 0.556 | 0.583 | 0.61 | 0.633 | 0.652 | 0.671 | 0.694 | 0.709 | 0.72 | 0.726 | 0.736 | 0.741 | 0.737 | 0.729 | 0.722 | 0.716 | 0.711 | 0.712 | 0.714 | 0.717 | 0.715 | 0.71 | 0.707 | 0.701 | 0.696 | 0.686 | 0.677 | 0.671 | 0.669 | 0.665 | 0.66 | 0.656 | 0.654 | 0.653 | 0.653 | 0.656 | 0.659 | 0.664 | 0.668 | 0.672 | 0.678 | 0.693 | 0.712 | 0.73 | 0.743 | 0.756 | 0.778 | 0.805 | 0.831 | 0.851 | 0.867 | 0.879 | 0.881 | 0.873 | 0.861 | 0.848 | 0.831 | 0.811 | 0.789 | 0.773 | 0.756 | 0.742 | 0.725 | 0.709 | 0.692 | 0.677 | 0.661 | 0.645 | 0.626 | 0.606 | 0.59 | 0.574 | 0.56 | 0.548 | 0.538 | 0.531 | 0.524 | 0.513 | 0.513 | 0.508 | 0.506 | 0.502 | 0.494 | 0.488 | 0.478 | 0.473 | 0.469 | 0.468 | 0.465 | 0.463 | 0.464 | 0.469 | 0.476 | 0.483 | 0.495 | 0.51 | 0.528 | 0.548 | 0.567 | 0.584 | 0.595 | 0.603 | 0.609 | 0.613 | 0.614 | 0.613 | 0.615 | 0.614 | 0.61 | 0.605 | 0.601 | 0.6 | 0.595 | 0.596 | 0.597 | 0.599 | 0.597 | 0.597 | 0.596 | 0.596 | 0.592 | 0.589 | 0.585 | 0.582 | 0.575 | 0.571 | 0.568 | 0.567 | 0.566 | 0.564 | 0.566 | 0.565 | 0.565 | 0.564 | 0.57 | 0.577 | 0.585 | 0.597 | 0.616 | 0.637 | 0.659 | 0.683 | 0.713 | 0.742 | 0.764 | 0.779 | 0.792 | 0.803 | 0.807 | 0.804 | 0.796 | 0.785 | 0.773 | 0.758 | 0.744 | 0.732 | 0.72 | 0.706 | 0.688 | 0.671 | 0.652 | 0.633 | 0.611 | 0.591 | 0.573 | 0.559 | 0.55 | 0.533 | 0.52 | 0.507 | 0.496 | 0.49 | 0.483 | 0.474 | 0.468 | 0.463 | 0.46 | 0.456 | 0.456 | 0.454 | 0.451 | 0.445 | 0.442 | 0.441 | 0.441 | 0.439 | 0.439 | 0.443 | 0.453 | 0.465 | 0.484 | 0.505 | 0.531 | 0.557 | 0.583 | 0.61 | 0.639 | 0.674 | 0.71 | 0.735 | 0.752 | 0.758 | 0.763 | 0.761 | 0.756 | 0.746 | 0.736 | 0.726 | 0.715 | 0.707 | 0.701 | 0.7 | 0.701 | 0.703 | 0.704 | 0.7 | 0.69 | 0.678 | 0.67 | 0.665 | 0.664 | 0.661 | 0.658 | 0.657 | 0.658 | 0.659 | 0.658 | 0.656 | 0.653 | 0.653 | 0.655 | 0.661 | 0.67 | 0.681 | 0.693 | 0.702 | 0.711 | 0.718 | 0.724 | 0.728 | 0.729 | 0.734 | 0.739 | 0.744 | 0.745 | 0.741 | 0.737 | 0.732 | 0.73 | 0.729 | 0.73 | 0.726 | 0.717 | 0.703 | 0.686 | 0.668 | 0.651 | 0.634 | 0.618 | 0.604 | 0.591 | 0.576 | 0.559 | 0.569 | 0.553 | 0.538 | 0.524 | 0.514 | 0.505 | 0.497 | 0.492 | 0.484 | 0.477 | 0.471 | 0.468 | 0.465 | 0.459 | 0.453 | 0.449 | 0.449 | 0.449 | 0.447 | 0.446 | 0.449 | 0.456 | 0.465 | 0.477 | 0.493 | 0.513 | 0.533 | 0.55 | 0.567 | 0.586 | 0.605 | 0.624 | 0.638 | 0.647 | 0.651 | 0.659 | 0.665 | 0.664 | 0.661 | 0.654 | 0.649 | 0.638 | 0.632 | 0.629 | 0.629 | 0.631 | 0.633 | 0.632 | 0.629 | 0.62 | 0.611 | 0.598 | 0.591 | 0.585 | 0.58 | 0.577 | 0.576 | 0.576 | 0.575 | 0.573 | 0.571 | 0.57 | 0.573 | 0.577 | 0.58 | 0.587 | 0.6 | 0.616 | 0.627 | 0.637 | 0.647 | 0.664 | 0.684 | 0.7 | 0.711 | 0.712 | 0.71 | 0.706 | 0.703 | 0.703 | 0.705 | 0.71 | 0.714 | 0.715 | 0.712 | 0.705 | 0.694 | 0.679 | 0.664 | 0.648 | 0.629 | 0.609 | 0.593 | 0.58 | 0.568 | 0.562 | 0.549 | 0.536 | 0.522 | 0.511 | 0.506 | 0.498 | 0.489 | 0.481 | 0.475 | 0.471 | 0.468 | 0.464 | 0.463 | 0.456 | 0.449 | 0.445 | 0.443 | 0.443 | 0.44 | 0.439 | 0.442 | 0.45 | 0.458 | 0.467 | 0.477 | 0.491 | 0.509 | 0.527 | 0.546 | 0.56 | 0.57 | 0.575 | 0.578 | 0.577 | 0.574 | 0.571 | 0.571 | 0.569 | 0.566 | 0.56 | 0.554 | 0.547 | 0.543 | 0.542 | 0.542 | 0.542 | 0.539 | 0.536 | 0.536 | 0.533 | 0.53 | 0.525 | 0.519 | 0.513 | 0.506 | 0.505 | 0.504 | 0.505 | 0.506 | 0.507 | 0.505 | 0.504 | 0.505 | 0.509 | 0.514 | 0.522 | 0.533 | 0.552 | 0.573 | 0.597 | 0.622 | 0.647 | 0.669 | 0.681 | 0.689 | 0.694 | 0.699 | 0.698 | 0.692 | 0.688 | 0.69 | 0.693 | 0.696 | 0.696 | 0.694 | 0.686 | 0.674 | 0.659 | 0.641 | 0.625 | 0.608 | 0.588 | 0.568 | 0.551 | 0.535 | 0.523 | 0.544 | 0.528 | 0.515 | 0.504 | 0.497 | 0.49 | 0.484 | 0.479 | 0.475 | 0.47 | 0.465 | 0.462 | 0.459 | 0.454 | 0.45 | 0.448 | 0.448 | 0.447 | 0.443 | 0.442 | 0.444 | 0.449 | 0.454 | 0.462 | 0.475 | 0.497 | 0.525 | 0.556 | 0.586 | 0.616 | 0.651 | 0.685 | 0.713 | 0.732 | 0.741 | 0.747 | 0.746 | 0.742 | 0.733 | 0.725 | 0.718 | 0.711 | 0.704 | 0.701 | 0.703 | 0.707 | 0.71 | 0.714 | 0.715 | 0.708 | 0.693 | 0.681 | 0.675 | 0.675 | 0.675 | 0.674 | 0.673 | 0.674 | 0.675 | 0.675 | 0.671 | 0.667 | 0.668 | 0.672 | 0.679 | 0.688 | 0.7 | 0.712 | 0.719 | 0.723 | 0.729 | 0.734 | 0.735 | 0.732 | 0.732 | 0.736 | 0.742 | 0.745 | 0.743 | 0.736 | 0.726 | 0.712 | 0.699 | 0.691 | 0.687 | 0.688 | 0.686 | 0.682 | 0.673 | 0.662 | 0.647 | 0.633 | 0.618 | 0.603 | 0.589 | 0.569 | 0.549 | 0.531 | 0.538 | 0.528 | 0.521 | 0.515 | 0.507 | 0.499 | 0.494 | 0.488 | 0.484 | 0.479 | 0.474 | 0.468 | 0.464 | 0.462 | 0.462 | 0.462 | 0.462 | 0.461 | 0.461 | 0.461 | 0.462 | 0.466 | 0.474 | 0.49 | 0.512 | 0.533 | 0.55 | 0.568 | 0.591 | 0.614 | 0.629 | 0.636 | 0.642 | 0.649 | 0.653 | 0.653 | 0.647 | 0.643 | 0.64 | 0.637 | 0.637 | 0.635 | 0.637 | 0.638 | 0.639 | 0.64 | 0.64 | 0.636 | 0.631 | 0.622 | 0.621 | 0.616 | 0.615 | 0.609 | 0.605 | 0.604 | 0.603 | 0.602 | 0.599 | 0.599 | 0.6 | 0.6 | 0.601 | 0.605 | 0.617 | 0.634 | 0.649 | 0.658 | 0.667 | 0.682 | 0.7 | 0.718 | 0.73 | 0.74 | 0.743 | 0.743 | 0.737 | 0.728 | 0.717 | 0.704 | 0.693 | 0.688 | 0.69 | 0.692 | 0.691 | 0.689 | 0.683 | 0.674 | 0.661 | 0.647 | 0.629 | 0.613 | 0.599 | 0.578 | 0.568 | 0.552 | 0.536 | 0.522 | 0.515 | 0.509 | 0.501 | 0.492 | 0.484 | 0.477 | 0.472 | 0.469 | 0.465 | 0.459 | 0.451 | 0.447 | 0.448 | 0.447 | 0.443 | 0.44 | 0.442 | 0.445 | 0.446 | 0.446 | 0.45 | 0.46 | 0.48 | 0.499 | 0.517 | 0.529 | 0.539 | 0.545 | 0.546 | 0.546 | 0.547 | 0.546 | 0.545 | 0.543 | 0.543 | 0.541 | 0.541 | 0.539 | 0.54 | 0.54 | 0.542 | 0.542 | 0.542 | 0.545 | 0.549 | 0.551 | 0.548 | 0.542 | 0.535 | 0.525 | 0.517 | 0.512 | 0.509 | 0.51 | 0.513 | 0.517 | 0.516 | 0.515 | 0.518 | 0.522 | 0.527 | 0.53 | 0.54 | 0.559 | 0.58 | 0.602 | 0.622 | 0.644 | 0.666 | 0.683 | 0.696 | 0.702 | 0.705 | 0.706 | 0.703 | 0.694 | 0.682 | 0.675 | 0.67 | 0.667 | 0.666 | 0.667 | 0.665 | 0.659 | 0.652 | 0.639 | 0.624 | 0.605 | 0.583 | 0.565 | 0.547 | 0.529 | 0.579 | 0.563 | 0.55 | 0.537 | 0.527 | 0.517 | 0.507 | 0.499 | 0.493 | 0.489 | 0.486 | 0.484 | 0.481 | 0.475 | 0.469 | 0.465 | 0.463 | 0.461 | 0.458 | 0.454 | 0.453 | 0.454 | 0.457 | 0.464 | 0.477 | 0.499 | 0.528 | 0.56 | 0.595 | 0.628 | 0.664 | 0.7 | 0.732 | 0.756 | 0.77 | 0.777 | 0.776 | 0.772 | 0.765 | 0.76 | 0.756 | 0.751 | 0.747 | 0.746 | 0.749 | 0.753 | 0.755 | 0.758 | 0.755 | 0.747 | 0.734 | 0.725 | 0.723 | 0.726 | 0.728 | 0.728 | 0.727 | 0.729 | 0.732 | 0.731 | 0.727 | 0.725 | 0.728 | 0.733 | 0.739 | 0.747 | 0.757 | 0.764 | 0.769 | 0.769 | 0.771 | 0.772 | 0.774 | 0.774 | 0.777 | 0.781 | 0.784 | 0.783 | 0.778 | 0.768 | 0.756 | 0.744 | 0.732 | 0.721 | 0.71 | 0.7 | 0.691 | 0.687 | 0.685 | 0.683 | 0.677 | 0.667 | 0.655 | 0.64 | 0.624 | 0.601 | 0.589 | 0.571 | 0.558 | 0.546 | 0.536 | 0.523 | 0.514 | 0.506 | 0.502 | 0.497 | 0.494 | 0.489 | 0.484 | 0.476 | 0.47 | 0.466 | 0.464 | 0.462 | 0.458 | 0.453 | 0.451 | 0.45 | 0.45 | 0.452 | 0.46 | 0.479 | 0.503 | 0.529 | 0.55 | 0.57 | 0.591 | 0.613 | 0.628 | 0.639 | 0.648 | 0.655 | 0.658 | 0.656 | 0.652 | 0.65 | 0.651 | 0.651 | 0.651 | 0.652 | 0.659 | 0.664 | 0.667 | 0.664 | 0.661 | 0.656 | 0.649 | 0.642 | 0.639 | 0.639 | 0.638 | 0.635 | 0.631 | 0.631 | 0.631 | 0.632 | 0.632 | 0.628 | 0.626 | 0.623 | 0.623 | 0.63 | 0.642 | 0.655 | 0.663 | 0.667 | 0.676 | 0.692 | 0.712 | 0.731 | 0.744 | 0.749 | 0.749 | 0.745 | 0.741 | 0.737 | 0.73 | 0.718 | 0.704 | 0.69 | 0.678 | 0.668 | 0.662 | 0.662 | 0.664 | 0.664 | 0.66 | 0.648 | 0.633 | 0.616 | 0.602 | 0.588 | 0.575 | 0.562 | 0.548 | 0.535 | 0.524 | 0.514 | 0.505 | 0.497 | 0.489 | 0.484 | 0.481 | 0.477 | 0.474 | 0.468 | 0.463 | 0.457 | 0.454 | 0.451 | 0.448 | 0.442 | 0.44 | 0.437 | 0.437 | 0.438 | 0.445 | 0.46 | 0.482 | 0.504 | 0.525 | 0.541 | 0.554 | 0.56 | 0.563 | 0.562 | 0.562 | 0.56 | 0.559 | 0.556 | 0.553 | 0.55 | 0.551 | 0.551 | 0.55 | 0.547 | 0.548 | 0.552 | 0.557 | 0.559 | 0.562 | 0.561 | 0.56 | 0.556 | 0.552 | 0.547 | 0.542 | 0.537 | 0.534 | 0.533 | 0.537 | 0.54 | 0.543 | 0.545 | 0.547 | 0.549 | 0.553 | 0.562 | 0.575 | 0.591 | 0.608 | 0.625 | 0.645 | 0.668 | 0.691 | 0.708 | 0.72 | 0.725 | 0.728 | 0.73 | 0.73 | 0.722 | 0.712 | 0.702 | 0.694 | 0.688 | 0.68 | 0.674 | 0.669 | 0.668 | 0.668 | 0.664 | 0.654 | 0.639 | 0.62 | 0.602 | 0.586 | 0.569 | 0.601 | 0.584 | 0.57 | 0.558 | 0.547 | 0.537 | 0.527 | 0.521 | 0.514 | 0.509 | 0.506 | 0.503 | 0.5 | 0.494 | 0.489 | 0.486 | 0.483 | 0.48 | 0.476 | 0.474 | 0.475 | 0.478 | 0.481 | 0.487 | 0.496 | 0.515 | 0.54 | 0.571 | 0.602 | 0.631 | 0.663 | 0.697 | 0.728 | 0.751 | 0.763 | 0.771 | 0.773 | 0.772 | 0.766 | 0.762 | 0.757 | 0.753 | 0.749 | 0.749 | 0.753 | 0.757 | 0.761 | 0.763 | 0.762 | 0.756 | 0.746 | 0.738 | 0.734 | 0.735 | 0.736 | 0.737 | 0.736 | 0.737 | 0.738 | 0.738 | 0.736 | 0.736 | 0.739 | 0.743 | 0.747 | 0.754 | 0.763 | 0.77 | 0.774 | 0.776 | 0.78 | 0.785 | 0.789 | 0.792 | 0.798 | 0.805 | 0.808 | 0.806 | 0.8 | 0.793 | 0.783 | 0.772 | 0.759 | 0.749 | 0.739 | 0.732 | 0.726 | 0.723 | 0.719 | 0.714 | 0.705 | 0.693 | 0.679 | 0.663 | 0.647 | 0.632 | 0.633 | 0.614 | 0.597 | 0.584 | 0.573 | 0.56 | 0.548 | 0.54 | 0.533 | 0.527 | 0.524 | 0.521 | 0.517 | 0.511 | 0.504 | 0.5 | 0.497 | 0.494 | 0.491 | 0.489 | 0.489 | 0.488 | 0.486 | 0.489 | 0.496 | 0.511 | 0.533 | 0.558 | 0.581 | 0.602 | 0.62 | 0.641 | 0.656 | 0.668 | 0.672 | 0.676 | 0.682 | 0.685 | 0.683 | 0.679 | 0.676 | 0.674 | 0.675 | 0.676 | 0.681 | 0.686 | 0.687 | 0.688 | 0.687 | 0.686 | 0.68 | 0.671 | 0.664 | 0.664 | 0.663 | 0.66 | 0.655 | 0.655 | 0.658 | 0.659 | 0.659 | 0.657 | 0.659 | 0.657 | 0.659 | 0.661 | 0.669 | 0.678 | 0.688 | 0.698 | 0.712 | 0.729 | 0.748 | 0.764 | 0.777 | 0.785 | 0.789 | 0.79 | 0.787 | 0.782 | 0.774 | 0.762 | 0.749 | 0.739 | 0.731 | 0.725 | 0.719 | 0.717 | 0.714 | 0.709 | 0.699 | 0.684 | 0.668 | 0.651 | 0.635 | 0.62 | 0.605 | 0.592 | 0.58 | 0.568 | 0.555 | 0.544 | 0.532 | 0.523 | 0.515 | 0.511 | 0.51 | 0.507 | 0.503 | 0.495 | 0.487 | 0.483 | 0.479 | 0.477 | 0.473 | 0.469 | 0.468 | 0.468 | 0.469 | 0.471 | 0.478 | 0.492 | 0.515 | 0.538 | 0.557 | 0.572 | 0.583 | 0.591 | 0.593 | 0.593 | 0.59 | 0.588 | 0.587 | 0.587 | 0.585 | 0.583 | 0.581 | 0.581 | 0.582 | 0.582 | 0.582 | 0.583 | 0.582 | 0.582 | 0.582 | 0.582 | 0.581 | 0.577 | 0.573 | 0.569 | 0.562 | 0.556 | 0.554 | 0.558 | 0.563 | 0.568 | 0.57 | 0.573 | 0.575 | 0.577 | 0.579 | 0.586 | 0.597 | 0.611 | 0.626 | 0.644 | 0.665 | 0.688 | 0.71 | 0.726 | 0.737 | 0.743 | 0.746 | 0.744 | 0.739 | 0.732 | 0.724 | 0.717 | 0.709 | 0.704 | 0.697 | 0.695 | 0.694 | 0.696 | 0.696 | 0.69 | 0.678 | 0.661 | 0.643 | 0.625 | 0.609 | 0.592 | 0.587 | 0.571 | 0.555 | 0.542 | 0.532 | 0.523 | 0.514 | 0.507 | 0.502 | 0.498 | 0.496 | 0.493 | 0.492 | 0.487 | 0.48 | 0.477 | 0.474 | 0.472 | 0.469 | 0.468 | 0.473 | 0.48 | 0.488 | 0.5 | 0.516 | 0.536 | 0.56 | 0.585 | 0.611 | 0.636 | 0.664 | 0.696 | 0.725 | 0.747 | 0.759 | 0.768 | 0.77 | 0.768 | 0.761 | 0.757 | 0.752 | 0.747 | 0.742 | 0.741 | 0.744 | 0.748 | 0.749 | 0.75 | 0.749 | 0.743 | 0.733 | 0.726 | 0.723 | 0.723 | 0.723 | 0.723 | 0.723 | 0.725 | 0.727 | 0.727 | 0.727 | 0.727 | 0.728 | 0.732 | 0.737 | 0.743 | 0.752 | 0.759 | 0.767 | 0.771 | 0.777 | 0.781 | 0.786 | 0.788 | 0.792 | 0.798 | 0.803 | 0.803 | 0.799 | 0.793 | 0.785 | 0.779 | 0.773 | 0.769 | 0.767 | 0.763 | 0.754 | 0.741 | 0.724 | 0.706 | 0.688 | 0.671 | 0.654 | 0.638 | 0.623 | 0.61 | 0.601 | 0.583 | 0.567 | 0.554 | 0.545 | 0.535 | 0.526 | 0.52 | 0.514 | 0.511 | 0.51 | 0.509 | 0.506 | 0.5 | 0.492 | 0.486 | 0.484 | 0.481 | 0.477 | 0.474 | 0.477 | 0.481 | 0.486 | 0.495 | 0.508 | 0.527 | 0.545 | 0.564 | 0.582 | 0.6 | 0.616 | 0.633 | 0.646 | 0.659 | 0.666 | 0.676 | 0.683 | 0.687 | 0.681 | 0.674 | 0.67 | 0.667 | 0.665 | 0.665 | 0.67 | 0.677 | 0.68 | 0.677 | 0.674 | 0.669 | 0.661 | 0.652 | 0.645 | 0.642 | 0.639 | 0.636 | 0.637 | 0.641 | 0.645 | 0.645 | 0.643 | 0.64 | 0.64 | 0.639 | 0.641 | 0.647 | 0.659 | 0.669 | 0.679 | 0.684 | 0.693 | 0.709 | 0.73 | 0.748 | 0.761 | 0.768 | 0.773 | 0.773 | 0.768 | 0.762 | 0.754 | 0.746 | 0.74 | 0.738 | 0.738 | 0.737 | 0.731 | 0.722 | 0.712 | 0.698 | 0.681 | 0.66 | 0.641 | 0.624 | 0.61 | 0.6 | 0.586 | 0.571 | 0.556 | 0.544 | 0.535 | 0.526 | 0.517 | 0.51 | 0.504 | 0.499 | 0.497 | 0.496 | 0.495 | 0.491 | 0.482 | 0.477 | 0.473 | 0.469 | 0.463 | 0.458 | 0.46 | 0.465 | 0.473 | 0.483 | 0.496 | 0.511 | 0.529 | 0.545 | 0.559 | 0.567 | 0.573 | 0.579 | 0.584 | 0.585 | 0.584 | 0.581 | 0.579 | 0.577 | 0.573 | 0.571 | 0.571 | 0.571 | 0.57 | 0.571 | 0.575 | 0.579 | 0.58 | 0.58 | 0.582 | 0.581 | 0.578 | 0.572 | 0.568 | 0.564 | 0.558 | 0.551 | 0.547 | 0.548 | 0.552 | 0.556 | 0.558 | 0.559 | 0.562 | 0.566 | 0.57 | 0.578 | 0.592 | 0.61 | 0.629 | 0.646 | 0.666 | 0.69 | 0.712 | 0.732 | 0.74 | 0.745 | 0.746 | 0.744 | 0.741 | 0.737 | 0.736 | 0.734 | 0.733 | 0.733 | 0.735 | 0.735 | 0.728 | 0.716 | 0.701 | 0.682 | 0.662 | 0.641 | 0.622 | 0.604 | 0.59 | 0.58 | 0.54 | 0.526 | 0.512 | 0.501 | 0.492 | 0.484 | 0.477 | 0.472 | 0.467 | 0.464 | 0.464 | 0.463 | 0.462 | 0.458 | 0.452 | 0.447 | 0.444 | 0.441 | 0.438 | 0.437 | 0.442 | 0.453 | 0.467 | 0.488 | 0.512 | 0.541 | 0.575 | 0.61 | 0.642 | 0.669 | 0.698 | 0.732 | 0.761 | 0.783 | 0.792 | 0.796 | 0.794 | 0.789 | 0.78 | 0.77 | 0.758 | 0.75 | 0.744 | 0.741 | 0.741 | 0.743 | 0.743 | 0.741 | 0.735 | 0.725 | 0.714 | 0.705 | 0.701 | 0.702 | 0.703 | 0.703 | 0.701 | 0.702 | 0.704 | 0.704 | 0.705 | 0.706 | 0.709 | 0.715 | 0.72 | 0.728 | 0.737 | 0.745 | 0.751 | 0.753 | 0.759 | 0.764 | 0.77 | 0.773 | 0.78 | 0.789 | 0.8 | 0.808 | 0.812 | 0.816 | 0.817 | 0.814 | 0.804 | 0.788 | 0.768 | 0.747 | 0.725 | 0.702 | 0.681 | 0.661 | 0.642 | 0.623 | 0.606 | 0.591 | 0.576 | 0.562 | 0.551 | 0.534 | 0.52 | 0.51 | 0.503 | 0.495 | 0.486 | 0.479 | 0.475 | 0.471 | 0.47 | 0.469 | 0.468 | 0.462 | 0.457 | 0.452 | 0.449 | 0.443 | 0.438 | 0.435 | 0.439 | 0.444 | 0.453 | 0.468 | 0.486 | 0.508 | 0.531 | 0.555 | 0.575 | 0.589 | 0.603 | 0.621 | 0.637 | 0.651 | 0.662 | 0.672 | 0.677 | 0.674 | 0.668 | 0.66 | 0.654 | 0.645 | 0.641 | 0.639 | 0.644 | 0.649 | 0.651 | 0.648 | 0.643 | 0.637 | 0.629 | 0.619 | 0.613 | 0.608 | 0.606 | 0.602 | 0.6 | 0.6 | 0.598 | 0.596 | 0.595 | 0.597 | 0.601 | 0.603 | 0.603 | 0.607 | 0.616 | 0.631 | 0.645 | 0.653 | 0.662 | 0.679 | 0.706 | 0.729 | 0.745 | 0.752 | 0.76 | 0.763 | 0.767 | 0.771 | 0.775 | 0.775 | 0.771 | 0.759 | 0.743 | 0.725 | 0.71 | 0.693 | 0.676 | 0.66 | 0.644 | 0.625 | 0.603 | 0.585 | 0.571 | 0.559 | 0.546 | 0.531 | 0.518 | 0.509 | 0.501 | 0.494 | 0.485 | 0.477 | 0.47 | 0.465 | 0.463 | 0.46 | 0.457 | 0.453 | 0.448 | 0.442 | 0.436 | 0.432 | 0.429 | 0.426 | 0.426 | 0.431 | 0.44 | 0.455 | 0.471 | 0.492 | 0.513 | 0.535 | 0.553 | 0.563 | 0.568 | 0.573 | 0.576 | 0.577 | 0.575 | 0.571 | 0.569 | 0.569 | 0.568 | 0.564 | 0.56 | 0.557 | 0.556 | 0.555 | 0.556 | 0.558 | 0.56 | 0.562 | 0.564 | 0.565 | 0.565 | 0.562 | 0.558 | 0.553 | 0.551 | 0.545 | 0.539 | 0.537 | 0.54 | 0.544 | 0.546 | 0.549 | 0.552 | 0.555 | 0.555 | 0.562 | 0.577 | 0.601 | 0.622 | 0.642 | 0.659 | 0.682 | 0.704 | 0.726 | 0.742 | 0.752 | 0.756 | 0.754 | 0.754 | 0.756 | 0.76 | 0.759 | 0.754 | 0.744 | 0.732 | 0.715 | 0.699 | 0.678 | 0.658 | 0.635 | 0.613 | 0.589 | 0.568 | 0.549 | 0.535 | 0.522 | 0.534 | 0.519 | 0.506 | 0.496 | 0.487 | 0.481 | 0.475 | 0.469 | 0.464 | 0.459 | 0.457 | 0.456 | 0.456 | 0.452 | 0.447 | 0.443 | 0.441 | 0.439 | 0.436 | 0.436 | 0.442 | 0.454 | 0.469 | 0.491 | 0.514 | 0.542 | 0.576 | 0.617 | 0.66 | 0.702 | 0.742 | 0.782 | 0.812 | 0.829 | 0.834 | 0.831 | 0.826 | 0.819 | 0.812 | 0.804 | 0.794 | 0.786 | 0.779 | 0.774 | 0.77 | 0.767 | 0.765 | 0.763 | 0.758 | 0.747 | 0.733 | 0.723 | 0.72 | 0.72 | 0.72 | 0.719 | 0.718 | 0.719 | 0.721 | 0.721 | 0.72 | 0.72 | 0.723 | 0.73 | 0.738 | 0.749 | 0.762 | 0.774 | 0.781 | 0.786 | 0.796 | 0.806 | 0.815 | 0.824 | 0.84 | 0.858 | 0.873 | 0.88 | 0.878 | 0.866 | 0.846 | 0.824 | 0.804 | 0.784 | 0.763 | 0.74 | 0.718 | 0.697 | 0.677 | 0.657 | 0.638 | 0.623 | 0.606 | 0.591 | 0.575 | 0.561 | 0.561 | 0.544 | 0.528 | 0.517 | 0.507 | 0.498 | 0.489 | 0.483 | 0.477 | 0.474 | 0.471 | 0.47 | 0.468 | 0.463 | 0.458 | 0.453 | 0.45 | 0.446 | 0.444 | 0.444 | 0.449 | 0.457 | 0.468 | 0.486 | 0.506 | 0.531 | 0.558 | 0.589 | 0.619 | 0.645 | 0.668 | 0.689 | 0.703 | 0.71 | 0.713 | 0.719 | 0.722 | 0.724 | 0.719 | 0.714 | 0.708 | 0.704 | 0.699 | 0.693 | 0.689 | 0.69 | 0.693 | 0.693 | 0.689 | 0.682 | 0.676 | 0.671 | 0.665 | 0.659 | 0.653 | 0.649 | 0.644 | 0.642 | 0.64 | 0.641 | 0.644 | 0.648 | 0.653 | 0.656 | 0.657 | 0.66 | 0.673 | 0.691 | 0.709 | 0.723 | 0.738 | 0.758 | 0.785 | 0.812 | 0.835 | 0.854 | 0.865 | 0.867 | 0.86 | 0.847 | 0.83 | 0.81 | 0.789 | 0.769 | 0.748 | 0.728 | 0.71 | 0.695 | 0.682 | 0.667 | 0.652 | 0.635 | 0.616 | 0.598 | 0.582 | 0.57 | 0.555 | 0.539 | 0.525 | 0.515 | 0.508 | 0.502 | 0.496 | 0.489 | 0.483 | 0.476 | 0.471 | 0.466 | 0.464 | 0.459 | 0.454 | 0.448 | 0.445 | 0.442 | 0.44 | 0.44 | 0.444 | 0.453 | 0.464 | 0.48 | 0.497 | 0.52 | 0.544 | 0.57 | 0.594 | 0.613 | 0.625 | 0.628 | 0.627 | 0.622 | 0.617 | 0.612 | 0.608 | 0.607 | 0.605 | 0.605 | 0.605 | 0.603 | 0.602 | 0.6 | 0.604 | 0.605 | 0.603 | 0.599 | 0.597 | 0.597 | 0.595 | 0.59 | 0.585 | 0.58 | 0.573 | 0.567 | 0.562 | 0.562 | 0.566 | 0.569 | 0.573 | 0.577 | 0.581 | 0.585 | 0.592 | 0.604 | 0.622 | 0.645 | 0.669 | 0.69 | 0.712 | 0.738 | 0.766 | 0.791 | 0.81 | 0.823 | 0.831 | 0.832 | 0.826 | 0.812 | 0.797 | 0.781 | 0.765 | 0.747 | 0.729 | 0.711 | 0.693 | 0.675 | 0.657 | 0.638 | 0.618 | 0.599 | 0.578 | 0.559 | 0.542 | 0.53 | 0.558 | 0.545 | 0.531 | 0.521 | 0.513 | 0.506 | 0.499 | 0.494 | 0.49 | 0.487 | 0.482 | 0.479 | 0.476 | 0.472 | 0.467 | 0.46 | 0.458 | 0.456 | 0.456 | 0.461 | 0.471 | 0.485 | 0.502 | 0.525 | 0.551 | 0.581 | 0.617 | 0.656 | 0.698 | 0.736 | 0.777 | 0.818 | 0.849 | 0.866 | 0.871 | 0.87 | 0.866 | 0.86 | 0.855 | 0.85 | 0.843 | 0.835 | 0.826 | 0.819 | 0.817 | 0.817 | 0.817 | 0.813 | 0.806 | 0.794 | 0.781 | 0.771 | 0.766 | 0.767 | 0.769 | 0.771 | 0.773 | 0.776 | 0.78 | 0.783 | 0.783 | 0.786 | 0.793 | 0.806 | 0.823 | 0.845 | 0.872 | 0.9 | 0.923 | 0.938 | 0.947 | 0.945 | 0.94 | 0.93 | 0.925 | 0.924 | 0.925 | 0.92 | 0.908 | 0.889 | 0.866 | 0.844 | 0.822 | 0.8 | 0.78 | 0.759 | 0.739 | 0.718 | 0.698 | 0.677 | 0.657 | 0.644 | 0.63 | 0.617 | 0.6 | 0.583 | 0.584 | 0.569 | 0.557 | 0.548 | 0.541 | 0.534 | 0.526 | 0.518 | 0.51 | 0.502 | 0.495 | 0.491 | 0.488 | 0.484 | 0.48 | 0.474 | 0.469 | 0.463 | 0.461 | 0.465 | 0.475 | 0.488 | 0.502 | 0.518 | 0.536 | 0.558 | 0.585 | 0.618 | 0.65 | 0.678 | 0.701 | 0.722 | 0.737 | 0.745 | 0.747 | 0.752 | 0.758 | 0.763 | 0.761 | 0.758 | 0.753 | 0.748 | 0.744 | 0.742 | 0.742 | 0.742 | 0.739 | 0.736 | 0.729 | 0.723 | 0.714 | 0.707 | 0.7 | 0.698 | 0.697 | 0.696 | 0.692 | 0.691 | 0.694 | 0.7 | 0.702 | 0.703 | 0.708 | 0.715 | 0.728 | 0.747 | 0.777 | 0.812 | 0.847 | 0.869 | 0.885 | 0.895 | 0.907 | 0.912 | 0.913 | 0.907 | 0.899 | 0.887 | 0.873 | 0.854 | 0.834 | 0.812 | 0.792 | 0.771 | 0.752 | 0.737 | 0.724 | 0.707 | 0.69 | 0.671 | 0.654 | 0.64 | 0.625 | 0.611 | 0.594 | 0.58 | 0.567 | 0.555 | 0.542 | 0.532 | 0.524 | 0.517 | 0.511 | 0.505 | 0.499 | 0.494 | 0.488 | 0.483 | 0.48 | 0.473 | 0.468 | 0.461 | 0.458 | 0.455 | 0.454 | 0.455 | 0.46 | 0.468 | 0.48 | 0.494 | 0.511 | 0.532 | 0.557 | 0.585 | 0.612 | 0.632 | 0.644 | 0.648 | 0.649 | 0.648 | 0.645 | 0.64 | 0.635 | 0.631 | 0.631 | 0.632 | 0.635 | 0.634 | 0.634 | 0.635 | 0.637 | 0.636 | 0.635 | 0.634 | 0.632 | 0.627 | 0.623 | 0.62 | 0.619 | 0.615 | 0.61 | 0.607 | 0.606 | 0.608 | 0.613 | 0.619 | 0.626 | 0.63 | 0.637 | 0.645 | 0.66 | 0.68 | 0.713 | 0.753 | 0.79 | 0.815 | 0.834 | 0.851 | 0.862 | 0.867 | 0.867 | 0.866 | 0.86 | 0.85 | 0.836 | 0.824 | 0.809 | 0.793 | 0.775 | 0.754 | 0.735 | 0.717 | 0.7 | 0.682 | 0.663 | 0.642 | 0.622 | 0.605 | 0.588 | 0.571 | 0.551 | 0.538 | 0.587 | 0.573 | 0.56 | 0.55 | 0.541 | 0.531 | 0.522 | 0.515 | 0.512 | 0.512 | 0.509 | 0.504 | 0.498 | 0.492 | 0.487 | 0.484 | 0.484 | 0.484 | 0.483 | 0.485 | 0.491 | 0.505 | 0.522 | 0.544 | 0.567 | 0.593 | 0.626 | 0.664 | 0.704 | 0.742 | 0.785 | 0.829 | 0.869 | 0.896 | 0.909 | 0.912 | 0.908 | 0.903 | 0.899 | 0.896 | 0.89 | 0.882 | 0.873 | 0.867 | 0.865 | 0.866 | 0.865 | 0.859 | 0.849 | 0.836 | 0.824 | 0.815 | 0.812 | 0.813 | 0.813 | 0.814 | 0.813 | 0.817 | 0.822 | 0.826 | 0.825 | 0.826 | 0.831 | 0.845 | 0.863 | 0.888 | 0.916 | 0.941 | 0.957 | 0.962 | 0.964 | 0.96 | 0.955 | 0.947 | 0.942 | 0.938 | 0.934 | 0.926 | 0.913 | 0.894 | 0.875 | 0.854 | 0.833 | 0.812 | 0.793 | 0.775 | 0.759 | 0.741 | 0.722 | 0.701 | 0.683 | 0.67 | 0.659 | 0.646 | 0.628 | 0.609 | 0.597 | 0.589 | 0.581 | 0.573 | 0.563 | 0.555 | 0.545 | 0.537 | 0.531 | 0.526 | 0.521 | 0.515 | 0.508 | 0.499 | 0.496 | 0.494 | 0.493 | 0.49 | 0.487 | 0.489 | 0.495 | 0.507 | 0.521 | 0.539 | 0.558 | 0.579 | 0.605 | 0.637 | 0.668 | 0.694 | 0.719 | 0.746 | 0.773 | 0.79 | 0.801 | 0.803 | 0.804 | 0.8 | 0.798 | 0.796 | 0.793 | 0.788 | 0.783 | 0.781 | 0.781 | 0.785 | 0.787 | 0.784 | 0.777 | 0.769 | 0.761 | 0.754 | 0.75 | 0.749 | 0.747 | 0.743 | 0.741 | 0.745 | 0.752 | 0.758 | 0.758 | 0.758 | 0.763 | 0.772 | 0.787 | 0.806 | 0.838 | 0.864 | 0.883 | 0.892 | 0.901 | 0.91 | 0.919 | 0.921 | 0.919 | 0.908 | 0.899 | 0.887 | 0.875 | 0.86 | 0.844 | 0.827 | 0.81 | 0.791 | 0.773 | 0.754 | 0.742 | 0.724 | 0.709 | 0.691 | 0.678 | 0.666 | 0.653 | 0.64 | 0.624 | 0.605 | 0.593 | 0.583 | 0.573 | 0.562 | 0.553 | 0.543 | 0.534 | 0.525 | 0.521 | 0.518 | 0.513 | 0.507 | 0.501 | 0.496 | 0.49 | 0.485 | 0.485 | 0.481 | 0.48 | 0.479 | 0.486 | 0.496 | 0.506 | 0.52 | 0.535 | 0.558 | 0.581 | 0.608 | 0.631 | 0.65 | 0.668 | 0.682 | 0.694 | 0.697 | 0.695 | 0.69 | 0.688 | 0.689 | 0.692 | 0.694 | 0.693 | 0.686 | 0.683 | 0.685 | 0.691 | 0.695 | 0.694 | 0.693 | 0.692 | 0.692 | 0.688 | 0.685 | 0.68 | 0.676 | 0.674 | 0.672 | 0.674 | 0.673 | 0.675 | 0.678 | 0.684 | 0.692 | 0.702 | 0.713 | 0.728 | 0.751 | 0.785 | 0.819 | 0.846 | 0.861 | 0.878 | 0.897 | 0.912 | 0.914 | 0.911 | 0.903 | 0.894 | 0.881 | 0.866 | 0.85 | 0.835 | 0.819 | 0.803 | 0.786 | 0.767 | 0.752 | 0.734 | 0.716 | 0.696 | 0.676 | 0.659 | 0.642 | 0.624 | 0.605 | 0.584 | 0.571
E2B | -3456 | 0.615 | 0.603 | 0.589 | 0.577 | 0.565 | 0.553 | 0.546 | 0.541 | 0.537 | 0.532 | 0.528 | 0.525 | 0.522 | 0.517 | 0.514 | 0.51 | 0.509 | 0.508 | 0.509 | 0.512 | 0.52 | 0.53 | 0.544 | 0.563 | 0.587 | 0.617 | 0.653 | 0.695 | 0.738 | 0.782 | 0.83 | 0.881 | 0.92 | 0.942 | 0.951 | 0.955 | 0.953 | 0.944 | 0.93 | 0.917 | 0.903 | 0.885 | 0.867 | 0.853 | 0.845 | 0.838 | 0.831 | 0.824 | 0.813 | 0.798 | 0.785 | 0.779 | 0.777 | 0.78 | 0.783 | 0.785 | 0.787 | 0.79 | 0.797 | 0.803 | 0.807 | 0.813 | 0.827 | 0.847 | 0.869 | 0.892 | 0.921 | 0.947 | 0.971 | 0.986 | 0.999 | 1 | 0.996 | 0.99 | 0.987 | 0.986 | 0.981 | 0.973 | 0.963 | 0.949 | 0.928 | 0.903 | 0.878 | 0.855 | 0.834 | 0.815 | 0.797 | 0.777 | 0.755 | 0.733 | 0.713 | 0.701 | 0.688 | 0.674 | 0.657 | 0.642 | 0.642 | 0.628 | 0.614 | 0.602 | 0.592 | 0.583 | 0.574 | 0.565 | 0.558 | 0.551 | 0.546 | 0.54 | 0.536 | 0.531 | 0.527 | 0.524 | 0.522 | 0.52 | 0.52 | 0.521 | 0.526 | 0.533 | 0.542 | 0.555 | 0.571 | 0.595 | 0.621 | 0.652 | 0.679 | 0.704 | 0.731 | 0.766 | 0.795 | 0.809 | 0.813 | 0.821 | 0.83 | 0.837 | 0.833 | 0.828 | 0.819 | 0.806 | 0.795 | 0.785 | 0.779 | 0.775 | 0.77 | 0.763 | 0.754 | 0.745 | 0.738 | 0.734 | 0.731 | 0.728 | 0.725 | 0.723 | 0.723 | 0.726 | 0.731 | 0.738 | 0.742 | 0.746 | 0.756 | 0.769 | 0.783 | 0.801 | 0.828 | 0.857 | 0.885 | 0.911 | 0.931 | 0.944 | 0.951 | 0.955 | 0.955 | 0.948 | 0.938 | 0.93 | 0.921 | 0.909 | 0.892 | 0.872 | 0.852 | 0.834 | 0.814 | 0.795 | 0.779 | 0.762 | 0.745 | 0.729 | 0.715 | 0.7 | 0.686 | 0.67 | 0.654 | 0.635 | 0.618 | 0.607 | 0.592 | 0.58 | 0.567 | 0.556 | 0.548 | 0.54 | 0.535 | 0.529 | 0.525 | 0.522 | 0.518 | 0.512 | 0.506 | 0.503 | 0.503 | 0.501 | 0.502 | 0.502 | 0.508 | 0.513 | 0.524 | 0.537 | 0.553 | 0.576 | 0.6 | 0.628 | 0.651 | 0.671 | 0.687 | 0.702 | 0.709 | 0.705 | 0.693 | 0.685 | 0.682 | 0.682 | 0.68 | 0.677 | 0.673 | 0.667 | 0.662 | 0.657 | 0.651 | 0.643 | 0.637 | 0.636 | 0.636 | 0.634 | 0.635 | 0.638 | 0.638 | 0.632 | 0.624 | 0.618 | 0.615 | 0.616 | 0.622 | 0.629 | 0.635 | 0.639 | 0.648 | 0.662 | 0.676 | 0.695 | 0.724 | 0.761 | 0.8 | 0.831 | 0.859 | 0.879 | 0.898 | 0.908 | 0.912 | 0.909 | 0.904 | 0.894 | 0.883 | 0.869 | 0.855 | 0.838 | 0.818 | 0.798 | 0.781 | 0.765 | 0.752 | 0.734 | 0.715 | 0.695 | 0.676 | 0.659 | 0.643 | 0.627 | 0.61 | 0.596 | 0.596 | 0.584 | 0.574 | 0.563 | 0.556 | 0.55 | 0.543 | 0.538 | 0.534 | 0.531 | 0.527 | 0.524 | 0.521 | 0.516 | 0.511 | 0.509 | 0.508 | 0.506 | 0.505 | 0.507 | 0.516 | 0.528 | 0.543 | 0.563 | 0.589 | 0.619 | 0.654 | 0.692 | 0.732 | 0.772 | 0.813 | 0.856 | 0.887 | 0.906 | 0.912 | 0.912 | 0.903 | 0.888 | 0.87 | 0.853 | 0.834 | 0.815 | 0.798 | 0.785 | 0.776 | 0.769 | 0.764 | 0.755 | 0.742 | 0.725 | 0.711 | 0.704 | 0.702 | 0.703 | 0.704 | 0.703 | 0.705 | 0.709 | 0.716 | 0.72 | 0.724 | 0.729 | 0.741 | 0.759 | 0.781 | 0.802 | 0.825 | 0.845 | 0.864 | 0.88 | 0.899 | 0.916 | 0.93 | 0.94 | 0.95 | 0.955 | 0.953 | 0.946 | 0.936 | 0.922 | 0.903 | 0.882 | 0.859 | 0.836 | 0.816 | 0.796 | 0.778 | 0.759 | 0.738 | 0.715 | 0.694 | 0.682 | 0.67 | 0.655 | 0.635 | 0.621 | 0.63 | 0.619 | 0.604 | 0.592 | 0.582 | 0.574 | 0.565 | 0.557 | 0.552 | 0.545 | 0.541 | 0.537 | 0.532 | 0.526 | 0.521 | 0.521 | 0.519 | 0.516 | 0.514 | 0.515 | 0.519 | 0.527 | 0.539 | 0.556 | 0.575 | 0.598 | 0.624 | 0.654 | 0.681 | 0.706 | 0.725 | 0.749 | 0.763 | 0.773 | 0.774 | 0.776 | 0.776 | 0.769 | 0.758 | 0.745 | 0.73 | 0.717 | 0.71 | 0.704 | 0.697 | 0.687 | 0.68 | 0.671 | 0.663 | 0.652 | 0.642 | 0.632 | 0.624 | 0.621 | 0.616 | 0.612 | 0.609 | 0.612 | 0.622 | 0.63 | 0.637 | 0.642 | 0.653 | 0.664 | 0.676 | 0.69 | 0.712 | 0.74 | 0.769 | 0.793 | 0.817 | 0.844 | 0.873 | 0.896 | 0.91 | 0.916 | 0.914 | 0.904 | 0.889 | 0.875 | 0.859 | 0.84 | 0.819 | 0.799 | 0.782 | 0.769 | 0.757 | 0.744 | 0.728 | 0.708 | 0.693 | 0.675 | 0.656 | 0.635 | 0.616 | 0.602 | 0.587 | 0.576 | 0.565 | 0.557 | 0.548 | 0.54 | 0.532 | 0.528 | 0.527 | 0.525 | 0.521 | 0.514 | 0.507 | 0.5 | 0.495 | 0.494 | 0.495 | 0.494 | 0.493 | 0.494 | 0.499 | 0.507 | 0.517 | 0.529 | 0.543 | 0.561 | 0.58 | 0.599 | 0.619 | 0.639 | 0.654 | 0.665 | 0.669 | 0.665 | 0.656 | 0.646 | 0.64 | 0.631 | 0.624 | 0.612 | 0.602 | 0.591 | 0.585 | 0.58 | 0.572 | 0.564 | 0.556 | 0.55 | 0.549 | 0.545 | 0.54 | 0.532 | 0.527 | 0.525 | 0.523 | 0.519 | 0.517 | 0.518 | 0.526 | 0.536 | 0.544 | 0.555 | 0.563 | 0.577 | 0.588 | 0.608 | 0.637 | 0.673 | 0.706 | 0.733 | 0.766 | 0.801 | 0.837 | 0.861 | 0.878 | 0.881 | 0.877 | 0.865 | 0.854 | 0.84 | 0.829 | 0.814 | 0.796 | 0.775 | 0.759 | 0.747 | 0.736 | 0.721 | 0.702 | 0.68 | 0.659 | 0.639 | 0.62 | 0.602 | 0.585 | 0.575 | 0.566 | 0.554 | 0.541 | 0.531 | 0.525 | 0.519 | 0.512 | 0.507 | 0.503 | 0.5 | 0.495 | 0.493 | 0.492 | 0.488 | 0.483 | 0.479 | 0.478 | 0.476 | 0.475 | 0.477 | 0.484 | 0.497 | 0.512 | 0.534 | 0.558 | 0.589 | 0.62 | 0.652 | 0.683 | 0.712 | 0.744 | 0.774 | 0.797 | 0.808 | 0.808 | 0.803 | 0.791 | 0.775 | 0.755 | 0.735 | 0.717 | 0.699 | 0.684 | 0.672 | 0.663 | 0.658 | 0.654 | 0.648 | 0.636 | 0.62 | 0.606 | 0.597 | 0.594 | 0.595 | 0.596 | 0.598 | 0.599 | 0.604 | 0.608 | 0.612 | 0.613 | 0.617 | 0.626 | 0.642 | 0.661 | 0.683 | 0.706 | 0.727 | 0.746 | 0.761 | 0.777 | 0.791 | 0.807 | 0.822 | 0.839 | 0.858 | 0.876 | 0.883 | 0.881 | 0.871 | 0.856 | 0.839 | 0.819 | 0.799 | 0.778 | 0.757 | 0.737 | 0.716 | 0.696 | 0.677 | 0.66 | 0.647 | 0.635 | 0.622 | 0.603 | 0.588 | 0.596 | 0.587 | 0.575 | 0.561 | 0.553 | 0.543 | 0.534 | 0.525 | 0.52 | 0.514 | 0.506 | 0.501 | 0.498 | 0.493 | 0.486 | 0.483 | 0.48 | 0.479 | 0.478 | 0.482 | 0.487 | 0.493 | 0.501 | 0.514 | 0.531 | 0.556 | 0.583 | 0.609 | 0.631 | 0.648 | 0.663 | 0.679 | 0.687 | 0.689 | 0.686 | 0.687 | 0.682 | 0.67 | 0.653 | 0.637 | 0.624 | 0.611 | 0.605 | 0.601 | 0.598 | 0.592 | 0.585 | 0.579 | 0.57 | 0.563 | 0.552 | 0.543 | 0.538 | 0.536 | 0.534 | 0.531 | 0.53 | 0.531 | 0.534 | 0.54 | 0.549 | 0.558 | 0.57 | 0.582 | 0.595 | 0.61 | 0.635 | 0.665 | 0.693 | 0.715 | 0.737 | 0.764 | 0.797 | 0.826 | 0.848 | 0.865 | 0.877 | 0.878 | 0.871 | 0.86 | 0.846 | 0.829 | 0.808 | 0.787 | 0.771 | 0.753 | 0.74 | 0.723 | 0.707 | 0.689 | 0.674 | 0.659 | 0.643 | 0.624 | 0.604 | 0.587 | 0.572 | 0.558 | 0.545 | 0.535 | 0.528 | 0.521 | 0.511 | 0.511 | 0.506 | 0.504 | 0.5 | 0.492 | 0.486 | 0.477 | 0.472 | 0.468 | 0.467 | 0.464 | 0.463 | 0.464 | 0.468 | 0.476 | 0.484 | 0.495 | 0.51 | 0.529 | 0.548 | 0.567 | 0.584 | 0.593 | 0.598 | 0.599 | 0.597 | 0.591 | 0.583 | 0.575 | 0.565 | 0.551 | 0.538 | 0.525 | 0.515 | 0.503 | 0.496 | 0.49 | 0.487 | 0.479 | 0.475 | 0.47 | 0.466 | 0.46 | 0.455 | 0.45 | 0.446 | 0.439 | 0.436 | 0.435 | 0.436 | 0.438 | 0.441 | 0.447 | 0.452 | 0.457 | 0.463 | 0.476 | 0.49 | 0.508 | 0.529 | 0.556 | 0.588 | 0.619 | 0.651 | 0.689 | 0.724 | 0.751 | 0.769 | 0.784 | 0.798 | 0.803 | 0.801 | 0.793 | 0.782 | 0.77 | 0.756 | 0.742 | 0.729 | 0.717 | 0.703 | 0.686 | 0.668 | 0.65 | 0.631 | 0.609 | 0.589 | 0.571 | 0.556 | 0.548 | 0.53 | 0.517 | 0.504 | 0.493 | 0.486 | 0.479 | 0.471 | 0.465 | 0.459 | 0.457 | 0.453 | 0.452 | 0.451 | 0.448 | 0.442 | 0.439 | 0.439 | 0.439 | 0.437 | 0.438 | 0.442 | 0.452 | 0.464 | 0.484 | 0.505 | 0.531 | 0.557 | 0.582 | 0.608 | 0.634 | 0.666 | 0.694 | 0.712 | 0.719 | 0.718 | 0.711 | 0.698 | 0.681 | 0.661 | 0.64 | 0.619 | 0.599 | 0.581 | 0.567 | 0.557 | 0.551 | 0.546 | 0.542 | 0.533 | 0.519 | 0.505 | 0.494 | 0.488 | 0.486 | 0.482 | 0.48 | 0.479 | 0.482 | 0.485 | 0.487 | 0.488 | 0.489 | 0.494 | 0.502 | 0.515 | 0.53 | 0.549 | 0.571 | 0.59 | 0.61 | 0.628 | 0.646 | 0.661 | 0.673 | 0.687 | 0.702 | 0.714 | 0.722 | 0.723 | 0.725 | 0.723 | 0.725 | 0.726 | 0.727 | 0.723 | 0.714 | 0.701 | 0.684 | 0.666 | 0.649 | 0.631 | 0.616 | 0.602 | 0.588 | 0.573 | 0.556 | 0.566 | 0.549 | 0.534 | 0.521 | 0.511 | 0.502 | 0.494 | 0.488 | 0.481 | 0.474 | 0.468 | 0.465 | 0.462 | 0.456 | 0.451 | 0.447 | 0.447 | 0.447 | 0.445 | 0.445 | 0.449 | 0.456 | 0.465 | 0.477 | 0.493 | 0.513 | 0.533 | 0.549 | 0.564 | 0.58 | 0.595 | 0.608 | 0.613 | 0.613 | 0.61 | 0.606 | 0.601 | 0.588 | 0.575 | 0.557 | 0.541 | 0.52 | 0.505 | 0.493 | 0.486 | 0.48 | 0.476 | 0.469 | 0.462 | 0.45 | 0.438 | 0.423 | 0.414 | 0.406 | 0.401 | 0.398 | 0.399 | 0.4 | 0.401 | 0.401 | 0.403 | 0.406 | 0.414 | 0.424 | 0.434 | 0.447 | 0.467 | 0.493 | 0.515 | 0.536 | 0.557 | 0.585 | 0.616 | 0.643 | 0.663 | 0.674 | 0.68 | 0.682 | 0.684 | 0.69 | 0.696 | 0.705 | 0.711 | 0.712 | 0.71 | 0.702 | 0.692 | 0.677 | 0.662 | 0.645 | 0.627 | 0.607 | 0.59 | 0.577 | 0.565 | 0.559 | 0.546 | 0.533 | 0.519 | 0.508 | 0.502 | 0.495 | 0.485 | 0.478 | 0.472 | 0.468 | 0.464 | 0.461 | 0.46 | 0.454 | 0.447 | 0.442 | 0.441 | 0.441 | 0.438 | 0.438 | 0.442 | 0.449 | 0.458 | 0.467 | 0.477 | 0.491 | 0.509 | 0.527 | 0.544 | 0.556 | 0.563 | 0.561 | 0.556 | 0.546 | 0.535 | 0.522 | 0.511 | 0.497 | 0.483 | 0.466 | 0.449 | 0.432 | 0.418 | 0.409 | 0.401 | 0.392 | 0.383 | 0.375 | 0.37 | 0.365 | 0.358 | 0.351 | 0.343 | 0.334 | 0.328 | 0.327 | 0.327 | 0.33 | 0.332 | 0.336 | 0.338 | 0.34 | 0.346 | 0.356 | 0.367 | 0.382 | 0.401 | 0.429 | 0.46 | 0.496 | 0.531 | 0.568 | 0.601 | 0.625 | 0.642 | 0.657 | 0.67 | 0.676 | 0.674 | 0.676 | 0.682 | 0.689 | 0.694 | 0.694 | 0.692 | 0.684 | 0.672 | 0.657 | 0.639 | 0.622 | 0.605 | 0.585 | 0.565 | 0.549 | 0.532 | 0.52 | 0.539 | 0.524 | 0.51 | 0.5 | 0.492 | 0.485 | 0.479 | 0.474 | 0.47 | 0.465 | 0.46 | 0.457 | 0.454 | 0.45 | 0.445 | 0.444 | 0.445 | 0.444 | 0.44 | 0.44 | 0.442 | 0.448 | 0.453 | 0.461 | 0.473 | 0.494 | 0.521 | 0.548 | 0.573 | 0.596 | 0.624 | 0.649 | 0.667 | 0.676 | 0.674 | 0.67 | 0.659 | 0.644 | 0.624 | 0.606 | 0.588 | 0.572 | 0.556 | 0.545 | 0.539 | 0.537 | 0.534 | 0.534 | 0.53 | 0.521 | 0.504 | 0.489 | 0.482 | 0.48 | 0.48 | 0.479 | 0.479 | 0.481 | 0.485 | 0.487 | 0.486 | 0.487 | 0.491 | 0.501 | 0.514 | 0.53 | 0.549 | 0.57 | 0.587 | 0.603 | 0.62 | 0.636 | 0.648 | 0.655 | 0.665 | 0.678 | 0.692 | 0.701 | 0.707 | 0.707 | 0.703 | 0.695 | 0.685 | 0.681 | 0.68 | 0.683 | 0.682 | 0.679 | 0.67 | 0.658 | 0.643 | 0.629 | 0.613 | 0.599 | 0.584 | 0.564 | 0.544 | 0.526 | 0.533 | 0.523 | 0.516 | 0.51 | 0.502 | 0.495 | 0.489 | 0.484 | 0.479 | 0.474 | 0.469 | 0.464 | 0.46 | 0.458 | 0.459 | 0.459 | 0.459 | 0.459 | 0.459 | 0.46 | 0.462 | 0.465 | 0.472 | 0.487 | 0.507 | 0.524 | 0.537 | 0.548 | 0.564 | 0.577 | 0.582 | 0.579 | 0.574 | 0.57 | 0.563 | 0.553 | 0.536 | 0.521 | 0.508 | 0.496 | 0.487 | 0.477 | 0.472 | 0.466 | 0.461 | 0.458 | 0.453 | 0.446 | 0.439 | 0.428 | 0.426 | 0.42 | 0.419 | 0.413 | 0.41 | 0.41 | 0.411 | 0.412 | 0.413 | 0.417 | 0.422 | 0.428 | 0.434 | 0.445 | 0.465 | 0.491 | 0.517 | 0.537 | 0.558 | 0.583 | 0.612 | 0.64 | 0.662 | 0.681 | 0.692 | 0.699 | 0.7 | 0.699 | 0.693 | 0.686 | 0.679 | 0.678 | 0.682 | 0.687 | 0.688 | 0.686 | 0.68 | 0.671 | 0.657 | 0.643 | 0.625 | 0.609 | 0.594 | 0.574 | 0.563 | 0.548 | 0.532 | 0.518 | 0.511 | 0.505 | 0.497 | 0.487 | 0.479 | 0.473 | 0.468 | 0.465 | 0.461 | 0.455 | 0.447 | 0.444 | 0.445 | 0.444 | 0.441 | 0.438 | 0.441 | 0.444 | 0.445 | 0.445 | 0.448 | 0.457 | 0.475 | 0.491 | 0.504 | 0.509 | 0.512 | 0.51 | 0.502 | 0.492 | 0.482 | 0.471 | 0.459 | 0.447 | 0.436 | 0.424 | 0.414 | 0.403 | 0.394 | 0.387 | 0.382 | 0.376 | 0.37 | 0.369 | 0.369 | 0.367 | 0.363 | 0.355 | 0.347 | 0.335 | 0.328 | 0.323 | 0.32 | 0.323 | 0.327 | 0.334 | 0.336 | 0.339 | 0.346 | 0.356 | 0.366 | 0.376 | 0.394 | 0.421 | 0.453 | 0.486 | 0.518 | 0.551 | 0.583 | 0.61 | 0.633 | 0.647 | 0.658 | 0.666 | 0.669 | 0.667 | 0.661 | 0.659 | 0.657 | 0.658 | 0.66 | 0.662 | 0.662 | 0.656 | 0.649 | 0.635 | 0.62 | 0.601 | 0.579 | 0.561 | 0.543 | 0.525 | 0.574 | 0.558 | 0.545 | 0.532 | 0.522 | 0.512 | 0.502 | 0.495 | 0.489 | 0.485 | 0.482 | 0.479 | 0.476 | 0.47 | 0.464 | 0.46 | 0.459 | 0.457 | 0.455 | 0.451 | 0.45 | 0.451 | 0.454 | 0.461 | 0.473 | 0.492 | 0.519 | 0.547 | 0.576 | 0.603 | 0.63 | 0.658 | 0.681 | 0.696 | 0.699 | 0.695 | 0.685 | 0.671 | 0.653 | 0.638 | 0.624 | 0.611 | 0.598 | 0.591 | 0.587 | 0.586 | 0.583 | 0.581 | 0.575 | 0.564 | 0.55 | 0.539 | 0.535 | 0.537 | 0.538 | 0.538 | 0.538 | 0.541 | 0.546 | 0.546 | 0.545 | 0.546 | 0.553 | 0.562 | 0.573 | 0.587 | 0.605 | 0.62 | 0.634 | 0.644 | 0.658 | 0.668 | 0.68 | 0.689 | 0.701 | 0.713 | 0.724 | 0.729 | 0.732 | 0.729 | 0.723 | 0.717 | 0.709 | 0.703 | 0.697 | 0.69 | 0.683 | 0.681 | 0.68 | 0.679 | 0.673 | 0.663 | 0.65 | 0.635 | 0.619 | 0.596 | 0.584 | 0.566 | 0.552 | 0.541 | 0.531 | 0.518 | 0.508 | 0.501 | 0.497 | 0.492 | 0.489 | 0.484 | 0.479 | 0.471 | 0.466 | 0.462 | 0.46 | 0.458 | 0.454 | 0.45 | 0.448 | 0.447 | 0.447 | 0.449 | 0.455 | 0.471 | 0.493 | 0.515 | 0.531 | 0.545 | 0.557 | 0.57 | 0.576 | 0.578 | 0.575 | 0.572 | 0.565 | 0.553 | 0.538 | 0.527 | 0.518 | 0.51 | 0.502 | 0.496 | 0.497 | 0.497 | 0.494 | 0.487 | 0.48 | 0.473 | 0.464 | 0.456 | 0.451 | 0.45 | 0.448 | 0.445 | 0.442 | 0.442 | 0.444 | 0.447 | 0.449 | 0.449 | 0.451 | 0.452 | 0.458 | 0.47 | 0.489 | 0.51 | 0.528 | 0.543 | 0.563 | 0.589 | 0.619 | 0.647 | 0.669 | 0.682 | 0.688 | 0.691 | 0.695 | 0.697 | 0.697 | 0.69 | 0.681 | 0.672 | 0.665 | 0.658 | 0.653 | 0.655 | 0.659 | 0.66 | 0.655 | 0.643 | 0.628 | 0.611 | 0.597 | 0.583 | 0.57 | 0.557 | 0.543 | 0.53 | 0.519 | 0.509 | 0.5 | 0.492 | 0.484 | 0.479 | 0.476 | 0.472 | 0.469 | 0.463 | 0.458 | 0.452 | 0.45 | 0.447 | 0.445 | 0.439 | 0.437 | 0.435 | 0.434 | 0.434 | 0.44 | 0.453 | 0.472 | 0.491 | 0.505 | 0.515 | 0.52 | 0.517 | 0.51 | 0.499 | 0.488 | 0.476 | 0.465 | 0.452 | 0.438 | 0.425 | 0.417 | 0.408 | 0.398 | 0.388 | 0.384 | 0.384 | 0.383 | 0.381 | 0.381 | 0.378 | 0.374 | 0.369 | 0.364 | 0.357 | 0.353 | 0.347 | 0.346 | 0.345 | 0.351 | 0.356 | 0.362 | 0.367 | 0.374 | 0.38 | 0.389 | 0.404 | 0.424 | 0.448 | 0.475 | 0.503 | 0.533 | 0.567 | 0.598 | 0.625 | 0.645 | 0.658 | 0.669 | 0.677 | 0.684 | 0.683 | 0.679 | 0.675 | 0.672 | 0.67 | 0.666 | 0.664 | 0.66 | 0.661 | 0.663 | 0.66 | 0.65 | 0.634 | 0.615 | 0.597 | 0.581 | 0.564 | 0.596 | 0.579 | 0.565 | 0.553 | 0.542 | 0.532 | 0.522 | 0.516 | 0.51 | 0.505 | 0.501 | 0.498 | 0.494 | 0.489 | 0.484 | 0.481 | 0.479 | 0.476 | 0.473 | 0.471 | 0.473 | 0.476 | 0.479 | 0.485 | 0.494 | 0.512 | 0.535 | 0.562 | 0.589 | 0.611 | 0.635 | 0.662 | 0.683 | 0.696 | 0.697 | 0.694 | 0.686 | 0.674 | 0.658 | 0.643 | 0.628 | 0.615 | 0.602 | 0.594 | 0.591 | 0.589 | 0.587 | 0.585 | 0.58 | 0.57 | 0.558 | 0.548 | 0.542 | 0.541 | 0.542 | 0.543 | 0.543 | 0.545 | 0.548 | 0.55 | 0.551 | 0.554 | 0.561 | 0.57 | 0.58 | 0.592 | 0.608 | 0.624 | 0.638 | 0.651 | 0.666 | 0.68 | 0.694 | 0.707 | 0.722 | 0.737 | 0.748 | 0.754 | 0.755 | 0.755 | 0.751 | 0.746 | 0.737 | 0.732 | 0.726 | 0.723 | 0.719 | 0.718 | 0.715 | 0.709 | 0.7 | 0.689 | 0.675 | 0.658 | 0.642 | 0.627 | 0.628 | 0.608 | 0.592 | 0.579 | 0.568 | 0.555 | 0.543 | 0.535 | 0.528 | 0.523 | 0.519 | 0.516 | 0.512 | 0.505 | 0.499 | 0.495 | 0.493 | 0.49 | 0.488 | 0.487 | 0.487 | 0.486 | 0.484 | 0.487 | 0.493 | 0.508 | 0.527 | 0.549 | 0.567 | 0.582 | 0.592 | 0.604 | 0.61 | 0.612 | 0.605 | 0.6 | 0.594 | 0.587 | 0.575 | 0.56 | 0.547 | 0.535 | 0.527 | 0.521 | 0.518 | 0.517 | 0.513 | 0.509 | 0.505 | 0.501 | 0.492 | 0.482 | 0.473 | 0.471 | 0.47 | 0.466 | 0.462 | 0.464 | 0.469 | 0.472 | 0.475 | 0.477 | 0.483 | 0.485 | 0.492 | 0.5 | 0.516 | 0.532 | 0.552 | 0.572 | 0.598 | 0.625 | 0.654 | 0.68 | 0.702 | 0.719 | 0.73 | 0.737 | 0.741 | 0.744 | 0.742 | 0.737 | 0.728 | 0.723 | 0.719 | 0.716 | 0.712 | 0.711 | 0.709 | 0.704 | 0.694 | 0.679 | 0.663 | 0.646 | 0.63 | 0.615 | 0.6 | 0.586 | 0.575 | 0.563 | 0.55 | 0.539 | 0.527 | 0.518 | 0.511 | 0.506 | 0.504 | 0.502 | 0.497 | 0.49 | 0.482 | 0.478 | 0.475 | 0.473 | 0.47 | 0.467 | 0.466 | 0.466 | 0.467 | 0.469 | 0.476 | 0.49 | 0.51 | 0.53 | 0.544 | 0.553 | 0.556 | 0.556 | 0.548 | 0.538 | 0.525 | 0.512 | 0.501 | 0.49 | 0.478 | 0.464 | 0.452 | 0.441 | 0.433 | 0.425 | 0.418 | 0.412 | 0.406 | 0.401 | 0.397 | 0.394 | 0.391 | 0.385 | 0.38 | 0.373 | 0.366 | 0.36 | 0.359 | 0.363 | 0.37 | 0.377 | 0.382 | 0.389 | 0.395 | 0.402 | 0.409 | 0.422 | 0.44 | 0.463 | 0.487 | 0.516 | 0.547 | 0.582 | 0.614 | 0.639 | 0.66 | 0.674 | 0.685 | 0.69 | 0.692 | 0.693 | 0.692 | 0.692 | 0.688 | 0.687 | 0.685 | 0.686 | 0.687 | 0.69 | 0.691 | 0.685 | 0.673 | 0.656 | 0.638 | 0.621 | 0.604 | 0.587 | 0.583 | 0.567 | 0.551 | 0.538 | 0.528 | 0.519 | 0.51 | 0.503 | 0.499 | 0.494 | 0.491 | 0.489 | 0.487 | 0.482 | 0.476 | 0.472 | 0.471 | 0.469 | 0.466 | 0.466 | 0.471 | 0.479 | 0.487 | 0.499 | 0.516 | 0.536 | 0.559 | 0.583 | 0.608 | 0.629 | 0.651 | 0.675 | 0.696 | 0.708 | 0.71 | 0.708 | 0.7 | 0.687 | 0.669 | 0.654 | 0.638 | 0.623 | 0.609 | 0.599 | 0.594 | 0.591 | 0.586 | 0.582 | 0.576 | 0.567 | 0.555 | 0.545 | 0.54 | 0.538 | 0.538 | 0.538 | 0.539 | 0.542 | 0.547 | 0.549 | 0.553 | 0.557 | 0.563 | 0.572 | 0.584 | 0.597 | 0.614 | 0.631 | 0.649 | 0.664 | 0.682 | 0.697 | 0.712 | 0.723 | 0.736 | 0.749 | 0.762 | 0.77 | 0.771 | 0.772 | 0.77 | 0.769 | 0.765 | 0.763 | 0.762 | 0.759 | 0.751 | 0.738 | 0.721 | 0.702 | 0.684 | 0.667 | 0.65 | 0.634 | 0.619 | 0.605 | 0.596 | 0.578 | 0.563 | 0.55 | 0.541 | 0.531 | 0.522 | 0.516 | 0.511 | 0.508 | 0.506 | 0.504 | 0.501 | 0.495 | 0.487 | 0.482 | 0.48 | 0.478 | 0.474 | 0.472 | 0.475 | 0.48 | 0.484 | 0.494 | 0.508 | 0.527 | 0.545 | 0.563 | 0.58 | 0.593 | 0.604 | 0.614 | 0.619 | 0.622 | 0.62 | 0.619 | 0.615 | 0.608 | 0.592 | 0.573 | 0.559 | 0.546 | 0.534 | 0.525 | 0.522 | 0.522 | 0.519 | 0.511 | 0.504 | 0.496 | 0.486 | 0.474 | 0.464 | 0.459 | 0.455 | 0.453 | 0.455 | 0.46 | 0.467 | 0.469 | 0.47 | 0.471 | 0.475 | 0.481 | 0.49 | 0.502 | 0.522 | 0.542 | 0.562 | 0.578 | 0.599 | 0.626 | 0.657 | 0.684 | 0.705 | 0.721 | 0.734 | 0.741 | 0.741 | 0.741 | 0.739 | 0.736 | 0.733 | 0.732 | 0.734 | 0.733 | 0.728 | 0.72 | 0.709 | 0.694 | 0.677 | 0.656 | 0.637 | 0.621 | 0.606 | 0.596 | 0.582 | 0.566 | 0.552 | 0.539 | 0.531 | 0.522 | 0.514 | 0.506 | 0.5 | 0.496 | 0.493 | 0.492 | 0.49 | 0.486 | 0.478 | 0.472 | 0.469 | 0.466 | 0.46 | 0.456 | 0.458 | 0.464 | 0.472 | 0.482 | 0.496 | 0.512 | 0.529 | 0.545 | 0.556 | 0.561 | 0.561 | 0.56 | 0.557 | 0.549 | 0.537 | 0.524 | 0.512 | 0.498 | 0.484 | 0.471 | 0.46 | 0.449 | 0.439 | 0.431 | 0.427 | 0.424 | 0.419 | 0.413 | 0.411 | 0.407 | 0.401 | 0.393 | 0.386 | 0.38 | 0.373 | 0.367 | 0.363 | 0.366 | 0.373 | 0.379 | 0.384 | 0.39 | 0.398 | 0.407 | 0.417 | 0.433 | 0.455 | 0.482 | 0.512 | 0.54 | 0.571 | 0.606 | 0.639 | 0.668 | 0.684 | 0.698 | 0.707 | 0.712 | 0.714 | 0.717 | 0.722 | 0.725 | 0.726 | 0.728 | 0.731 | 0.731 | 0.725 | 0.713 | 0.697 | 0.678 | 0.658 | 0.637 | 0.618 | 0.6 | 0.586 | 0.576 | 0.537 | 0.523 | 0.509 | 0.498 | 0.489 | 0.481 | 0.474 | 0.469 | 0.465 | 0.462 | 0.461 | 0.46 | 0.459 | 0.455 | 0.449 | 0.444 | 0.442 | 0.439 | 0.436 | 0.436 | 0.441 | 0.452 | 0.467 | 0.487 | 0.512 | 0.541 | 0.576 | 0.61 | 0.643 | 0.67 | 0.697 | 0.727 | 0.751 | 0.766 | 0.768 | 0.763 | 0.751 | 0.737 | 0.718 | 0.697 | 0.676 | 0.656 | 0.641 | 0.63 | 0.622 | 0.616 | 0.611 | 0.603 | 0.592 | 0.579 | 0.565 | 0.555 | 0.548 | 0.549 | 0.549 | 0.55 | 0.551 | 0.554 | 0.559 | 0.562 | 0.566 | 0.572 | 0.58 | 0.593 | 0.606 | 0.622 | 0.639 | 0.657 | 0.673 | 0.686 | 0.702 | 0.717 | 0.733 | 0.745 | 0.758 | 0.773 | 0.788 | 0.801 | 0.808 | 0.813 | 0.814 | 0.812 | 0.802 | 0.786 | 0.765 | 0.744 | 0.722 | 0.699 | 0.678 | 0.658 | 0.639 | 0.621 | 0.604 | 0.588 | 0.573 | 0.559 | 0.548 | 0.531 | 0.517 | 0.507 | 0.5 | 0.492 | 0.484 | 0.476 | 0.472 | 0.468 | 0.467 | 0.466 | 0.465 | 0.459 | 0.453 | 0.449 | 0.446 | 0.44 | 0.436 | 0.434 | 0.438 | 0.443 | 0.452 | 0.468 | 0.486 | 0.508 | 0.531 | 0.555 | 0.575 | 0.589 | 0.601 | 0.615 | 0.625 | 0.632 | 0.635 | 0.636 | 0.631 | 0.618 | 0.603 | 0.584 | 0.566 | 0.547 | 0.534 | 0.523 | 0.52 | 0.519 | 0.515 | 0.505 | 0.496 | 0.486 | 0.476 | 0.464 | 0.456 | 0.45 | 0.448 | 0.445 | 0.445 | 0.447 | 0.448 | 0.449 | 0.452 | 0.458 | 0.468 | 0.476 | 0.484 | 0.495 | 0.513 | 0.538 | 0.562 | 0.582 | 0.601 | 0.629 | 0.665 | 0.697 | 0.72 | 0.733 | 0.747 | 0.754 | 0.762 | 0.767 | 0.772 | 0.773 | 0.769 | 0.757 | 0.741 | 0.722 | 0.707 | 0.69 | 0.673 | 0.657 | 0.641 | 0.622 | 0.6 | 0.582 | 0.568 | 0.556 | 0.542 | 0.528 | 0.516 | 0.506 | 0.498 | 0.491 | 0.482 | 0.474 | 0.467 | 0.463 | 0.46 | 0.457 | 0.454 | 0.45 | 0.445 | 0.439 | 0.434 | 0.43 | 0.427 | 0.424 | 0.425 | 0.431 | 0.44 | 0.455 | 0.471 | 0.492 | 0.514 | 0.536 | 0.553 | 0.563 | 0.566 | 0.567 | 0.564 | 0.56 | 0.55 | 0.537 | 0.525 | 0.514 | 0.504 | 0.49 | 0.475 | 0.462 | 0.452 | 0.442 | 0.436 | 0.431 | 0.427 | 0.423 | 0.421 | 0.419 | 0.417 | 0.411 | 0.406 | 0.4 | 0.397 | 0.392 | 0.388 | 0.388 | 0.395 | 0.401 | 0.408 | 0.415 | 0.424 | 0.433 | 0.44 | 0.455 | 0.479 | 0.512 | 0.544 | 0.573 | 0.601 | 0.635 | 0.666 | 0.696 | 0.718 | 0.735 | 0.744 | 0.746 | 0.749 | 0.753 | 0.757 | 0.757 | 0.753 | 0.742 | 0.73 | 0.712 | 0.696 | 0.675 | 0.655 | 0.632 | 0.61 | 0.586 | 0.565 | 0.546 | 0.532 | 0.519 | 0.532 | 0.517 | 0.504 | 0.494 | 0.486 | 0.479 | 0.473 | 0.467 | 0.462 | 0.458 | 0.455 | 0.455 | 0.454 | 0.45 | 0.445 | 0.441 | 0.439 | 0.437 | 0.435 | 0.436 | 0.441 | 0.453 | 0.468 | 0.491 | 0.514 | 0.542 | 0.577 | 0.618 | 0.661 | 0.702 | 0.742 | 0.782 | 0.811 | 0.826 | 0.826 | 0.819 | 0.807 | 0.794 | 0.779 | 0.763 | 0.744 | 0.727 | 0.711 | 0.699 | 0.687 | 0.678 | 0.67 | 0.663 | 0.653 | 0.638 | 0.622 | 0.61 | 0.605 | 0.605 | 0.605 | 0.605 | 0.606 | 0.61 | 0.615 | 0.619 | 0.623 | 0.628 | 0.637 | 0.651 | 0.666 | 0.685 | 0.706 | 0.727 | 0.742 | 0.757 | 0.773 | 0.791 | 0.806 | 0.82 | 0.838 | 0.857 | 0.872 | 0.879 | 0.878 | 0.865 | 0.844 | 0.822 | 0.802 | 0.782 | 0.761 | 0.738 | 0.716 | 0.695 | 0.675 | 0.655 | 0.636 | 0.621 | 0.604 | 0.589 | 0.573 | 0.559 | 0.559 | 0.542 | 0.526 | 0.515 | 0.505 | 0.496 | 0.487 | 0.482 | 0.476 | 0.472 | 0.469 | 0.468 | 0.466 | 0.461 | 0.456 | 0.451 | 0.449 | 0.445 | 0.443 | 0.444 | 0.448 | 0.457 | 0.467 | 0.486 | 0.506 | 0.531 | 0.558 | 0.589 | 0.619 | 0.645 | 0.668 | 0.689 | 0.701 | 0.707 | 0.707 | 0.707 | 0.704 | 0.698 | 0.686 | 0.672 | 0.658 | 0.645 | 0.632 | 0.618 | 0.606 | 0.6 | 0.597 | 0.591 | 0.582 | 0.572 | 0.563 | 0.556 | 0.548 | 0.542 | 0.536 | 0.533 | 0.53 | 0.53 | 0.531 | 0.537 | 0.544 | 0.553 | 0.564 | 0.574 | 0.582 | 0.594 | 0.614 | 0.641 | 0.668 | 0.691 | 0.714 | 0.742 | 0.775 | 0.807 | 0.833 | 0.852 | 0.864 | 0.866 | 0.86 | 0.846 | 0.829 | 0.807 | 0.786 | 0.766 | 0.746 | 0.725 | 0.707 | 0.693 | 0.68 | 0.665 | 0.65 | 0.633 | 0.614 | 0.596 | 0.581 | 0.568 | 0.553 | 0.537 | 0.523 | 0.513 | 0.507 | 0.5 | 0.494 | 0.487 | 0.481 | 0.474 | 0.469 | 0.464 | 0.462 | 0.457 | 0.452 | 0.446 | 0.443 | 0.441 | 0.439 | 0.439 | 0.443 | 0.452 | 0.463 | 0.48 | 0.497 | 0.52 | 0.544 | 0.57 | 0.595 | 0.613 | 0.625 | 0.627 | 0.625 | 0.617 | 0.607 | 0.596 | 0.586 | 0.578 | 0.569 | 0.56 | 0.551 | 0.541 | 0.533 | 0.523 | 0.52 | 0.514 | 0.507 | 0.498 | 0.492 | 0.489 | 0.485 | 0.478 | 0.472 | 0.467 | 0.461 | 0.456 | 0.454 | 0.457 | 0.464 | 0.471 | 0.481 | 0.489 | 0.5 | 0.511 | 0.525 | 0.545 | 0.57 | 0.602 | 0.633 | 0.663 | 0.691 | 0.723 | 0.757 | 0.787 | 0.808 | 0.822 | 0.83 | 0.83 | 0.825 | 0.811 | 0.795 | 0.779 | 0.763 | 0.745 | 0.726 | 0.709 | 0.691 | 0.673 | 0.655 | 0.637 | 0.616 | 0.597 | 0.576 | 0.557 | 0.54 | 0.528 | 0.557 | 0.544 | 0.53 | 0.52 | 0.512 | 0.505 | 0.498 | 0.493 | 0.489 | 0.485 | 0.48 | 0.478 | 0.475 | 0.471 | 0.466 | 0.46 | 0.458 | 0.456 | 0.456 | 0.461 | 0.471 | 0.486 | 0.503 | 0.525 | 0.551 | 0.581 | 0.617 | 0.656 | 0.698 | 0.737 | 0.776 | 0.817 | 0.846 | 0.862 | 0.862 | 0.857 | 0.848 | 0.837 | 0.825 | 0.814 | 0.802 | 0.788 | 0.773 | 0.762 | 0.756 | 0.753 | 0.749 | 0.744 | 0.736 | 0.724 | 0.71 | 0.701 | 0.697 | 0.7 | 0.706 | 0.711 | 0.717 | 0.724 | 0.733 | 0.741 | 0.747 | 0.755 | 0.769 | 0.787 | 0.81 | 0.836 | 0.868 | 0.898 | 0.922 | 0.938 | 0.947 | 0.945 | 0.94 | 0.929 | 0.925 | 0.923 | 0.924 | 0.919 | 0.906 | 0.887 | 0.865 | 0.842 | 0.82 | 0.799 | 0.778 | 0.757 | 0.738 | 0.717 | 0.697 | 0.676 | 0.656 | 0.643 | 0.629 | 0.615 | 0.598 | 0.582 | 0.582 | 0.568 | 0.556 | 0.547 | 0.54 | 0.533 | 0.525 | 0.516 | 0.508 | 0.501 | 0.494 | 0.49 | 0.487 | 0.483 | 0.48 | 0.474 | 0.469 | 0.463 | 0.461 | 0.465 | 0.475 | 0.488 | 0.502 | 0.518 | 0.536 | 0.558 | 0.585 | 0.618 | 0.65 | 0.678 | 0.7 | 0.721 | 0.735 | 0.74 | 0.739 | 0.74 | 0.741 | 0.741 | 0.732 | 0.723 | 0.713 | 0.702 | 0.693 | 0.687 | 0.683 | 0.679 | 0.674 | 0.669 | 0.661 | 0.654 | 0.645 | 0.639 | 0.633 | 0.633 | 0.635 | 0.637 | 0.637 | 0.641 | 0.649 | 0.659 | 0.667 | 0.674 | 0.685 | 0.697 | 0.715 | 0.738 | 0.773 | 0.81 | 0.845 | 0.869 | 0.885 | 0.895 | 0.907 | 0.911 | 0.912 | 0.906 | 0.898 | 0.885 | 0.871 | 0.852 | 0.832 | 0.811 | 0.79 | 0.769 | 0.751 | 0.736 | 0.723 | 0.706 | 0.689 | 0.67 | 0.653 | 0.638 | 0.624 | 0.61 | 0.593 | 0.578 | 0.565 | 0.554 | 0.541 | 0.531 | 0.523 | 0.516 | 0.51 | 0.503 | 0.498 | 0.493 | 0.487 | 0.482 | 0.479 | 0.472 | 0.468 | 0.46 | 0.458 | 0.455 | 0.454 | 0.455 | 0.46 | 0.469 | 0.48 | 0.494 | 0.511 | 0.532 | 0.557 | 0.585 | 0.612 | 0.632 | 0.644 | 0.647 | 0.647 | 0.644 | 0.637 | 0.628 | 0.618 | 0.609 | 0.602 | 0.598 | 0.595 | 0.589 | 0.583 | 0.579 | 0.577 | 0.574 | 0.569 | 0.566 | 0.563 | 0.558 | 0.554 | 0.552 | 0.552 | 0.55 | 0.548 | 0.548 | 0.551 | 0.558 | 0.568 | 0.579 | 0.591 | 0.601 | 0.614 | 0.627 | 0.647 | 0.672 | 0.71 | 0.751 | 0.789 | 0.814 | 0.834 | 0.851 | 0.862 | 0.866 | 0.866 | 0.865 | 0.859 | 0.848 | 0.834 | 0.822 | 0.808 | 0.792 | 0.774 | 0.753 | 0.734 | 0.715 | 0.699 | 0.681 | 0.662 | 0.641 | 0.621 | 0.604 | 0.587 | 0.569 | 0.549 | 0.536 | 0.586 | 0.572 | 0.559 | 0.549 | 0.54 | 0.53 | 0.521 | 0.514 | 0.511 | 0.511 | 0.507 | 0.503 | 0.497 | 0.491 | 0.486 | 0.484 | 0.484 | 0.484 | 0.483 | 0.485 | 0.491 | 0.505 | 0.522 | 0.545 | 0.567 | 0.594 | 0.626 | 0.664 | 0.704 | 0.742 | 0.784 | 0.829 | 0.868 | 0.895 | 0.907 | 0.908 | 0.902 | 0.896 | 0.886 | 0.879 | 0.869 | 0.857 | 0.842 | 0.831 | 0.826 | 0.823 | 0.819 | 0.811 | 0.8 | 0.786 | 0.773 | 0.765 | 0.762 | 0.765 | 0.768 | 0.771 | 0.774 | 0.781 | 0.79 | 0.798 | 0.801 | 0.806 | 0.817 | 0.833 | 0.854 | 0.881 | 0.913 | 0.939 | 0.955 | 0.961 | 0.964 | 0.96 | 0.955 | 0.946 | 0.941 | 0.937 | 0.933 | 0.924 | 0.911 | 0.892 | 0.873 | 0.852 | 0.832 | 0.811 | 0.792 | 0.774 | 0.758 | 0.74 | 0.721 | 0.7 | 0.682 | 0.669 | 0.658 | 0.645 | 0.627 | 0.608 | 0.596 | 0.588 | 0.58 | 0.572 | 0.562 | 0.554 | 0.544 | 0.536 | 0.53 | 0.525 | 0.52 | 0.514 | 0.507 | 0.499 | 0.495 | 0.493 | 0.493 | 0.49 | 0.487 | 0.489 | 0.495 | 0.507 | 0.521 | 0.539 | 0.558 | 0.579 | 0.606 | 0.637 | 0.668 | 0.694 | 0.719 | 0.746 | 0.773 | 0.79 | 0.798 | 0.799 | 0.799 | 0.792 | 0.785 | 0.778 | 0.771 | 0.763 | 0.752 | 0.745 | 0.741 | 0.742 | 0.741 | 0.735 | 0.727 | 0.718 | 0.71 | 0.703 | 0.7 | 0.7 | 0.701 | 0.7 | 0.701 | 0.708 | 0.72 | 0.73 | 0.734 | 0.738 | 0.748 | 0.76 | 0.778 | 0.8 | 0.835 | 0.862 | 0.882 | 0.891 | 0.901 | 0.91 | 0.919 | 0.92 | 0.919 | 0.907 | 0.898 | 0.885 | 0.873 | 0.858 | 0.842 | 0.825 | 0.808 | 0.79 | 0.772 | 0.753 | 0.741 | 0.723 | 0.708 | 0.69 | 0.677 | 0.665 | 0.652 | 0.638 | 0.623 | 0.604 | 0.591 | 0.582 | 0.572 | 0.561 | 0.551 | 0.542 | 0.532 | 0.524 | 0.52 | 0.517 | 0.512 | 0.506 | 0.5 | 0.495 | 0.49 | 0.485 | 0.484 | 0.481 | 0.48 | 0.479 | 0.486 | 0.496 | 0.506 | 0.52 | 0.535 | 0.558 | 0.581 | 0.609 | 0.632 | 0.65 | 0.668 | 0.681 | 0.694 | 0.696 | 0.692 | 0.686 | 0.682 | 0.68 | 0.678 | 0.676 | 0.669 | 0.659 | 0.651 | 0.648 | 0.65 | 0.651 | 0.647 | 0.644 | 0.641 | 0.64 | 0.637 | 0.634 | 0.63 | 0.627 | 0.628 | 0.629 | 0.633 | 0.636 | 0.643 | 0.649 | 0.66 | 0.673 | 0.688 | 0.702 | 0.72 | 0.744 | 0.782 | 0.817 | 0.844 | 0.86 | 0.877 | 0.897 | 0.911 | 0.914 | 0.91 | 0.902 | 0.893 | 0.879 | 0.865 | 0.848 | 0.833 | 0.817 | 0.801 | 0.784 | 0.766 | 0.751 | 0.733 | 0.715 | 0.695 | 0.675 | 0.658 | 0.641 | 0.623 | 0.604 | 0.583 | 0.57
E3A | -3456 | 0.404 | 0.402 | 0.4 | 0.401 | 0.402 | 0.401 | 0.4 | 0.399 | 0.397 | 0.395 | 0.395 | 0.395 | 0.396 | 0.396 | 0.396 | 0.396 | 0.398 | 0.399 | 0.401 | 0.403 | 0.408 | 0.414 | 0.422 | 0.433 | 0.449 | 0.47 | 0.496 | 0.534 | 0.582 | 0.642 | 0.705 | 0.778 | 0.84 | 0.892 | 0.926 | 0.948 | 0.963 | 0.969 | 0.973 | 0.975 | 0.98 | 0.987 | 0.994 | 0.998 | 1 | 1 | 1 | 0.994 | 0.982 | 0.963 | 0.948 | 0.945 | 0.956 | 0.97 | 0.978 | 0.979 | 0.978 | 0.973 | 0.967 | 0.954 | 0.945 | 0.937 | 0.933 | 0.92 | 0.899 | 0.867 | 0.835 | 0.798 | 0.764 | 0.73 | 0.703 | 0.675 | 0.651 | 0.629 | 0.616 | 0.607 | 0.6 | 0.592 | 0.585 | 0.576 | 0.567 | 0.557 | 0.549 | 0.539 | 0.528 | 0.515 | 0.503 | 0.489 | 0.476 | 0.462 | 0.453 | 0.446 | 0.441 | 0.435 | 0.425 | 0.417 | 0.414 | 0.41 | 0.407 | 0.408 | 0.408 | 0.408 | 0.405 | 0.404 | 0.401 | 0.399 | 0.398 | 0.398 | 0.398 | 0.397 | 0.396 | 0.395 | 0.396 | 0.396 | 0.398 | 0.398 | 0.4 | 0.403 | 0.406 | 0.409 | 0.413 | 0.417 | 0.423 | 0.432 | 0.441 | 0.451 | 0.462 | 0.478 | 0.49 | 0.501 | 0.506 | 0.516 | 0.526 | 0.537 | 0.546 | 0.554 | 0.561 | 0.566 | 0.57 | 0.572 | 0.573 | 0.574 | 0.573 | 0.571 | 0.566 | 0.561 | 0.554 | 0.551 | 0.548 | 0.546 | 0.544 | 0.543 | 0.541 | 0.539 | 0.536 | 0.533 | 0.531 | 0.529 | 0.527 | 0.525 | 0.524 | 0.522 | 0.522 | 0.52 | 0.52 | 0.519 | 0.518 | 0.512 | 0.505 | 0.5 | 0.497 | 0.496 | 0.494 | 0.491 | 0.488 | 0.485 | 0.482 | 0.478 | 0.474 | 0.469 | 0.466 | 0.462 | 0.462 | 0.458 | 0.454 | 0.448 | 0.445 | 0.44 | 0.437 | 0.433 | 0.426 | 0.407 | 0.407 | 0.404 | 0.403 | 0.404 | 0.404 | 0.404 | 0.402 | 0.4 | 0.398 | 0.395 | 0.394 | 0.393 | 0.394 | 0.393 | 0.392 | 0.389 | 0.39 | 0.391 | 0.392 | 0.392 | 0.393 | 0.394 | 0.396 | 0.396 | 0.397 | 0.397 | 0.399 | 0.402 | 0.406 | 0.409 | 0.409 | 0.412 | 0.412 | 0.411 | 0.407 | 0.404 | 0.405 | 0.406 | 0.408 | 0.41 | 0.412 | 0.416 | 0.42 | 0.423 | 0.426 | 0.427 | 0.431 | 0.433 | 0.435 | 0.435 | 0.436 | 0.437 | 0.438 | 0.438 | 0.438 | 0.438 | 0.439 | 0.439 | 0.439 | 0.438 | 0.438 | 0.436 | 0.436 | 0.437 | 0.437 | 0.439 | 0.442 | 0.45 | 0.459 | 0.466 | 0.471 | 0.472 | 0.471 | 0.469 | 0.467 | 0.464 | 0.462 | 0.46 | 0.458 | 0.455 | 0.452 | 0.45 | 0.448 | 0.445 | 0.443 | 0.441 | 0.439 | 0.435 | 0.43 | 0.425 | 0.421 | 0.418 | 0.416 | 0.411 | 0.404 | 0.397 | 0.399 | 0.397 | 0.396 | 0.397 | 0.397 | 0.396 | 0.395 | 0.394 | 0.393 | 0.391 | 0.39 | 0.39 | 0.391 | 0.39 | 0.39 | 0.389 | 0.391 | 0.391 | 0.394 | 0.397 | 0.401 | 0.407 | 0.416 | 0.427 | 0.443 | 0.464 | 0.491 | 0.529 | 0.576 | 0.634 | 0.693 | 0.755 | 0.811 | 0.859 | 0.895 | 0.922 | 0.939 | 0.947 | 0.951 | 0.955 | 0.961 | 0.968 | 0.975 | 0.979 | 0.981 | 0.982 | 0.982 | 0.976 | 0.965 | 0.947 | 0.93 | 0.926 | 0.936 | 0.951 | 0.958 | 0.959 | 0.958 | 0.952 | 0.946 | 0.934 | 0.925 | 0.917 | 0.911 | 0.897 | 0.874 | 0.841 | 0.805 | 0.763 | 0.722 | 0.684 | 0.66 | 0.642 | 0.63 | 0.62 | 0.613 | 0.606 | 0.6 | 0.593 | 0.586 | 0.578 | 0.569 | 0.559 | 0.549 | 0.538 | 0.526 | 0.513 | 0.499 | 0.485 | 0.47 | 0.457 | 0.446 | 0.437 | 0.431 | 0.424 | 0.415 | 0.409 | 0.398 | 0.395 | 0.392 | 0.393 | 0.392 | 0.392 | 0.391 | 0.39 | 0.389 | 0.386 | 0.385 | 0.384 | 0.386 | 0.383 | 0.384 | 0.383 | 0.384 | 0.383 | 0.386 | 0.386 | 0.389 | 0.389 | 0.393 | 0.395 | 0.4 | 0.403 | 0.409 | 0.417 | 0.425 | 0.434 | 0.441 | 0.45 | 0.459 | 0.469 | 0.48 | 0.494 | 0.507 | 0.519 | 0.527 | 0.536 | 0.544 | 0.551 | 0.555 | 0.559 | 0.562 | 0.562 | 0.563 | 0.561 | 0.556 | 0.549 | 0.542 | 0.538 | 0.535 | 0.533 | 0.532 | 0.529 | 0.527 | 0.523 | 0.52 | 0.515 | 0.513 | 0.51 | 0.509 | 0.505 | 0.502 | 0.497 | 0.494 | 0.488 | 0.483 | 0.476 | 0.474 | 0.474 | 0.476 | 0.478 | 0.477 | 0.477 | 0.475 | 0.473 | 0.471 | 0.468 | 0.464 | 0.46 | 0.457 | 0.454 | 0.45 | 0.447 | 0.445 | 0.442 | 0.438 | 0.434 | 0.431 | 0.426 | 0.422 | 0.418 | 0.411 | 0.405 | 0.398 | 0.397 | 0.396 | 0.398 | 0.399 | 0.399 | 0.398 | 0.397 | 0.394 | 0.391 | 0.389 | 0.388 | 0.39 | 0.388 | 0.388 | 0.385 | 0.385 | 0.384 | 0.384 | 0.384 | 0.386 | 0.388 | 0.389 | 0.387 | 0.389 | 0.389 | 0.391 | 0.392 | 0.394 | 0.394 | 0.392 | 0.387 | 0.383 | 0.379 | 0.38 | 0.382 | 0.387 | 0.39 | 0.394 | 0.399 | 0.403 | 0.407 | 0.41 | 0.413 | 0.417 | 0.42 | 0.423 | 0.424 | 0.424 | 0.425 | 0.426 | 0.428 | 0.429 | 0.429 | 0.429 | 0.43 | 0.429 | 0.428 | 0.427 | 0.428 | 0.428 | 0.428 | 0.428 | 0.427 | 0.428 | 0.428 | 0.428 | 0.429 | 0.431 | 0.433 | 0.437 | 0.443 | 0.452 | 0.458 | 0.462 | 0.462 | 0.46 | 0.458 | 0.456 | 0.454 | 0.451 | 0.449 | 0.447 | 0.443 | 0.44 | 0.437 | 0.435 | 0.432 | 0.428 | 0.423 | 0.419 | 0.415 | 0.412 | 0.408 | 0.401 | 0.395 | 0.368 | 0.365 | 0.363 | 0.364 | 0.364 | 0.365 | 0.362 | 0.361 | 0.36 | 0.359 | 0.358 | 0.359 | 0.36 | 0.36 | 0.361 | 0.36 | 0.362 | 0.363 | 0.366 | 0.369 | 0.374 | 0.381 | 0.389 | 0.401 | 0.416 | 0.435 | 0.456 | 0.486 | 0.524 | 0.573 | 0.628 | 0.69 | 0.747 | 0.798 | 0.836 | 0.865 | 0.883 | 0.892 | 0.897 | 0.9 | 0.907 | 0.915 | 0.922 | 0.925 | 0.927 | 0.928 | 0.928 | 0.922 | 0.91 | 0.891 | 0.874 | 0.871 | 0.881 | 0.896 | 0.905 | 0.907 | 0.905 | 0.9 | 0.893 | 0.881 | 0.872 | 0.864 | 0.858 | 0.845 | 0.822 | 0.789 | 0.753 | 0.709 | 0.667 | 0.625 | 0.594 | 0.566 | 0.547 | 0.537 | 0.541 | 0.55 | 0.559 | 0.562 | 0.561 | 0.557 | 0.553 | 0.548 | 0.541 | 0.531 | 0.517 | 0.503 | 0.487 | 0.47 | 0.451 | 0.435 | 0.421 | 0.41 | 0.402 | 0.395 | 0.385 | 0.379 | 0.369 | 0.366 | 0.362 | 0.363 | 0.363 | 0.363 | 0.36 | 0.359 | 0.356 | 0.354 | 0.353 | 0.353 | 0.355 | 0.355 | 0.354 | 0.353 | 0.354 | 0.354 | 0.356 | 0.356 | 0.358 | 0.36 | 0.363 | 0.365 | 0.368 | 0.368 | 0.368 | 0.369 | 0.373 | 0.378 | 0.386 | 0.399 | 0.413 | 0.428 | 0.443 | 0.459 | 0.473 | 0.484 | 0.492 | 0.501 | 0.509 | 0.517 | 0.521 | 0.524 | 0.526 | 0.526 | 0.525 | 0.522 | 0.515 | 0.507 | 0.501 | 0.498 | 0.495 | 0.493 | 0.492 | 0.49 | 0.488 | 0.485 | 0.483 | 0.48 | 0.477 | 0.475 | 0.472 | 0.469 | 0.464 | 0.46 | 0.455 | 0.449 | 0.441 | 0.435 | 0.428 | 0.422 | 0.416 | 0.417 | 0.423 | 0.432 | 0.439 | 0.442 | 0.442 | 0.439 | 0.435 | 0.43 | 0.427 | 0.423 | 0.422 | 0.419 | 0.416 | 0.412 | 0.407 | 0.403 | 0.399 | 0.393 | 0.39 | 0.386 | 0.381 | 0.375 | 0.366 | 0.364 | 0.363 | 0.365 | 0.365 | 0.366 | 0.363 | 0.364 | 0.361 | 0.36 | 0.358 | 0.357 | 0.357 | 0.357 | 0.356 | 0.354 | 0.355 | 0.354 | 0.356 | 0.355 | 0.355 | 0.356 | 0.356 | 0.358 | 0.357 | 0.357 | 0.356 | 0.354 | 0.35 | 0.346 | 0.342 | 0.341 | 0.342 | 0.345 | 0.349 | 0.354 | 0.359 | 0.363 | 0.367 | 0.37 | 0.374 | 0.377 | 0.378 | 0.381 | 0.383 | 0.386 | 0.386 | 0.388 | 0.39 | 0.391 | 0.391 | 0.392 | 0.394 | 0.394 | 0.393 | 0.391 | 0.391 | 0.389 | 0.389 | 0.386 | 0.387 | 0.385 | 0.386 | 0.384 | 0.383 | 0.382 | 0.382 | 0.381 | 0.38 | 0.378 | 0.377 | 0.376 | 0.379 | 0.382 | 0.39 | 0.397 | 0.404 | 0.406 | 0.407 | 0.406 | 0.407 | 0.407 | 0.407 | 0.405 | 0.403 | 0.4 | 0.397 | 0.394 | 0.39 | 0.386 | 0.382 | 0.379 | 0.376 | 0.374 | 0.368 | 0.363 | 0.338 | 0.334 | 0.331 | 0.334 | 0.334 | 0.334 | 0.332 | 0.33 | 0.328 | 0.327 | 0.327 | 0.327 | 0.329 | 0.329 | 0.329 | 0.328 | 0.33 | 0.331 | 0.335 | 0.337 | 0.342 | 0.347 | 0.354 | 0.364 | 0.376 | 0.391 | 0.408 | 0.433 | 0.467 | 0.513 | 0.564 | 0.622 | 0.675 | 0.723 | 0.759 | 0.785 | 0.802 | 0.811 | 0.816 | 0.82 | 0.828 | 0.837 | 0.844 | 0.848 | 0.851 | 0.853 | 0.855 | 0.85 | 0.839 | 0.822 | 0.808 | 0.805 | 0.815 | 0.828 | 0.837 | 0.839 | 0.838 | 0.832 | 0.826 | 0.815 | 0.807 | 0.799 | 0.793 | 0.781 | 0.76 | 0.731 | 0.699 | 0.658 | 0.619 | 0.58 | 0.549 | 0.521 | 0.495 | 0.476 | 0.464 | 0.457 | 0.452 | 0.448 | 0.446 | 0.447 | 0.452 | 0.463 | 0.477 | 0.486 | 0.488 | 0.48 | 0.469 | 0.453 | 0.436 | 0.418 | 0.403 | 0.389 | 0.379 | 0.37 | 0.36 | 0.351 | 0.35 | 0.345 | 0.34 | 0.341 | 0.341 | 0.34 | 0.336 | 0.334 | 0.332 | 0.331 | 0.331 | 0.331 | 0.332 | 0.331 | 0.331 | 0.33 | 0.33 | 0.331 | 0.334 | 0.334 | 0.335 | 0.335 | 0.336 | 0.336 | 0.336 | 0.335 | 0.335 | 0.335 | 0.339 | 0.345 | 0.354 | 0.367 | 0.382 | 0.395 | 0.408 | 0.421 | 0.433 | 0.443 | 0.452 | 0.46 | 0.467 | 0.473 | 0.477 | 0.479 | 0.482 | 0.482 | 0.483 | 0.481 | 0.477 | 0.471 | 0.466 | 0.463 | 0.461 | 0.459 | 0.458 | 0.457 | 0.455 | 0.452 | 0.448 | 0.445 | 0.443 | 0.44 | 0.437 | 0.435 | 0.431 | 0.426 | 0.421 | 0.414 | 0.407 | 0.399 | 0.39 | 0.383 | 0.376 | 0.374 | 0.372 | 0.371 | 0.371 | 0.371 | 0.369 | 0.369 | 0.369 | 0.374 | 0.381 | 0.389 | 0.395 | 0.396 | 0.395 | 0.391 | 0.386 | 0.381 | 0.378 | 0.373 | 0.37 | 0.364 | 0.357 | 0.356 | 0.349 | 0.346 | 0.345 | 0.347 | 0.347 | 0.346 | 0.344 | 0.343 | 0.341 | 0.339 | 0.338 | 0.337 | 0.337 | 0.336 | 0.334 | 0.332 | 0.332 | 0.332 | 0.334 | 0.334 | 0.335 | 0.337 | 0.337 | 0.336 | 0.334 | 0.331 | 0.327 | 0.321 | 0.318 | 0.315 | 0.314 | 0.316 | 0.319 | 0.323 | 0.327 | 0.333 | 0.338 | 0.343 | 0.346 | 0.349 | 0.354 | 0.359 | 0.362 | 0.362 | 0.365 | 0.368 | 0.37 | 0.371 | 0.372 | 0.374 | 0.374 | 0.375 | 0.375 | 0.375 | 0.371 | 0.369 | 0.369 | 0.367 | 0.368 | 0.366 | 0.366 | 0.362 | 0.361 | 0.36 | 0.36 | 0.358 | 0.356 | 0.354 | 0.353 | 0.351 | 0.349 | 0.346 | 0.343 | 0.341 | 0.341 | 0.342 | 0.342 | 0.34 | 0.34 | 0.341 | 0.345 | 0.351 | 0.359 | 0.366 | 0.373 | 0.375 | 0.374 | 0.369 | 0.365 | 0.359 | 0.355 | 0.351 | 0.346 | 0.342 | 0.336 | 0.335 | 0.331 | 0.327 | 0.323 | 0.325 | 0.326 | 0.325 | 0.323 | 0.321 | 0.32 | 0.318 | 0.318 | 0.317 | 0.319 | 0.318 | 0.319 | 0.318 | 0.32 | 0.32 | 0.322 | 0.323 | 0.325 | 0.326 | 0.326 | 0.33 | 0.336 | 0.348 | 0.364 | 0.392 | 0.429 | 0.475 | 0.525 | 0.58 | 0.631 | 0.674 | 0.708 | 0.732 | 0.749 | 0.759 | 0.765 | 0.769 | 0.777 | 0.786 | 0.795 | 0.799 | 0.804 | 0.806 | 0.809 | 0.805 | 0.797 | 0.783 | 0.771 | 0.768 | 0.778 | 0.792 | 0.8 | 0.802 | 0.802 | 0.797 | 0.792 | 0.783 | 0.777 | 0.771 | 0.768 | 0.757 | 0.738 | 0.711 | 0.681 | 0.642 | 0.605 | 0.567 | 0.537 | 0.509 | 0.484 | 0.464 | 0.452 | 0.443 | 0.436 | 0.43 | 0.425 | 0.42 | 0.415 | 0.412 | 0.411 | 0.413 | 0.418 | 0.424 | 0.426 | 0.423 | 0.415 | 0.403 | 0.391 | 0.379 | 0.369 | 0.361 | 0.352 | 0.345 | 0.34 | 0.335 | 0.331 | 0.333 | 0.332 | 0.33 | 0.326 | 0.324 | 0.321 | 0.318 | 0.315 | 0.315 | 0.316 | 0.315 | 0.314 | 0.312 | 0.314 | 0.314 | 0.315 | 0.314 | 0.313 | 0.309 | 0.304 | 0.299 | 0.296 | 0.296 | 0.298 | 0.303 | 0.311 | 0.319 | 0.33 | 0.343 | 0.358 | 0.372 | 0.387 | 0.401 | 0.416 | 0.427 | 0.436 | 0.444 | 0.451 | 0.457 | 0.461 | 0.464 | 0.466 | 0.468 | 0.469 | 0.469 | 0.465 | 0.461 | 0.455 | 0.451 | 0.45 | 0.449 | 0.449 | 0.448 | 0.446 | 0.444 | 0.442 | 0.439 | 0.436 | 0.433 | 0.432 | 0.429 | 0.427 | 0.423 | 0.418 | 0.41 | 0.402 | 0.393 | 0.386 | 0.379 | 0.372 | 0.367 | 0.364 | 0.363 | 0.361 | 0.361 | 0.361 | 0.358 | 0.355 | 0.353 | 0.353 | 0.354 | 0.355 | 0.361 | 0.366 | 0.37 | 0.371 | 0.369 | 0.366 | 0.362 | 0.359 | 0.353 | 0.346 | 0.338 | 0.331 | 0.327 | 0.323 | 0.325 | 0.325 | 0.324 | 0.322 | 0.32 | 0.319 | 0.316 | 0.315 | 0.314 | 0.314 | 0.313 | 0.313 | 0.311 | 0.312 | 0.312 | 0.313 | 0.311 | 0.31 | 0.307 | 0.301 | 0.295 | 0.29 | 0.286 | 0.284 | 0.284 | 0.286 | 0.289 | 0.293 | 0.297 | 0.3 | 0.304 | 0.308 | 0.314 | 0.319 | 0.325 | 0.329 | 0.335 | 0.34 | 0.344 | 0.348 | 0.349 | 0.353 | 0.356 | 0.358 | 0.359 | 0.36 | 0.362 | 0.363 | 0.364 | 0.364 | 0.363 | 0.362 | 0.359 | 0.358 | 0.356 | 0.355 | 0.353 | 0.353 | 0.352 | 0.352 | 0.351 | 0.35 | 0.349 | 0.348 | 0.348 | 0.347 | 0.346 | 0.344 | 0.342 | 0.34 | 0.338 | 0.338 | 0.336 | 0.336 | 0.334 | 0.335 | 0.333 | 0.333 | 0.332 | 0.333 | 0.335 | 0.339 | 0.344 | 0.35 | 0.353 | 0.354 | 0.351 | 0.347 | 0.344 | 0.34 | 0.336 | 0.331 | 0.327 | 0.333 | 0.329 | 0.326 | 0.327 | 0.327 | 0.326 | 0.324 | 0.321 | 0.32 | 0.318 | 0.317 | 0.317 | 0.318 | 0.318 | 0.318 | 0.317 | 0.318 | 0.318 | 0.32 | 0.318 | 0.316 | 0.312 | 0.311 | 0.317 | 0.328 | 0.342 | 0.36 | 0.393 | 0.433 | 0.485 | 0.539 | 0.599 | 0.656 | 0.706 | 0.745 | 0.772 | 0.792 | 0.804 | 0.812 | 0.818 | 0.827 | 0.838 | 0.847 | 0.854 | 0.859 | 0.862 | 0.864 | 0.86 | 0.852 | 0.836 | 0.822 | 0.819 | 0.83 | 0.845 | 0.854 | 0.856 | 0.856 | 0.852 | 0.846 | 0.836 | 0.829 | 0.824 | 0.819 | 0.807 | 0.786 | 0.756 | 0.722 | 0.679 | 0.638 | 0.596 | 0.563 | 0.531 | 0.504 | 0.481 | 0.467 | 0.455 | 0.447 | 0.44 | 0.434 | 0.427 | 0.42 | 0.413 | 0.408 | 0.403 | 0.398 | 0.395 | 0.394 | 0.395 | 0.396 | 0.394 | 0.388 | 0.379 | 0.371 | 0.364 | 0.354 | 0.345 | 0.335 | 0.329 | 0.323 | 0.323 | 0.323 | 0.32 | 0.318 | 0.314 | 0.313 | 0.309 | 0.308 | 0.306 | 0.306 | 0.304 | 0.304 | 0.301 | 0.302 | 0.301 | 0.302 | 0.299 | 0.293 | 0.286 | 0.28 | 0.279 | 0.28 | 0.282 | 0.283 | 0.29 | 0.298 | 0.31 | 0.322 | 0.337 | 0.352 | 0.365 | 0.378 | 0.391 | 0.406 | 0.418 | 0.429 | 0.437 | 0.445 | 0.451 | 0.455 | 0.459 | 0.462 | 0.464 | 0.465 | 0.463 | 0.459 | 0.454 | 0.449 | 0.446 | 0.444 | 0.443 | 0.441 | 0.439 | 0.436 | 0.434 | 0.432 | 0.43 | 0.429 | 0.427 | 0.425 | 0.42 | 0.417 | 0.412 | 0.408 | 0.401 | 0.393 | 0.384 | 0.377 | 0.369 | 0.362 | 0.357 | 0.355 | 0.354 | 0.352 | 0.351 | 0.349 | 0.349 | 0.347 | 0.345 | 0.343 | 0.341 | 0.339 | 0.338 | 0.338 | 0.341 | 0.348 | 0.351 | 0.354 | 0.352 | 0.349 | 0.344 | 0.338 | 0.333 | 0.325 | 0.321 | 0.316 | 0.317 | 0.318 | 0.317 | 0.315 | 0.312 | 0.31 | 0.307 | 0.305 | 0.304 | 0.304 | 0.304 | 0.303 | 0.301 | 0.302 | 0.301 | 0.303 | 0.298 | 0.293 | 0.284 | 0.277 | 0.274 | 0.271 | 0.27 | 0.268 | 0.27 | 0.274 | 0.279 | 0.283 | 0.287 | 0.292 | 0.295 | 0.3 | 0.306 | 0.312 | 0.319 | 0.323 | 0.329 | 0.333 | 0.339 | 0.341 | 0.344 | 0.348 | 0.351 | 0.355 | 0.357 | 0.361 | 0.36 | 0.361 | 0.361 | 0.362 | 0.362 | 0.362 | 0.36 | 0.36 | 0.359 | 0.359 | 0.358 | 0.358 | 0.358 | 0.357 | 0.356 | 0.355 | 0.353 | 0.353 | 0.352 | 0.35 | 0.348 | 0.345 | 0.341 | 0.34 | 0.341 | 0.341 | 0.338 | 0.336 | 0.335 | 0.334 | 0.333 | 0.332 | 0.331 | 0.33 | 0.329 | 0.328 | 0.328 | 0.329 | 0.334 | 0.339 | 0.343 | 0.343 | 0.342 | 0.339 | 0.335 | 0.327 | 0.319 | 0.341 | 0.337 | 0.333 | 0.334 | 0.335 | 0.334 | 0.332 | 0.33 | 0.33 | 0.328 | 0.327 | 0.326 | 0.327 | 0.326 | 0.327 | 0.326 | 0.328 | 0.328 | 0.329 | 0.329 | 0.33 | 0.328 | 0.327 | 0.33 | 0.337 | 0.347 | 0.362 | 0.39 | 0.426 | 0.472 | 0.519 | 0.575 | 0.627 | 0.673 | 0.707 | 0.732 | 0.752 | 0.764 | 0.773 | 0.78 | 0.788 | 0.798 | 0.807 | 0.812 | 0.816 | 0.82 | 0.823 | 0.82 | 0.814 | 0.802 | 0.792 | 0.789 | 0.798 | 0.809 | 0.817 | 0.818 | 0.817 | 0.813 | 0.809 | 0.801 | 0.795 | 0.789 | 0.784 | 0.774 | 0.757 | 0.732 | 0.704 | 0.665 | 0.627 | 0.586 | 0.556 | 0.524 | 0.497 | 0.474 | 0.461 | 0.45 | 0.442 | 0.435 | 0.43 | 0.423 | 0.417 | 0.41 | 0.404 | 0.4 | 0.396 | 0.394 | 0.394 | 0.396 | 0.395 | 0.391 | 0.386 | 0.379 | 0.373 | 0.367 | 0.359 | 0.353 | 0.342 | 0.337 | 0.331 | 0.332 | 0.331 | 0.33 | 0.328 | 0.325 | 0.323 | 0.321 | 0.32 | 0.318 | 0.317 | 0.315 | 0.314 | 0.313 | 0.313 | 0.313 | 0.313 | 0.312 | 0.31 | 0.306 | 0.302 | 0.298 | 0.297 | 0.295 | 0.294 | 0.298 | 0.305 | 0.314 | 0.325 | 0.339 | 0.353 | 0.367 | 0.378 | 0.391 | 0.404 | 0.417 | 0.426 | 0.435 | 0.441 | 0.446 | 0.447 | 0.449 | 0.451 | 0.453 | 0.455 | 0.456 | 0.453 | 0.449 | 0.446 | 0.445 | 0.444 | 0.442 | 0.441 | 0.439 | 0.438 | 0.435 | 0.433 | 0.432 | 0.43 | 0.428 | 0.427 | 0.424 | 0.422 | 0.42 | 0.417 | 0.411 | 0.402 | 0.393 | 0.384 | 0.376 | 0.37 | 0.367 | 0.364 | 0.362 | 0.359 | 0.358 | 0.356 | 0.355 | 0.354 | 0.352 | 0.35 | 0.348 | 0.349 | 0.352 | 0.356 | 0.36 | 0.364 | 0.367 | 0.369 | 0.367 | 0.364 | 0.359 | 0.355 | 0.35 | 0.344 | 0.34 | 0.337 | 0.338 | 0.339 | 0.339 | 0.337 | 0.335 | 0.333 | 0.332 | 0.331 | 0.33 | 0.33 | 0.329 | 0.327 | 0.323 | 0.322 | 0.319 | 0.319 | 0.317 | 0.314 | 0.309 | 0.303 | 0.298 | 0.294 | 0.289 | 0.287 | 0.286 | 0.289 | 0.293 | 0.296 | 0.301 | 0.308 | 0.315 | 0.32 | 0.325 | 0.328 | 0.332 | 0.336 | 0.342 | 0.347 | 0.353 | 0.355 | 0.36 | 0.363 | 0.365 | 0.366 | 0.368 | 0.37 | 0.372 | 0.372 | 0.372 | 0.37 | 0.369 | 0.368 | 0.366 | 0.366 | 0.364 | 0.363 | 0.361 | 0.361 | 0.361 | 0.362 | 0.361 | 0.362 | 0.36 | 0.361 | 0.359 | 0.357 | 0.352 | 0.349 | 0.347 | 0.346 | 0.346 | 0.346 | 0.346 | 0.344 | 0.344 | 0.345 | 0.343 | 0.342 | 0.339 | 0.338 | 0.337 | 0.336 | 0.337 | 0.341 | 0.346 | 0.351 | 0.353 | 0.352 | 0.352 | 0.347 | 0.345 | 0.339 | 0.334 | 0.336 | 0.332 | 0.328 | 0.33 | 0.33 | 0.33 | 0.327 | 0.325 | 0.324 | 0.323 | 0.322 | 0.32 | 0.321 | 0.32 | 0.321 | 0.319 | 0.321 | 0.321 | 0.322 | 0.323 | 0.326 | 0.33 | 0.334 | 0.34 | 0.346 | 0.352 | 0.362 | 0.384 | 0.415 | 0.457 | 0.501 | 0.554 | 0.604 | 0.649 | 0.683 | 0.709 | 0.727 | 0.741 | 0.749 | 0.756 | 0.763 | 0.772 | 0.78 | 0.786 | 0.79 | 0.794 | 0.796 | 0.794 | 0.788 | 0.777 | 0.767 | 0.765 | 0.774 | 0.786 | 0.793 | 0.795 | 0.795 | 0.792 | 0.788 | 0.781 | 0.775 | 0.771 | 0.767 | 0.758 | 0.741 | 0.715 | 0.685 | 0.646 | 0.607 | 0.568 | 0.537 | 0.506 | 0.48 | 0.459 | 0.446 | 0.437 | 0.431 | 0.426 | 0.422 | 0.418 | 0.416 | 0.418 | 0.425 | 0.433 | 0.44 | 0.44 | 0.436 | 0.427 | 0.415 | 0.402 | 0.39 | 0.38 | 0.371 | 0.364 | 0.355 | 0.348 | 0.34 | 0.334 | 0.328 | 0.329 | 0.328 | 0.327 | 0.325 | 0.324 | 0.322 | 0.319 | 0.317 | 0.315 | 0.314 | 0.313 | 0.314 | 0.312 | 0.312 | 0.311 | 0.312 | 0.312 | 0.313 | 0.315 | 0.316 | 0.315 | 0.312 | 0.307 | 0.303 | 0.302 | 0.305 | 0.311 | 0.32 | 0.331 | 0.344 | 0.357 | 0.368 | 0.381 | 0.393 | 0.407 | 0.416 | 0.423 | 0.43 | 0.436 | 0.44 | 0.44 | 0.442 | 0.444 | 0.447 | 0.447 | 0.443 | 0.439 | 0.436 | 0.433 | 0.431 | 0.43 | 0.43 | 0.429 | 0.427 | 0.425 | 0.424 | 0.422 | 0.42 | 0.417 | 0.417 | 0.414 | 0.411 | 0.407 | 0.404 | 0.398 | 0.391 | 0.381 | 0.375 | 0.37 | 0.367 | 0.364 | 0.361 | 0.359 | 0.357 | 0.356 | 0.356 | 0.355 | 0.356 | 0.356 | 0.359 | 0.363 | 0.369 | 0.373 | 0.374 | 0.374 | 0.372 | 0.369 | 0.364 | 0.359 | 0.356 | 0.351 | 0.344 | 0.338 | 0.33 | 0.326 | 0.321 | 0.323 | 0.323 | 0.322 | 0.319 | 0.317 | 0.315 | 0.314 | 0.313 | 0.311 | 0.311 | 0.31 | 0.309 | 0.306 | 0.306 | 0.306 | 0.307 | 0.306 | 0.307 | 0.308 | 0.308 | 0.305 | 0.301 | 0.294 | 0.288 | 0.285 | 0.285 | 0.286 | 0.287 | 0.291 | 0.296 | 0.301 | 0.305 | 0.309 | 0.314 | 0.319 | 0.323 | 0.328 | 0.332 | 0.336 | 0.34 | 0.343 | 0.345 | 0.347 | 0.349 | 0.352 | 0.355 | 0.357 | 0.358 | 0.357 | 0.357 | 0.357 | 0.357 | 0.356 | 0.354 | 0.354 | 0.354 | 0.353 | 0.353 | 0.352 | 0.352 | 0.352 | 0.353 | 0.354 | 0.354 | 0.352 | 0.352 | 0.349 | 0.347 | 0.343 | 0.34 | 0.342 | 0.343 | 0.345 | 0.344 | 0.343 | 0.342 | 0.341 | 0.342 | 0.344 | 0.349 | 0.355 | 0.362 | 0.366 | 0.368 | 0.365 | 0.363 | 0.359 | 0.355 | 0.349 | 0.344 | 0.34 | 0.335 | 0.334 | 0.33 | 0.326 | 0.321 | 0.324 | 0.324 | 0.324 | 0.321 | 0.32 | 0.319 | 0.317 | 0.316 | 0.315 | 0.316 | 0.316 | 0.317 | 0.316 | 0.317 | 0.318 | 0.32 | 0.322 | 0.326 | 0.331 | 0.338 | 0.349 | 0.363 | 0.38 | 0.402 | 0.434 | 0.472 | 0.519 | 0.569 | 0.627 | 0.681 | 0.729 | 0.764 | 0.791 | 0.808 | 0.818 | 0.824 | 0.829 | 0.836 | 0.845 | 0.853 | 0.858 | 0.863 | 0.865 | 0.867 | 0.863 | 0.854 | 0.837 | 0.823 | 0.821 | 0.832 | 0.846 | 0.855 | 0.857 | 0.856 | 0.851 | 0.845 | 0.835 | 0.828 | 0.822 | 0.816 | 0.803 | 0.782 | 0.75 | 0.716 | 0.672 | 0.63 | 0.587 | 0.555 | 0.524 | 0.498 | 0.478 | 0.467 | 0.462 | 0.463 | 0.469 | 0.482 | 0.495 | 0.505 | 0.51 | 0.51 | 0.504 | 0.494 | 0.479 | 0.464 | 0.445 | 0.427 | 0.409 | 0.394 | 0.38 | 0.37 | 0.36 | 0.351 | 0.343 | 0.336 | 0.331 | 0.325 | 0.327 | 0.326 | 0.325 | 0.322 | 0.319 | 0.317 | 0.316 | 0.314 | 0.313 | 0.312 | 0.311 | 0.31 | 0.308 | 0.308 | 0.307 | 0.309 | 0.309 | 0.311 | 0.312 | 0.313 | 0.315 | 0.317 | 0.32 | 0.323 | 0.328 | 0.33 | 0.333 | 0.338 | 0.35 | 0.365 | 0.379 | 0.393 | 0.406 | 0.42 | 0.432 | 0.442 | 0.45 | 0.457 | 0.462 | 0.465 | 0.468 | 0.471 | 0.474 | 0.475 | 0.475 | 0.471 | 0.465 | 0.461 | 0.457 | 0.455 | 0.453 | 0.453 | 0.451 | 0.449 | 0.446 | 0.444 | 0.44 | 0.437 | 0.434 | 0.434 | 0.431 | 0.427 | 0.422 | 0.419 | 0.413 | 0.404 | 0.394 | 0.386 | 0.379 | 0.374 | 0.37 | 0.368 | 0.366 | 0.367 | 0.367 | 0.372 | 0.378 | 0.386 | 0.391 | 0.394 | 0.393 | 0.392 | 0.388 | 0.384 | 0.38 | 0.377 | 0.372 | 0.367 | 0.361 | 0.356 | 0.351 | 0.345 | 0.34 | 0.332 | 0.329 | 0.326 | 0.329 | 0.328 | 0.327 | 0.323 | 0.321 | 0.319 | 0.32 | 0.318 | 0.318 | 0.317 | 0.319 | 0.318 | 0.315 | 0.314 | 0.313 | 0.315 | 0.315 | 0.317 | 0.317 | 0.317 | 0.317 | 0.316 | 0.317 | 0.315 | 0.314 | 0.311 | 0.307 | 0.303 | 0.301 | 0.301 | 0.305 | 0.309 | 0.314 | 0.319 | 0.325 | 0.33 | 0.335 | 0.339 | 0.342 | 0.346 | 0.349 | 0.352 | 0.353 | 0.355 | 0.358 | 0.36 | 0.361 | 0.362 | 0.362 | 0.363 | 0.363 | 0.363 | 0.362 | 0.362 | 0.362 | 0.36 | 0.359 | 0.356 | 0.355 | 0.353 | 0.353 | 0.353 | 0.353 | 0.351 | 0.351 | 0.349 | 0.348 | 0.345 | 0.343 | 0.341 | 0.342 | 0.342 | 0.342 | 0.341 | 0.343 | 0.348 | 0.354 | 0.36 | 0.367 | 0.371 | 0.371 | 0.369 | 0.365 | 0.362 | 0.357 | 0.35 | 0.345 | 0.34 | 0.335 | 0.331 | 0.326 | 0.321 | 0.317 | 0.338 | 0.334 | 0.332 | 0.334 | 0.333 | 0.333 | 0.331 | 0.33 | 0.329 | 0.328 | 0.327 | 0.327 | 0.327 | 0.328 | 0.328 | 0.327 | 0.328 | 0.329 | 0.331 | 0.333 | 0.338 | 0.343 | 0.351 | 0.362 | 0.377 | 0.397 | 0.422 | 0.461 | 0.507 | 0.564 | 0.619 | 0.678 | 0.73 | 0.775 | 0.807 | 0.831 | 0.846 | 0.853 | 0.858 | 0.86 | 0.866 | 0.874 | 0.882 | 0.887 | 0.89 | 0.891 | 0.892 | 0.887 | 0.876 | 0.858 | 0.842 | 0.839 | 0.849 | 0.864 | 0.873 | 0.874 | 0.873 | 0.868 | 0.863 | 0.852 | 0.844 | 0.837 | 0.832 | 0.818 | 0.796 | 0.765 | 0.73 | 0.688 | 0.646 | 0.606 | 0.576 | 0.549 | 0.53 | 0.52 | 0.523 | 0.533 | 0.544 | 0.552 | 0.553 | 0.548 | 0.54 | 0.533 | 0.525 | 0.514 | 0.5 | 0.484 | 0.468 | 0.45 | 0.432 | 0.414 | 0.399 | 0.386 | 0.376 | 0.368 | 0.359 | 0.351 | 0.346 | 0.341 | 0.335 | 0.336 | 0.334 | 0.334 | 0.331 | 0.328 | 0.325 | 0.324 | 0.322 | 0.322 | 0.322 | 0.322 | 0.32 | 0.319 | 0.321 | 0.321 | 0.323 | 0.323 | 0.325 | 0.326 | 0.327 | 0.33 | 0.333 | 0.338 | 0.345 | 0.355 | 0.365 | 0.374 | 0.381 | 0.39 | 0.399 | 0.408 | 0.416 | 0.426 | 0.439 | 0.449 | 0.458 | 0.467 | 0.475 | 0.481 | 0.484 | 0.486 | 0.487 | 0.488 | 0.487 | 0.485 | 0.481 | 0.475 | 0.47 | 0.466 | 0.464 | 0.463 | 0.462 | 0.461 | 0.46 | 0.458 | 0.455 | 0.453 | 0.449 | 0.448 | 0.446 | 0.444 | 0.44 | 0.436 | 0.432 | 0.426 | 0.419 | 0.41 | 0.404 | 0.397 | 0.395 | 0.394 | 0.398 | 0.405 | 0.411 | 0.415 | 0.416 | 0.414 | 0.41 | 0.406 | 0.403 | 0.399 | 0.396 | 0.392 | 0.389 | 0.386 | 0.383 | 0.379 | 0.374 | 0.371 | 0.366 | 0.361 | 0.354 | 0.348 | 0.341 | 0.338 | 0.334 | 0.337 | 0.335 | 0.335 | 0.331 | 0.331 | 0.33 | 0.33 | 0.328 | 0.326 | 0.325 | 0.323 | 0.321 | 0.319 | 0.319 | 0.318 | 0.319 | 0.319 | 0.32 | 0.321 | 0.322 | 0.321 | 0.321 | 0.323 | 0.324 | 0.327 | 0.328 | 0.328 | 0.325 | 0.322 | 0.321 | 0.321 | 0.323 | 0.325 | 0.331 | 0.335 | 0.34 | 0.344 | 0.349 | 0.351 | 0.354 | 0.357 | 0.361 | 0.361 | 0.363 | 0.366 | 0.368 | 0.369 | 0.368 | 0.369 | 0.371 | 0.372 | 0.372 | 0.37 | 0.37 | 0.369 | 0.37 | 0.368 | 0.368 | 0.367 | 0.366 | 0.366 | 0.367 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.367 | 0.368 | 0.37 | 0.374 | 0.379 | 0.384 | 0.387 | 0.39 | 0.389 | 0.388 | 0.387 | 0.385 | 0.383 | 0.38 | 0.376 | 0.372 | 0.367 | 0.363 | 0.359 | 0.355 | 0.35 | 0.346 | 0.343 | 0.337 | 0.331 | 0.35 | 0.347 | 0.345 | 0.348 | 0.348 | 0.347 | 0.346 | 0.345 | 0.344 | 0.342 | 0.34 | 0.34 | 0.341 | 0.341 | 0.342 | 0.342 | 0.345 | 0.346 | 0.349 | 0.351 | 0.356 | 0.363 | 0.371 | 0.383 | 0.4 | 0.422 | 0.448 | 0.488 | 0.536 | 0.595 | 0.652 | 0.712 | 0.767 | 0.814 | 0.849 | 0.875 | 0.891 | 0.899 | 0.903 | 0.905 | 0.912 | 0.919 | 0.927 | 0.932 | 0.934 | 0.935 | 0.935 | 0.929 | 0.918 | 0.9 | 0.884 | 0.881 | 0.891 | 0.906 | 0.916 | 0.918 | 0.917 | 0.912 | 0.906 | 0.895 | 0.887 | 0.881 | 0.876 | 0.865 | 0.847 | 0.821 | 0.798 | 0.769 | 0.742 | 0.711 | 0.686 | 0.659 | 0.636 | 0.616 | 0.604 | 0.595 | 0.589 | 0.582 | 0.575 | 0.567 | 0.557 | 0.547 | 0.536 | 0.524 | 0.511 | 0.495 | 0.479 | 0.461 | 0.443 | 0.425 | 0.41 | 0.398 | 0.39 | 0.383 | 0.373 | 0.363 | 0.361 | 0.358 | 0.355 | 0.357 | 0.356 | 0.354 | 0.351 | 0.349 | 0.348 | 0.345 | 0.344 | 0.344 | 0.344 | 0.344 | 0.343 | 0.343 | 0.344 | 0.344 | 0.345 | 0.345 | 0.347 | 0.35 | 0.352 | 0.356 | 0.359 | 0.363 | 0.369 | 0.378 | 0.388 | 0.399 | 0.407 | 0.416 | 0.426 | 0.434 | 0.445 | 0.457 | 0.469 | 0.479 | 0.487 | 0.495 | 0.503 | 0.508 | 0.514 | 0.518 | 0.52 | 0.52 | 0.519 | 0.517 | 0.514 | 0.509 | 0.505 | 0.501 | 0.499 | 0.496 | 0.495 | 0.494 | 0.493 | 0.489 | 0.486 | 0.482 | 0.481 | 0.48 | 0.481 | 0.482 | 0.485 | 0.488 | 0.496 | 0.501 | 0.502 | 0.495 | 0.487 | 0.476 | 0.467 | 0.459 | 0.456 | 0.451 | 0.447 | 0.443 | 0.439 | 0.435 | 0.43 | 0.426 | 0.424 | 0.421 | 0.417 | 0.413 | 0.409 | 0.405 | 0.401 | 0.396 | 0.391 | 0.385 | 0.381 | 0.378 | 0.371 | 0.364 | 0.357 | 0.355 | 0.355 | 0.357 | 0.357 | 0.355 | 0.352 | 0.35 | 0.348 | 0.347 | 0.344 | 0.343 | 0.342 | 0.341 | 0.339 | 0.336 | 0.337 | 0.335 | 0.337 | 0.336 | 0.338 | 0.339 | 0.338 | 0.339 | 0.34 | 0.34 | 0.342 | 0.346 | 0.349 | 0.351 | 0.349 | 0.347 | 0.345 | 0.344 | 0.344 | 0.348 | 0.352 | 0.355 | 0.358 | 0.361 | 0.366 | 0.369 | 0.373 | 0.376 | 0.379 | 0.381 | 0.384 | 0.387 | 0.39 | 0.392 | 0.392 | 0.392 | 0.394 | 0.395 | 0.395 | 0.395 | 0.396 | 0.396 | 0.397 | 0.397 | 0.398 | 0.397 | 0.398 | 0.399 | 0.402 | 0.405 | 0.413 | 0.422 | 0.43 | 0.434 | 0.434 | 0.431 | 0.427 | 0.424 | 0.422 | 0.419 | 0.418 | 0.415 | 0.412 | 0.41 | 0.408 | 0.406 | 0.403 | 0.4 | 0.396 | 0.394 | 0.39 | 0.386 | 0.381 | 0.375 | 0.371 | 0.365 | 0.361 | 0.357 | 0.351 | 0.344 | 0.388 | 0.385 | 0.383 | 0.385 | 0.386 | 0.386 | 0.383 | 0.381 | 0.381 | 0.379 | 0.38 | 0.379 | 0.38 | 0.379 | 0.38 | 0.379 | 0.382 | 0.383 | 0.385 | 0.387 | 0.39 | 0.397 | 0.404 | 0.415 | 0.43 | 0.45 | 0.473 | 0.507 | 0.548 | 0.599 | 0.652 | 0.713 | 0.767 | 0.811 | 0.84 | 0.86 | 0.874 | 0.88 | 0.885 | 0.886 | 0.892 | 0.898 | 0.904 | 0.908 | 0.909 | 0.91 | 0.909 | 0.904 | 0.896 | 0.881 | 0.868 | 0.863 | 0.871 | 0.88 | 0.886 | 0.885 | 0.884 | 0.88 | 0.875 | 0.865 | 0.857 | 0.851 | 0.846 | 0.837 | 0.824 | 0.806 | 0.789 | 0.764 | 0.735 | 0.7 | 0.671 | 0.643 | 0.621 | 0.602 | 0.59 | 0.579 | 0.571 | 0.563 | 0.557 | 0.549 | 0.541 | 0.531 | 0.523 | 0.514 | 0.504 | 0.491 | 0.48 | 0.466 | 0.455 | 0.444 | 0.436 | 0.43 | 0.424 | 0.418 | 0.409 | 0.398 | 0.391 | 0.386 | 0.384 | 0.385 | 0.384 | 0.383 | 0.38 | 0.377 | 0.375 | 0.373 | 0.372 | 0.372 | 0.373 | 0.371 | 0.371 | 0.369 | 0.373 | 0.374 | 0.376 | 0.376 | 0.378 | 0.38 | 0.384 | 0.387 | 0.393 | 0.398 | 0.405 | 0.415 | 0.425 | 0.438 | 0.451 | 0.47 | 0.486 | 0.498 | 0.505 | 0.512 | 0.522 | 0.532 | 0.54 | 0.545 | 0.551 | 0.556 | 0.561 | 0.563 | 0.566 | 0.566 | 0.565 | 0.561 | 0.556 | 0.55 | 0.544 | 0.539 | 0.536 | 0.533 | 0.532 | 0.529 | 0.527 | 0.524 | 0.52 | 0.515 | 0.511 | 0.509 | 0.508 | 0.506 | 0.505 | 0.506 | 0.511 | 0.515 | 0.511 | 0.502 | 0.491 | 0.481 | 0.474 | 0.468 | 0.464 | 0.459 | 0.455 | 0.452 | 0.45 | 0.447 | 0.444 | 0.44 | 0.438 | 0.434 | 0.432 | 0.428 | 0.424 | 0.42 | 0.416 | 0.412 | 0.408 | 0.404 | 0.402 | 0.399 | 0.392 | 0.392 | 0.386 | 0.383 | 0.382 | 0.382 | 0.382 | 0.381 | 0.378 | 0.377 | 0.375 | 0.373 | 0.371 | 0.371 | 0.37 | 0.369 | 0.368 | 0.368 | 0.37 | 0.371 | 0.372 | 0.372 | 0.371 | 0.372 | 0.372 | 0.373 | 0.374 | 0.375 | 0.378 | 0.381 | 0.384 | 0.386 | 0.386 | 0.39 | 0.391 | 0.39 | 0.386 | 0.384 | 0.385 | 0.386 | 0.39 | 0.393 | 0.397 | 0.401 | 0.405 | 0.408 | 0.411 | 0.414 | 0.416 | 0.421 | 0.423 | 0.424 | 0.424 | 0.423 | 0.424 | 0.425 | 0.426 | 0.426 | 0.426 | 0.425 | 0.425 | 0.425 | 0.425 | 0.425 | 0.426 | 0.428 | 0.433 | 0.44 | 0.451 | 0.461 | 0.464 | 0.463 | 0.458 | 0.455 | 0.454 | 0.452 | 0.452 | 0.448 | 0.447 | 0.443 | 0.443 | 0.44 | 0.438 | 0.435 | 0.432 | 0.429 | 0.427 | 0.425 | 0.421 | 0.416 | 0.41 | 0.405 | 0.402 | 0.399 | 0.396 | 0.393 | 0.384 | 0.377
E3B | -3456 | 0.404 | 0.402 | 0.4 | 0.401 | 0.402 | 0.401 | 0.4 | 0.399 | 0.397 | 0.395 | 0.395 | 0.395 | 0.396 | 0.396 | 0.396 | 0.396 | 0.398 | 0.399 | 0.401 | 0.403 | 0.408 | 0.414 | 0.422 | 0.433 | 0.449 | 0.47 | 0.496 | 0.534 | 0.582 | 0.642 | 0.705 | 0.778 | 0.84 | 0.892 | 0.926 | 0.948 | 0.963 | 0.969 | 0.973 | 0.975 | 0.98 | 0.987 | 0.994 | 0.998 | 1 | 1 | 1 | 0.994 | 0.982 | 0.963 | 0.948 | 0.945 | 0.956 | 0.97 | 0.978 | 0.979 | 0.978 | 0.973 | 0.967 | 0.954 | 0.945 | 0.937 | 0.933 | 0.92 | 0.899 | 0.867 | 0.835 | 0.798 | 0.764 | 0.73 | 0.703 | 0.675 | 0.651 | 0.629 | 0.616 | 0.607 | 0.6 | 0.592 | 0.585 | 0.576 | 0.567 | 0.557 | 0.549 | 0.539 | 0.528 | 0.515 | 0.503 | 0.489 | 0.476 | 0.462 | 0.453 | 0.446 | 0.441 | 0.435 | 0.425 | 0.417 | 0.414 | 0.41 | 0.407 | 0.408 | 0.408 | 0.408 | 0.405 | 0.404 | 0.401 | 0.399 | 0.398 | 0.398 | 0.398 | 0.397 | 0.396 | 0.395 | 0.396 | 0.396 | 0.398 | 0.398 | 0.4 | 0.403 | 0.406 | 0.409 | 0.413 | 0.417 | 0.423 | 0.432 | 0.441 | 0.451 | 0.462 | 0.478 | 0.49 | 0.501 | 0.506 | 0.516 | 0.526 | 0.537 | 0.546 | 0.554 | 0.561 | 0.566 | 0.57 | 0.572 | 0.573 | 0.574 | 0.573 | 0.571 | 0.566 | 0.561 | 0.554 | 0.551 | 0.548 | 0.546 | 0.544 | 0.543 | 0.541 | 0.539 | 0.536 | 0.533 | 0.531 | 0.529 | 0.527 | 0.525 | 0.524 | 0.522 | 0.522 | 0.52 | 0.52 | 0.519 | 0.518 | 0.512 | 0.505 | 0.5 | 0.497 | 0.496 | 0.494 | 0.491 | 0.488 | 0.485 | 0.482 | 0.478 | 0.474 | 0.469 | 0.466 | 0.462 | 0.462 | 0.458 | 0.454 | 0.448 | 0.445 | 0.44 | 0.437 | 0.433 | 0.426 | 0.407 | 0.407 | 0.404 | 0.403 | 0.404 | 0.404 | 0.404 | 0.402 | 0.4 | 0.398 | 0.395 | 0.394 | 0.393 | 0.394 | 0.393 | 0.392 | 0.389 | 0.39 | 0.391 | 0.392 | 0.392 | 0.393 | 0.394 | 0.396 | 0.396 | 0.397 | 0.397 | 0.399 | 0.402 | 0.406 | 0.409 | 0.409 | 0.412 | 0.412 | 0.411 | 0.407 | 0.404 | 0.405 | 0.406 | 0.408 | 0.41 | 0.412 | 0.416 | 0.42 | 0.423 | 0.426 | 0.427 | 0.431 | 0.433 | 0.435 | 0.435 | 0.436 | 0.437 | 0.438 | 0.438 | 0.438 | 0.438 | 0.439 | 0.439 | 0.439 | 0.438 | 0.438 | 0.436 | 0.436 | 0.437 | 0.437 | 0.439 | 0.442 | 0.45 | 0.459 | 0.466 | 0.471 | 0.472 | 0.471 | 0.469 | 0.467 | 0.464 | 0.462 | 0.46 | 0.458 | 0.455 | 0.452 | 0.45 | 0.448 | 0.445 | 0.443 | 0.441 | 0.439 | 0.435 | 0.43 | 0.425 | 0.421 | 0.418 | 0.416 | 0.411 | 0.404 | 0.397 | 0.399 | 0.397 | 0.396 | 0.397 | 0.397 | 0.396 | 0.395 | 0.394 | 0.393 | 0.391 | 0.39 | 0.39 | 0.391 | 0.39 | 0.39 | 0.389 | 0.391 | 0.391 | 0.394 | 0.397 | 0.401 | 0.407 | 0.416 | 0.427 | 0.443 | 0.464 | 0.491 | 0.529 | 0.576 | 0.634 | 0.693 | 0.755 | 0.811 | 0.859 | 0.895 | 0.922 | 0.939 | 0.947 | 0.951 | 0.955 | 0.961 | 0.968 | 0.975 | 0.979 | 0.981 | 0.982 | 0.982 | 0.976 | 0.965 | 0.947 | 0.93 | 0.926 | 0.936 | 0.951 | 0.958 | 0.959 | 0.958 | 0.952 | 0.946 | 0.934 | 0.925 | 0.917 | 0.911 | 0.897 | 0.874 | 0.841 | 0.805 | 0.763 | 0.722 | 0.684 | 0.66 | 0.642 | 0.63 | 0.62 | 0.613 | 0.606 | 0.6 | 0.593 | 0.586 | 0.578 | 0.569 | 0.559 | 0.549 | 0.538 | 0.526 | 0.513 | 0.499 | 0.485 | 0.47 | 0.457 | 0.446 | 0.437 | 0.431 | 0.424 | 0.415 | 0.409 | 0.398 | 0.395 | 0.392 | 0.393 | 0.392 | 0.392 | 0.391 | 0.39 | 0.389 | 0.386 | 0.385 | 0.384 | 0.386 | 0.383 | 0.384 | 0.383 | 0.384 | 0.383 | 0.386 | 0.386 | 0.389 | 0.389 | 0.393 | 0.395 | 0.4 | 0.403 | 0.409 | 0.417 | 0.425 | 0.434 | 0.441 | 0.45 | 0.459 | 0.469 | 0.48 | 0.494 | 0.507 | 0.519 | 0.527 | 0.536 | 0.544 | 0.551 | 0.555 | 0.559 | 0.562 | 0.562 | 0.563 | 0.561 | 0.556 | 0.549 | 0.542 | 0.538 | 0.535 | 0.533 | 0.532 | 0.529 | 0.527 | 0.523 | 0.52 | 0.515 | 0.513 | 0.51 | 0.509 | 0.505 | 0.502 | 0.497 | 0.494 | 0.488 | 0.483 | 0.476 | 0.474 | 0.474 | 0.476 | 0.478 | 0.477 | 0.477 | 0.475 | 0.473 | 0.471 | 0.468 | 0.464 | 0.46 | 0.457 | 0.454 | 0.45 | 0.447 | 0.445 | 0.442 | 0.438 | 0.434 | 0.431 | 0.426 | 0.422 | 0.418 | 0.411 | 0.405 | 0.398 | 0.397 | 0.396 | 0.398 | 0.399 | 0.399 | 0.398 | 0.397 | 0.394 | 0.391 | 0.389 | 0.388 | 0.39 | 0.388 | 0.388 | 0.385 | 0.385 | 0.384 | 0.384 | 0.384 | 0.386 | 0.388 | 0.389 | 0.387 | 0.389 | 0.389 | 0.391 | 0.392 | 0.394 | 0.394 | 0.392 | 0.387 | 0.383 | 0.379 | 0.38 | 0.382 | 0.387 | 0.39 | 0.394 | 0.399 | 0.403 | 0.407 | 0.41 | 0.413 | 0.417 | 0.42 | 0.423 | 0.424 | 0.424 | 0.425 | 0.426 | 0.428 | 0.429 | 0.429 | 0.429 | 0.43 | 0.429 | 0.428 | 0.427 | 0.428 | 0.428 | 0.428 | 0.428 | 0.427 | 0.428 | 0.428 | 0.428 | 0.429 | 0.431 | 0.433 | 0.437 | 0.443 | 0.452 | 0.458 | 0.462 | 0.462 | 0.46 | 0.458 | 0.456 | 0.454 | 0.451 | 0.449 | 0.447 | 0.443 | 0.44 | 0.437 | 0.435 | 0.432 | 0.428 | 0.423 | 0.419 | 0.415 | 0.412 | 0.408 | 0.401 | 0.395 | 0.368 | 0.365 | 0.363 | 0.364 | 0.364 | 0.365 | 0.362 | 0.361 | 0.36 | 0.359 | 0.358 | 0.359 | 0.36 | 0.36 | 0.361 | 0.36 | 0.362 | 0.363 | 0.366 | 0.369 | 0.374 | 0.381 | 0.389 | 0.401 | 0.416 | 0.435 | 0.456 | 0.486 | 0.524 | 0.573 | 0.628 | 0.69 | 0.747 | 0.798 | 0.836 | 0.865 | 0.883 | 0.892 | 0.897 | 0.9 | 0.907 | 0.915 | 0.922 | 0.925 | 0.927 | 0.928 | 0.928 | 0.922 | 0.91 | 0.891 | 0.874 | 0.871 | 0.881 | 0.896 | 0.905 | 0.907 | 0.905 | 0.9 | 0.893 | 0.881 | 0.872 | 0.864 | 0.858 | 0.845 | 0.822 | 0.789 | 0.753 | 0.709 | 0.667 | 0.625 | 0.594 | 0.566 | 0.547 | 0.537 | 0.541 | 0.55 | 0.559 | 0.562 | 0.561 | 0.557 | 0.553 | 0.548 | 0.541 | 0.531 | 0.517 | 0.503 | 0.487 | 0.47 | 0.451 | 0.435 | 0.421 | 0.41 | 0.402 | 0.395 | 0.385 | 0.379 | 0.369 | 0.366 | 0.362 | 0.363 | 0.363 | 0.363 | 0.36 | 0.359 | 0.356 | 0.354 | 0.353 | 0.353 | 0.355 | 0.355 | 0.354 | 0.353 | 0.354 | 0.354 | 0.356 | 0.356 | 0.358 | 0.36 | 0.363 | 0.365 | 0.368 | 0.368 | 0.368 | 0.369 | 0.373 | 0.378 | 0.386 | 0.399 | 0.413 | 0.428 | 0.443 | 0.459 | 0.473 | 0.484 | 0.492 | 0.501 | 0.509 | 0.517 | 0.521 | 0.524 | 0.526 | 0.526 | 0.525 | 0.522 | 0.515 | 0.507 | 0.501 | 0.498 | 0.495 | 0.493 | 0.492 | 0.49 | 0.488 | 0.485 | 0.483 | 0.48 | 0.477 | 0.475 | 0.472 | 0.469 | 0.464 | 0.46 | 0.455 | 0.449 | 0.441 | 0.435 | 0.428 | 0.422 | 0.416 | 0.417 | 0.423 | 0.432 | 0.439 | 0.442 | 0.442 | 0.439 | 0.435 | 0.43 | 0.427 | 0.423 | 0.422 | 0.419 | 0.416 | 0.412 | 0.407 | 0.403 | 0.399 | 0.393 | 0.39 | 0.386 | 0.381 | 0.375 | 0.366 | 0.364 | 0.363 | 0.365 | 0.365 | 0.366 | 0.363 | 0.364 | 0.361 | 0.36 | 0.358 | 0.357 | 0.357 | 0.357 | 0.356 | 0.354 | 0.355 | 0.354 | 0.356 | 0.355 | 0.355 | 0.356 | 0.356 | 0.358 | 0.357 | 0.357 | 0.356 | 0.354 | 0.35 | 0.346 | 0.342 | 0.341 | 0.342 | 0.345 | 0.349 | 0.354 | 0.359 | 0.363 | 0.367 | 0.37 | 0.374 | 0.377 | 0.378 | 0.381 | 0.383 | 0.386 | 0.386 | 0.388 | 0.39 | 0.391 | 0.391 | 0.392 | 0.394 | 0.394 | 0.393 | 0.391 | 0.391 | 0.389 | 0.389 | 0.386 | 0.387 | 0.385 | 0.386 | 0.384 | 0.383 | 0.382 | 0.382 | 0.381 | 0.38 | 0.378 | 0.377 | 0.376 | 0.379 | 0.382 | 0.39 | 0.397 | 0.404 | 0.406 | 0.407 | 0.406 | 0.407 | 0.407 | 0.407 | 0.405 | 0.403 | 0.4 | 0.397 | 0.394 | 0.39 | 0.386 | 0.382 | 0.379 | 0.376 | 0.374 | 0.368 | 0.363 | 0.338 | 0.334 | 0.331 | 0.334 | 0.334 | 0.334 | 0.332 | 0.33 | 0.328 | 0.327 | 0.327 | 0.327 | 0.329 | 0.329 | 0.329 | 0.328 | 0.33 | 0.331 | 0.335 | 0.337 | 0.342 | 0.347 | 0.354 | 0.364 | 0.376 | 0.391 | 0.408 | 0.433 | 0.467 | 0.513 | 0.564 | 0.622 | 0.675 | 0.723 | 0.759 | 0.785 | 0.802 | 0.811 | 0.816 | 0.82 | 0.828 | 0.837 | 0.844 | 0.848 | 0.851 | 0.853 | 0.855 | 0.85 | 0.839 | 0.822 | 0.808 | 0.805 | 0.815 | 0.828 | 0.837 | 0.839 | 0.838 | 0.832 | 0.826 | 0.815 | 0.807 | 0.799 | 0.793 | 0.781 | 0.76 | 0.731 | 0.699 | 0.658 | 0.619 | 0.58 | 0.549 | 0.521 | 0.495 | 0.476 | 0.464 | 0.457 | 0.452 | 0.448 | 0.446 | 0.447 | 0.452 | 0.463 | 0.477 | 0.486 | 0.488 | 0.48 | 0.469 | 0.453 | 0.436 | 0.418 | 0.403 | 0.389 | 0.379 | 0.37 | 0.36 | 0.351 | 0.35 | 0.345 | 0.34 | 0.341 | 0.341 | 0.34 | 0.336 | 0.334 | 0.332 | 0.331 | 0.331 | 0.331 | 0.332 | 0.331 | 0.331 | 0.33 | 0.33 | 0.331 | 0.334 | 0.334 | 0.335 | 0.335 | 0.336 | 0.336 | 0.336 | 0.335 | 0.335 | 0.335 | 0.339 | 0.345 | 0.354 | 0.367 | 0.382 | 0.395 | 0.408 | 0.421 | 0.433 | 0.443 | 0.452 | 0.46 | 0.467 | 0.473 | 0.477 | 0.479 | 0.482 | 0.482 | 0.483 | 0.481 | 0.477 | 0.471 | 0.466 | 0.463 | 0.461 | 0.459 | 0.458 | 0.457 | 0.455 | 0.452 | 0.448 | 0.445 | 0.443 | 0.44 | 0.437 | 0.435 | 0.431 | 0.426 | 0.421 | 0.414 | 0.407 | 0.399 | 0.39 | 0.383 | 0.376 | 0.374 | 0.372 | 0.371 | 0.371 | 0.371 | 0.369 | 0.369 | 0.369 | 0.374 | 0.381 | 0.389 | 0.395 | 0.396 | 0.395 | 0.391 | 0.386 | 0.381 | 0.378 | 0.373 | 0.37 | 0.364 | 0.357 | 0.356 | 0.349 | 0.346 | 0.345 | 0.347 | 0.347 | 0.346 | 0.344 | 0.343 | 0.341 | 0.339 | 0.338 | 0.337 | 0.337 | 0.336 | 0.334 | 0.332 | 0.332 | 0.332 | 0.334 | 0.334 | 0.335 | 0.337 | 0.337 | 0.336 | 0.334 | 0.331 | 0.327 | 0.321 | 0.318 | 0.315 | 0.314 | 0.316 | 0.319 | 0.323 | 0.327 | 0.333 | 0.338 | 0.343 | 0.346 | 0.349 | 0.354 | 0.359 | 0.362 | 0.362 | 0.365 | 0.368 | 0.37 | 0.371 | 0.372 | 0.374 | 0.374 | 0.375 | 0.375 | 0.375 | 0.371 | 0.369 | 0.369 | 0.367 | 0.368 | 0.366 | 0.366 | 0.362 | 0.361 | 0.36 | 0.36 | 0.358 | 0.356 | 0.354 | 0.353 | 0.351 | 0.349 | 0.346 | 0.343 | 0.341 | 0.341 | 0.342 | 0.342 | 0.34 | 0.34 | 0.341 | 0.345 | 0.351 | 0.359 | 0.366 | 0.373 | 0.375 | 0.374 | 0.369 | 0.365 | 0.359 | 0.355 | 0.351 | 0.346 | 0.342 | 0.336 | 0.335 | 0.331 | 0.327 | 0.323 | 0.325 | 0.326 | 0.325 | 0.323 | 0.321 | 0.32 | 0.318 | 0.318 | 0.317 | 0.319 | 0.318 | 0.319 | 0.318 | 0.32 | 0.32 | 0.322 | 0.323 | 0.325 | 0.326 | 0.326 | 0.33 | 0.336 | 0.348 | 0.364 | 0.392 | 0.429 | 0.475 | 0.525 | 0.58 | 0.631 | 0.674 | 0.708 | 0.732 | 0.749 | 0.759 | 0.765 | 0.769 | 0.777 | 0.786 | 0.795 | 0.799 | 0.804 | 0.806 | 0.809 | 0.805 | 0.797 | 0.783 | 0.771 | 0.768 | 0.778 | 0.792 | 0.8 | 0.802 | 0.802 | 0.797 | 0.792 | 0.783 | 0.777 | 0.771 | 0.768 | 0.757 | 0.738 | 0.711 | 0.681 | 0.642 | 0.605 | 0.567 | 0.537 | 0.509 | 0.484 | 0.464 | 0.452 | 0.443 | 0.436 | 0.43 | 0.425 | 0.42 | 0.415 | 0.412 | 0.411 | 0.413 | 0.418 | 0.424 | 0.426 | 0.423 | 0.415 | 0.403 | 0.391 | 0.379 | 0.369 | 0.361 | 0.352 | 0.345 | 0.34 | 0.335 | 0.331 | 0.333 | 0.332 | 0.33 | 0.326 | 0.324 | 0.321 | 0.318 | 0.315 | 0.315 | 0.316 | 0.315 | 0.314 | 0.312 | 0.314 | 0.314 | 0.315 | 0.314 | 0.313 | 0.309 | 0.304 | 0.299 | 0.296 | 0.296 | 0.298 | 0.303 | 0.311 | 0.319 | 0.33 | 0.343 | 0.358 | 0.372 | 0.387 | 0.401 | 0.416 | 0.427 | 0.436 | 0.444 | 0.451 | 0.457 | 0.461 | 0.464 | 0.466 | 0.468 | 0.469 | 0.469 | 0.465 | 0.461 | 0.455 | 0.451 | 0.45 | 0.449 | 0.449 | 0.448 | 0.446 | 0.444 | 0.442 | 0.439 | 0.436 | 0.433 | 0.432 | 0.429 | 0.427 | 0.423 | 0.418 | 0.41 | 0.402 | 0.393 | 0.386 | 0.379 | 0.372 | 0.367 | 0.364 | 0.363 | 0.361 | 0.361 | 0.361 | 0.358 | 0.355 | 0.353 | 0.353 | 0.354 | 0.355 | 0.361 | 0.366 | 0.37 | 0.371 | 0.369 | 0.366 | 0.362 | 0.359 | 0.353 | 0.346 | 0.338 | 0.331 | 0.327 | 0.323 | 0.325 | 0.325 | 0.324 | 0.322 | 0.32 | 0.319 | 0.316 | 0.315 | 0.314 | 0.314 | 0.313 | 0.313 | 0.311 | 0.312 | 0.312 | 0.313 | 0.311 | 0.31 | 0.307 | 0.301 | 0.295 | 0.29 | 0.286 | 0.284 | 0.284 | 0.286 | 0.289 | 0.293 | 0.297 | 0.3 | 0.304 | 0.308 | 0.314 | 0.319 | 0.325 | 0.329 | 0.335 | 0.34 | 0.344 | 0.348 | 0.349 | 0.353 | 0.356 | 0.358 | 0.359 | 0.36 | 0.362 | 0.363 | 0.364 | 0.364 | 0.363 | 0.362 | 0.359 | 0.358 | 0.356 | 0.355 | 0.353 | 0.353 | 0.352 | 0.352 | 0.351 | 0.35 | 0.349 | 0.348 | 0.348 | 0.347 | 0.346 | 0.344 | 0.342 | 0.34 | 0.338 | 0.338 | 0.336 | 0.336 | 0.334 | 0.335 | 0.333 | 0.333 | 0.332 | 0.333 | 0.335 | 0.339 | 0.344 | 0.35 | 0.353 | 0.354 | 0.351 | 0.347 | 0.344 | 0.34 | 0.336 | 0.331 | 0.327 | 0.333 | 0.329 | 0.326 | 0.327 | 0.327 | 0.326 | 0.324 | 0.321 | 0.32 | 0.318 | 0.317 | 0.317 | 0.318 | 0.318 | 0.318 | 0.317 | 0.318 | 0.318 | 0.32 | 0.318 | 0.316 | 0.312 | 0.311 | 0.317 | 0.328 | 0.342 | 0.36 | 0.393 | 0.433 | 0.485 | 0.539 | 0.599 | 0.656 | 0.706 | 0.745 | 0.772 | 0.792 | 0.804 | 0.812 | 0.818 | 0.827 | 0.838 | 0.847 | 0.854 | 0.859 | 0.862 | 0.864 | 0.86 | 0.852 | 0.836 | 0.822 | 0.819 | 0.83 | 0.845 | 0.854 | 0.856 | 0.856 | 0.852 | 0.846 | 0.836 | 0.829 | 0.824 | 0.819 | 0.807 | 0.786 | 0.756 | 0.722 | 0.679 | 0.638 | 0.596 | 0.563 | 0.531 | 0.504 | 0.481 | 0.467 | 0.455 | 0.447 | 0.44 | 0.434 | 0.427 | 0.42 | 0.413 | 0.408 | 0.403 | 0.398 | 0.395 | 0.394 | 0.395 | 0.396 | 0.394 | 0.388 | 0.379 | 0.371 | 0.364 | 0.354 | 0.345 | 0.335 | 0.329 | 0.323 | 0.323 | 0.323 | 0.32 | 0.318 | 0.314 | 0.313 | 0.309 | 0.308 | 0.306 | 0.306 | 0.304 | 0.304 | 0.301 | 0.302 | 0.301 | 0.302 | 0.299 | 0.293 | 0.286 | 0.28 | 0.279 | 0.28 | 0.282 | 0.283 | 0.29 | 0.298 | 0.31 | 0.322 | 0.337 | 0.352 | 0.365 | 0.378 | 0.391 | 0.406 | 0.418 | 0.429 | 0.437 | 0.445 | 0.451 | 0.455 | 0.459 | 0.462 | 0.464 | 0.465 | 0.463 | 0.459 | 0.454 | 0.449 | 0.446 | 0.444 | 0.443 | 0.441 | 0.439 | 0.436 | 0.434 | 0.432 | 0.43 | 0.429 | 0.427 | 0.425 | 0.42 | 0.417 | 0.412 | 0.408 | 0.401 | 0.393 | 0.384 | 0.377 | 0.369 | 0.362 | 0.357 | 0.355 | 0.354 | 0.352 | 0.351 | 0.349 | 0.349 | 0.347 | 0.345 | 0.343 | 0.341 | 0.339 | 0.338 | 0.338 | 0.341 | 0.348 | 0.351 | 0.354 | 0.352 | 0.349 | 0.344 | 0.338 | 0.333 | 0.325 | 0.321 | 0.316 | 0.317 | 0.318 | 0.317 | 0.315 | 0.312 | 0.31 | 0.307 | 0.305 | 0.304 | 0.304 | 0.304 | 0.303 | 0.301 | 0.302 | 0.301 | 0.303 | 0.298 | 0.293 | 0.284 | 0.277 | 0.274 | 0.271 | 0.27 | 0.268 | 0.27 | 0.274 | 0.279 | 0.283 | 0.287 | 0.292 | 0.295 | 0.3 | 0.306 | 0.312 | 0.319 | 0.323 | 0.329 | 0.333 | 0.339 | 0.341 | 0.344 | 0.348 | 0.351 | 0.355 | 0.357 | 0.361 | 0.36 | 0.361 | 0.361 | 0.362 | 0.362 | 0.362 | 0.36 | 0.36 | 0.359 | 0.359 | 0.358 | 0.358 | 0.358 | 0.357 | 0.356 | 0.355 | 0.353 | 0.353 | 0.352 | 0.35 | 0.348 | 0.345 | 0.341 | 0.34 | 0.341 | 0.341 | 0.338 | 0.336 | 0.335 | 0.334 | 0.333 | 0.332 | 0.331 | 0.33 | 0.329 | 0.328 | 0.328 | 0.329 | 0.334 | 0.339 | 0.343 | 0.343 | 0.342 | 0.339 | 0.335 | 0.327 | 0.319 | 0.341 | 0.337 | 0.333 | 0.334 | 0.335 | 0.334 | 0.332 | 0.33 | 0.33 | 0.328 | 0.327 | 0.326 | 0.327 | 0.326 | 0.327 | 0.326 | 0.328 | 0.328 | 0.329 | 0.329 | 0.33 | 0.328 | 0.327 | 0.33 | 0.337 | 0.347 | 0.362 | 0.39 | 0.426 | 0.472 | 0.519 | 0.575 | 0.627 | 0.673 | 0.707 | 0.732 | 0.752 | 0.764 | 0.773 | 0.78 | 0.788 | 0.798 | 0.807 | 0.812 | 0.816 | 0.82 | 0.823 | 0.82 | 0.814 | 0.802 | 0.792 | 0.789 | 0.798 | 0.809 | 0.817 | 0.818 | 0.817 | 0.813 | 0.809 | 0.801 | 0.795 | 0.789 | 0.784 | 0.774 | 0.757 | 0.732 | 0.704 | 0.665 | 0.627 | 0.586 | 0.556 | 0.524 | 0.497 | 0.474 | 0.461 | 0.45 | 0.442 | 0.435 | 0.43 | 0.423 | 0.417 | 0.41 | 0.404 | 0.4 | 0.396 | 0.394 | 0.394 | 0.396 | 0.395 | 0.391 | 0.386 | 0.379 | 0.373 | 0.367 | 0.359 | 0.353 | 0.342 | 0.337 | 0.331 | 0.332 | 0.331 | 0.33 | 0.328 | 0.325 | 0.323 | 0.321 | 0.32 | 0.318 | 0.317 | 0.315 | 0.314 | 0.313 | 0.313 | 0.313 | 0.313 | 0.312 | 0.31 | 0.306 | 0.302 | 0.298 | 0.297 | 0.295 | 0.294 | 0.298 | 0.305 | 0.314 | 0.325 | 0.339 | 0.353 | 0.367 | 0.378 | 0.391 | 0.404 | 0.417 | 0.426 | 0.435 | 0.441 | 0.446 | 0.447 | 0.449 | 0.451 | 0.453 | 0.455 | 0.456 | 0.453 | 0.449 | 0.446 | 0.445 | 0.444 | 0.442 | 0.441 | 0.439 | 0.438 | 0.435 | 0.433 | 0.432 | 0.43 | 0.428 | 0.427 | 0.424 | 0.422 | 0.42 | 0.417 | 0.411 | 0.402 | 0.393 | 0.384 | 0.376 | 0.37 | 0.367 | 0.364 | 0.362 | 0.359 | 0.358 | 0.356 | 0.355 | 0.354 | 0.352 | 0.35 | 0.348 | 0.349 | 0.352 | 0.356 | 0.36 | 0.364 | 0.367 | 0.369 | 0.367 | 0.364 | 0.359 | 0.355 | 0.35 | 0.344 | 0.34 | 0.337 | 0.338 | 0.339 | 0.339 | 0.337 | 0.335 | 0.333 | 0.332 | 0.331 | 0.33 | 0.33 | 0.329 | 0.327 | 0.323 | 0.322 | 0.319 | 0.319 | 0.317 | 0.314 | 0.309 | 0.303 | 0.298 | 0.294 | 0.289 | 0.287 | 0.286 | 0.289 | 0.293 | 0.296 | 0.301 | 0.308 | 0.315 | 0.32 | 0.325 | 0.328 | 0.332 | 0.336 | 0.342 | 0.347 | 0.353 | 0.355 | 0.36 | 0.363 | 0.365 | 0.366 | 0.368 | 0.37 | 0.372 | 0.372 | 0.372 | 0.37 | 0.369 | 0.368 | 0.366 | 0.366 | 0.364 | 0.363 | 0.361 | 0.361 | 0.361 | 0.362 | 0.361 | 0.362 | 0.36 | 0.361 | 0.359 | 0.357 | 0.352 | 0.349 | 0.347 | 0.346 | 0.346 | 0.346 | 0.346 | 0.344 | 0.344 | 0.345 | 0.343 | 0.342 | 0.339 | 0.338 | 0.337 | 0.336 | 0.337 | 0.341 | 0.346 | 0.351 | 0.353 | 0.352 | 0.352 | 0.347 | 0.345 | 0.339 | 0.334 | 0.336 | 0.332 | 0.328 | 0.33 | 0.33 | 0.33 | 0.327 | 0.325 | 0.324 | 0.323 | 0.322 | 0.32 | 0.321 | 0.32 | 0.321 | 0.319 | 0.321 | 0.321 | 0.322 | 0.323 | 0.326 | 0.33 | 0.334 | 0.34 | 0.346 | 0.352 | 0.362 | 0.384 | 0.415 | 0.457 | 0.501 | 0.554 | 0.604 | 0.649 | 0.683 | 0.709 | 0.727 | 0.741 | 0.749 | 0.756 | 0.763 | 0.772 | 0.78 | 0.786 | 0.79 | 0.794 | 0.796 | 0.794 | 0.788 | 0.777 | 0.767 | 0.765 | 0.774 | 0.786 | 0.793 | 0.795 | 0.795 | 0.792 | 0.788 | 0.781 | 0.775 | 0.771 | 0.767 | 0.758 | 0.741 | 0.715 | 0.685 | 0.646 | 0.607 | 0.568 | 0.537 | 0.506 | 0.48 | 0.459 | 0.446 | 0.437 | 0.431 | 0.426 | 0.422 | 0.418 | 0.416 | 0.418 | 0.425 | 0.433 | 0.44 | 0.44 | 0.436 | 0.427 | 0.415 | 0.402 | 0.39 | 0.38 | 0.371 | 0.364 | 0.355 | 0.348 | 0.34 | 0.334 | 0.328 | 0.329 | 0.328 | 0.327 | 0.325 | 0.324 | 0.322 | 0.319 | 0.317 | 0.315 | 0.314 | 0.313 | 0.314 | 0.312 | 0.312 | 0.311 | 0.312 | 0.312 | 0.313 | 0.315 | 0.316 | 0.315 | 0.312 | 0.307 | 0.303 | 0.302 | 0.305 | 0.311 | 0.32 | 0.331 | 0.344 | 0.357 | 0.368 | 0.381 | 0.393 | 0.407 | 0.416 | 0.423 | 0.43 | 0.436 | 0.44 | 0.44 | 0.442 | 0.444 | 0.447 | 0.447 | 0.443 | 0.439 | 0.436 | 0.433 | 0.431 | 0.43 | 0.43 | 0.429 | 0.427 | 0.425 | 0.424 | 0.422 | 0.42 | 0.417 | 0.417 | 0.414 | 0.411 | 0.407 | 0.404 | 0.398 | 0.391 | 0.381 | 0.375 | 0.37 | 0.367 | 0.364 | 0.361 | 0.359 | 0.357 | 0.356 | 0.356 | 0.355 | 0.356 | 0.356 | 0.359 | 0.363 | 0.369 | 0.373 | 0.374 | 0.374 | 0.372 | 0.369 | 0.364 | 0.359 | 0.356 | 0.351 | 0.344 | 0.338 | 0.33 | 0.326 | 0.321 | 0.323 | 0.323 | 0.322 | 0.319 | 0.317 | 0.315 | 0.314 | 0.313 | 0.311 | 0.311 | 0.31 | 0.309 | 0.306 | 0.306 | 0.306 | 0.307 | 0.306 | 0.307 | 0.308 | 0.308 | 0.305 | 0.301 | 0.294 | 0.288 | 0.285 | 0.285 | 0.286 | 0.287 | 0.291 | 0.296 | 0.301 | 0.305 | 0.309 | 0.314 | 0.319 | 0.323 | 0.328 | 0.332 | 0.336 | 0.34 | 0.343 | 0.345 | 0.347 | 0.349 | 0.352 | 0.355 | 0.357 | 0.358 | 0.357 | 0.357 | 0.357 | 0.357 | 0.356 | 0.354 | 0.354 | 0.354 | 0.353 | 0.353 | 0.352 | 0.352 | 0.352 | 0.353 | 0.354 | 0.354 | 0.352 | 0.352 | 0.349 | 0.347 | 0.343 | 0.34 | 0.342 | 0.343 | 0.345 | 0.344 | 0.343 | 0.342 | 0.341 | 0.342 | 0.344 | 0.349 | 0.355 | 0.362 | 0.366 | 0.368 | 0.365 | 0.363 | 0.359 | 0.355 | 0.349 | 0.344 | 0.34 | 0.335 | 0.334 | 0.33 | 0.326 | 0.321 | 0.324 | 0.324 | 0.324 | 0.321 | 0.32 | 0.319 | 0.317 | 0.316 | 0.315 | 0.316 | 0.316 | 0.317 | 0.316 | 0.317 | 0.318 | 0.32 | 0.322 | 0.326 | 0.331 | 0.338 | 0.349 | 0.363 | 0.38 | 0.402 | 0.434 | 0.472 | 0.519 | 0.569 | 0.627 | 0.681 | 0.729 | 0.764 | 0.791 | 0.808 | 0.818 | 0.824 | 0.829 | 0.836 | 0.845 | 0.853 | 0.858 | 0.863 | 0.865 | 0.867 | 0.863 | 0.854 | 0.837 | 0.823 | 0.821 | 0.832 | 0.846 | 0.855 | 0.857 | 0.856 | 0.851 | 0.845 | 0.835 | 0.828 | 0.822 | 0.816 | 0.803 | 0.782 | 0.75 | 0.716 | 0.672 | 0.63 | 0.587 | 0.555 | 0.524 | 0.498 | 0.478 | 0.467 | 0.462 | 0.463 | 0.469 | 0.482 | 0.495 | 0.505 | 0.51 | 0.51 | 0.504 | 0.494 | 0.479 | 0.464 | 0.445 | 0.427 | 0.409 | 0.394 | 0.38 | 0.37 | 0.36 | 0.351 | 0.343 | 0.336 | 0.331 | 0.325 | 0.327 | 0.326 | 0.325 | 0.322 | 0.319 | 0.317 | 0.316 | 0.314 | 0.313 | 0.312 | 0.311 | 0.31 | 0.308 | 0.308 | 0.307 | 0.309 | 0.309 | 0.311 | 0.312 | 0.313 | 0.315 | 0.317 | 0.32 | 0.323 | 0.328 | 0.33 | 0.333 | 0.338 | 0.35 | 0.365 | 0.379 | 0.393 | 0.406 | 0.42 | 0.432 | 0.442 | 0.45 | 0.457 | 0.462 | 0.465 | 0.468 | 0.471 | 0.474 | 0.475 | 0.475 | 0.471 | 0.465 | 0.461 | 0.457 | 0.455 | 0.453 | 0.453 | 0.451 | 0.449 | 0.446 | 0.444 | 0.44 | 0.437 | 0.434 | 0.434 | 0.431 | 0.427 | 0.422 | 0.419 | 0.413 | 0.404 | 0.394 | 0.386 | 0.379 | 0.374 | 0.37 | 0.368 | 0.366 | 0.367 | 0.367 | 0.372 | 0.378 | 0.386 | 0.391 | 0.394 | 0.393 | 0.392 | 0.388 | 0.384 | 0.38 | 0.377 | 0.372 | 0.367 | 0.361 | 0.356 | 0.351 | 0.345 | 0.34 | 0.332 | 0.329 | 0.326 | 0.329 | 0.328 | 0.327 | 0.323 | 0.321 | 0.319 | 0.32 | 0.318 | 0.318 | 0.317 | 0.319 | 0.318 | 0.315 | 0.314 | 0.313 | 0.315 | 0.315 | 0.317 | 0.317 | 0.317 | 0.317 | 0.316 | 0.317 | 0.315 | 0.314 | 0.311 | 0.307 | 0.303 | 0.301 | 0.301 | 0.305 | 0.309 | 0.314 | 0.319 | 0.325 | 0.33 | 0.335 | 0.339 | 0.342 | 0.346 | 0.349 | 0.352 | 0.353 | 0.355 | 0.358 | 0.36 | 0.361 | 0.362 | 0.362 | 0.363 | 0.363 | 0.363 | 0.362 | 0.362 | 0.362 | 0.36 | 0.359 | 0.356 | 0.355 | 0.353 | 0.353 | 0.353 | 0.353 | 0.351 | 0.351 | 0.349 | 0.348 | 0.345 | 0.343 | 0.341 | 0.342 | 0.342 | 0.342 | 0.341 | 0.343 | 0.348 | 0.354 | 0.36 | 0.367 | 0.371 | 0.371 | 0.369 | 0.365 | 0.362 | 0.357 | 0.35 | 0.345 | 0.34 | 0.335 | 0.331 | 0.326 | 0.321 | 0.317 | 0.338 | 0.334 | 0.332 | 0.334 | 0.333 | 0.333 | 0.331 | 0.33 | 0.329 | 0.328 | 0.327 | 0.327 | 0.327 | 0.328 | 0.328 | 0.327 | 0.328 | 0.329 | 0.331 | 0.333 | 0.338 | 0.343 | 0.351 | 0.362 | 0.377 | 0.397 | 0.422 | 0.461 | 0.507 | 0.564 | 0.619 | 0.678 | 0.73 | 0.775 | 0.807 | 0.831 | 0.846 | 0.853 | 0.858 | 0.86 | 0.866 | 0.874 | 0.882 | 0.887 | 0.89 | 0.891 | 0.892 | 0.887 | 0.876 | 0.858 | 0.842 | 0.839 | 0.849 | 0.864 | 0.873 | 0.874 | 0.873 | 0.868 | 0.863 | 0.852 | 0.844 | 0.837 | 0.832 | 0.818 | 0.796 | 0.765 | 0.73 | 0.688 | 0.646 | 0.606 | 0.576 | 0.549 | 0.53 | 0.52 | 0.523 | 0.533 | 0.544 | 0.552 | 0.553 | 0.548 | 0.54 | 0.533 | 0.525 | 0.514 | 0.5 | 0.484 | 0.468 | 0.45 | 0.432 | 0.414 | 0.399 | 0.386 | 0.376 | 0.368 | 0.359 | 0.351 | 0.346 | 0.341 | 0.335 | 0.336 | 0.334 | 0.334 | 0.331 | 0.328 | 0.325 | 0.324 | 0.322 | 0.322 | 0.322 | 0.322 | 0.32 | 0.319 | 0.321 | 0.321 | 0.323 | 0.323 | 0.325 | 0.326 | 0.327 | 0.33 | 0.333 | 0.338 | 0.345 | 0.355 | 0.365 | 0.374 | 0.381 | 0.39 | 0.399 | 0.408 | 0.416 | 0.426 | 0.439 | 0.449 | 0.458 | 0.467 | 0.475 | 0.481 | 0.484 | 0.486 | 0.487 | 0.488 | 0.487 | 0.485 | 0.481 | 0.475 | 0.47 | 0.466 | 0.464 | 0.463 | 0.462 | 0.461 | 0.46 | 0.458 | 0.455 | 0.453 | 0.449 | 0.448 | 0.446 | 0.444 | 0.44 | 0.436 | 0.432 | 0.426 | 0.419 | 0.41 | 0.404 | 0.397 | 0.395 | 0.394 | 0.398 | 0.405 | 0.411 | 0.415 | 0.416 | 0.414 | 0.41 | 0.406 | 0.403 | 0.399 | 0.396 | 0.392 | 0.389 | 0.386 | 0.383 | 0.379 | 0.374 | 0.371 | 0.366 | 0.361 | 0.354 | 0.348 | 0.341 | 0.338 | 0.334 | 0.337 | 0.335 | 0.335 | 0.331 | 0.331 | 0.33 | 0.33 | 0.328 | 0.326 | 0.325 | 0.323 | 0.321 | 0.319 | 0.319 | 0.318 | 0.319 | 0.319 | 0.32 | 0.321 | 0.322 | 0.321 | 0.321 | 0.323 | 0.324 | 0.327 | 0.328 | 0.328 | 0.325 | 0.322 | 0.321 | 0.321 | 0.323 | 0.325 | 0.331 | 0.335 | 0.34 | 0.344 | 0.349 | 0.351 | 0.354 | 0.357 | 0.361 | 0.361 | 0.363 | 0.366 | 0.368 | 0.369 | 0.368 | 0.369 | 0.371 | 0.372 | 0.372 | 0.37 | 0.37 | 0.369 | 0.37 | 0.368 | 0.368 | 0.367 | 0.366 | 0.366 | 0.367 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.367 | 0.368 | 0.37 | 0.374 | 0.379 | 0.384 | 0.387 | 0.39 | 0.389 | 0.388 | 0.387 | 0.385 | 0.383 | 0.38 | 0.376 | 0.372 | 0.367 | 0.363 | 0.359 | 0.355 | 0.35 | 0.346 | 0.343 | 0.337 | 0.331 | 0.35 | 0.347 | 0.345 | 0.348 | 0.348 | 0.347 | 0.346 | 0.345 | 0.344 | 0.342 | 0.34 | 0.34 | 0.341 | 0.341 | 0.342 | 0.342 | 0.345 | 0.346 | 0.349 | 0.351 | 0.356 | 0.363 | 0.371 | 0.383 | 0.4 | 0.422 | 0.448 | 0.488 | 0.536 | 0.595 | 0.652 | 0.712 | 0.767 | 0.814 | 0.849 | 0.875 | 0.891 | 0.899 | 0.903 | 0.905 | 0.912 | 0.919 | 0.927 | 0.932 | 0.934 | 0.935 | 0.935 | 0.929 | 0.918 | 0.9 | 0.884 | 0.881 | 0.891 | 0.906 | 0.916 | 0.918 | 0.917 | 0.912 | 0.906 | 0.895 | 0.887 | 0.881 | 0.876 | 0.865 | 0.847 | 0.821 | 0.798 | 0.769 | 0.742 | 0.711 | 0.686 | 0.659 | 0.636 | 0.616 | 0.604 | 0.595 | 0.589 | 0.582 | 0.575 | 0.567 | 0.557 | 0.547 | 0.536 | 0.524 | 0.511 | 0.495 | 0.479 | 0.461 | 0.443 | 0.425 | 0.41 | 0.398 | 0.39 | 0.383 | 0.373 | 0.363 | 0.361 | 0.358 | 0.355 | 0.357 | 0.356 | 0.354 | 0.351 | 0.349 | 0.348 | 0.345 | 0.344 | 0.344 | 0.344 | 0.344 | 0.343 | 0.343 | 0.344 | 0.344 | 0.345 | 0.345 | 0.347 | 0.35 | 0.352 | 0.356 | 0.359 | 0.363 | 0.369 | 0.378 | 0.388 | 0.399 | 0.407 | 0.416 | 0.426 | 0.434 | 0.445 | 0.457 | 0.469 | 0.479 | 0.487 | 0.495 | 0.503 | 0.508 | 0.514 | 0.518 | 0.52 | 0.52 | 0.519 | 0.517 | 0.514 | 0.509 | 0.505 | 0.501 | 0.499 | 0.496 | 0.495 | 0.494 | 0.493 | 0.489 | 0.486 | 0.482 | 0.481 | 0.48 | 0.481 | 0.482 | 0.485 | 0.488 | 0.496 | 0.501 | 0.502 | 0.495 | 0.487 | 0.476 | 0.467 | 0.459 | 0.456 | 0.451 | 0.447 | 0.443 | 0.439 | 0.435 | 0.43 | 0.426 | 0.424 | 0.421 | 0.417 | 0.413 | 0.409 | 0.405 | 0.401 | 0.396 | 0.391 | 0.385 | 0.381 | 0.378 | 0.371 | 0.364 | 0.357 | 0.355 | 0.355 | 0.357 | 0.357 | 0.355 | 0.352 | 0.35 | 0.348 | 0.347 | 0.344 | 0.343 | 0.342 | 0.341 | 0.339 | 0.336 | 0.337 | 0.335 | 0.337 | 0.336 | 0.338 | 0.339 | 0.338 | 0.339 | 0.34 | 0.34 | 0.342 | 0.346 | 0.349 | 0.351 | 0.349 | 0.347 | 0.345 | 0.344 | 0.344 | 0.348 | 0.352 | 0.355 | 0.358 | 0.361 | 0.366 | 0.369 | 0.373 | 0.376 | 0.379 | 0.381 | 0.384 | 0.387 | 0.39 | 0.392 | 0.392 | 0.392 | 0.394 | 0.395 | 0.395 | 0.395 | 0.396 | 0.396 | 0.397 | 0.397 | 0.398 | 0.397 | 0.398 | 0.399 | 0.402 | 0.405 | 0.413 | 0.422 | 0.43 | 0.434 | 0.434 | 0.431 | 0.427 | 0.424 | 0.422 | 0.419 | 0.418 | 0.415 | 0.412 | 0.41 | 0.408 | 0.406 | 0.403 | 0.4 | 0.396 | 0.394 | 0.39 | 0.386 | 0.381 | 0.375 | 0.371 | 0.365 | 0.361 | 0.357 | 0.351 | 0.344 | 0.388 | 0.385 | 0.383 | 0.385 | 0.386 | 0.386 | 0.383 | 0.381 | 0.381 | 0.379 | 0.38 | 0.379 | 0.38 | 0.379 | 0.38 | 0.379 | 0.382 | 0.383 | 0.385 | 0.387 | 0.39 | 0.397 | 0.404 | 0.415 | 0.43 | 0.45 | 0.473 | 0.507 | 0.548 | 0.599 | 0.652 | 0.713 | 0.767 | 0.811 | 0.84 | 0.86 | 0.874 | 0.88 | 0.885 | 0.886 | 0.892 | 0.898 | 0.904 | 0.908 | 0.909 | 0.91 | 0.909 | 0.904 | 0.896 | 0.881 | 0.868 | 0.863 | 0.871 | 0.88 | 0.886 | 0.885 | 0.884 | 0.88 | 0.875 | 0.865 | 0.857 | 0.851 | 0.846 | 0.837 | 0.824 | 0.806 | 0.789 | 0.764 | 0.735 | 0.7 | 0.671 | 0.643 | 0.621 | 0.602 | 0.59 | 0.579 | 0.571 | 0.563 | 0.557 | 0.549 | 0.541 | 0.531 | 0.523 | 0.514 | 0.504 | 0.491 | 0.48 | 0.466 | 0.455 | 0.444 | 0.436 | 0.43 | 0.424 | 0.418 | 0.409 | 0.398 | 0.391 | 0.386 | 0.384 | 0.385 | 0.384 | 0.383 | 0.38 | 0.377 | 0.375 | 0.373 | 0.372 | 0.372 | 0.373 | 0.371 | 0.371 | 0.369 | 0.373 | 0.374 | 0.376 | 0.376 | 0.378 | 0.38 | 0.384 | 0.387 | 0.393 | 0.398 | 0.405 | 0.415 | 0.425 | 0.438 | 0.451 | 0.47 | 0.486 | 0.498 | 0.505 | 0.512 | 0.522 | 0.532 | 0.54 | 0.545 | 0.551 | 0.556 | 0.561 | 0.563 | 0.566 | 0.566 | 0.565 | 0.561 | 0.556 | 0.55 | 0.544 | 0.539 | 0.536 | 0.533 | 0.532 | 0.529 | 0.527 | 0.524 | 0.52 | 0.515 | 0.511 | 0.509 | 0.508 | 0.506 | 0.505 | 0.506 | 0.511 | 0.515 | 0.511 | 0.502 | 0.491 | 0.481 | 0.474 | 0.468 | 0.464 | 0.459 | 0.455 | 0.452 | 0.45 | 0.447 | 0.444 | 0.44 | 0.438 | 0.434 | 0.432 | 0.428 | 0.424 | 0.42 | 0.416 | 0.412 | 0.408 | 0.404 | 0.402 | 0.399 | 0.392 | 0.392 | 0.386 | 0.383 | 0.382 | 0.382 | 0.382 | 0.381 | 0.378 | 0.377 | 0.375 | 0.373 | 0.371 | 0.371 | 0.37 | 0.369 | 0.368 | 0.368 | 0.37 | 0.371 | 0.372 | 0.372 | 0.371 | 0.372 | 0.372 | 0.373 | 0.374 | 0.375 | 0.378 | 0.381 | 0.384 | 0.386 | 0.386 | 0.39 | 0.391 | 0.39 | 0.386 | 0.384 | 0.385 | 0.386 | 0.39 | 0.393 | 0.397 | 0.401 | 0.405 | 0.408 | 0.411 | 0.414 | 0.416 | 0.421 | 0.423 | 0.424 | 0.424 | 0.423 | 0.424 | 0.425 | 0.426 | 0.426 | 0.426 | 0.425 | 0.425 | 0.425 | 0.425 | 0.425 | 0.426 | 0.428 | 0.433 | 0.44 | 0.451 | 0.461 | 0.464 | 0.463 | 0.458 | 0.455 | 0.454 | 0.452 | 0.452 | 0.448 | 0.447 | 0.443 | 0.443 | 0.44 | 0.438 | 0.435 | 0.432 | 0.429 | 0.427 | 0.425 | 0.421 | 0.416 | 0.41 | 0.405 | 0.402 | 0.399 | 0.396 | 0.393 | 0.384 | 0.377
E3C | -3456 | 0.404 | 0.402 | 0.4 | 0.401 | 0.402 | 0.401 | 0.4 | 0.399 | 0.397 | 0.395 | 0.395 | 0.395 | 0.396 | 0.396 | 0.396 | 0.396 | 0.398 | 0.399 | 0.401 | 0.403 | 0.408 | 0.414 | 0.422 | 0.433 | 0.449 | 0.47 | 0.496 | 0.534 | 0.582 | 0.642 | 0.705 | 0.778 | 0.84 | 0.892 | 0.926 | 0.948 | 0.963 | 0.969 | 0.973 | 0.975 | 0.98 | 0.987 | 0.994 | 0.998 | 1 | 1 | 1 | 0.994 | 0.982 | 0.963 | 0.948 | 0.945 | 0.956 | 0.97 | 0.978 | 0.979 | 0.978 | 0.973 | 0.967 | 0.954 | 0.945 | 0.937 | 0.933 | 0.92 | 0.899 | 0.867 | 0.835 | 0.798 | 0.764 | 0.73 | 0.703 | 0.675 | 0.651 | 0.629 | 0.616 | 0.607 | 0.6 | 0.592 | 0.585 | 0.576 | 0.567 | 0.557 | 0.549 | 0.539 | 0.528 | 0.515 | 0.503 | 0.489 | 0.476 | 0.462 | 0.453 | 0.446 | 0.441 | 0.435 | 0.425 | 0.417 | 0.414 | 0.41 | 0.407 | 0.408 | 0.408 | 0.408 | 0.405 | 0.404 | 0.401 | 0.399 | 0.398 | 0.398 | 0.398 | 0.397 | 0.396 | 0.395 | 0.396 | 0.396 | 0.398 | 0.398 | 0.4 | 0.403 | 0.406 | 0.409 | 0.413 | 0.417 | 0.423 | 0.432 | 0.441 | 0.451 | 0.462 | 0.478 | 0.49 | 0.501 | 0.506 | 0.516 | 0.526 | 0.537 | 0.546 | 0.554 | 0.561 | 0.566 | 0.57 | 0.572 | 0.573 | 0.574 | 0.573 | 0.571 | 0.566 | 0.561 | 0.554 | 0.551 | 0.548 | 0.546 | 0.544 | 0.543 | 0.541 | 0.539 | 0.536 | 0.533 | 0.531 | 0.529 | 0.527 | 0.525 | 0.524 | 0.522 | 0.522 | 0.52 | 0.52 | 0.519 | 0.518 | 0.512 | 0.505 | 0.5 | 0.497 | 0.496 | 0.494 | 0.491 | 0.488 | 0.485 | 0.482 | 0.478 | 0.474 | 0.469 | 0.466 | 0.462 | 0.462 | 0.458 | 0.454 | 0.448 | 0.445 | 0.44 | 0.437 | 0.433 | 0.426 | 0.407 | 0.407 | 0.404 | 0.403 | 0.404 | 0.404 | 0.404 | 0.402 | 0.4 | 0.398 | 0.395 | 0.394 | 0.393 | 0.394 | 0.393 | 0.392 | 0.389 | 0.39 | 0.391 | 0.392 | 0.392 | 0.393 | 0.394 | 0.396 | 0.396 | 0.397 | 0.397 | 0.399 | 0.402 | 0.406 | 0.409 | 0.409 | 0.412 | 0.412 | 0.411 | 0.407 | 0.404 | 0.405 | 0.406 | 0.408 | 0.41 | 0.412 | 0.416 | 0.42 | 0.423 | 0.426 | 0.427 | 0.431 | 0.433 | 0.435 | 0.435 | 0.436 | 0.437 | 0.438 | 0.438 | 0.438 | 0.438 | 0.439 | 0.439 | 0.439 | 0.438 | 0.438 | 0.436 | 0.436 | 0.437 | 0.437 | 0.439 | 0.442 | 0.45 | 0.459 | 0.466 | 0.471 | 0.472 | 0.471 | 0.469 | 0.467 | 0.464 | 0.462 | 0.46 | 0.458 | 0.455 | 0.452 | 0.45 | 0.448 | 0.445 | 0.443 | 0.441 | 0.439 | 0.435 | 0.43 | 0.425 | 0.421 | 0.418 | 0.416 | 0.411 | 0.404 | 0.397 | 0.399 | 0.397 | 0.396 | 0.397 | 0.397 | 0.396 | 0.395 | 0.394 | 0.393 | 0.391 | 0.39 | 0.39 | 0.391 | 0.39 | 0.39 | 0.389 | 0.391 | 0.391 | 0.394 | 0.397 | 0.401 | 0.407 | 0.416 | 0.427 | 0.443 | 0.464 | 0.491 | 0.529 | 0.576 | 0.634 | 0.693 | 0.755 | 0.811 | 0.859 | 0.895 | 0.922 | 0.939 | 0.947 | 0.951 | 0.955 | 0.961 | 0.968 | 0.975 | 0.979 | 0.981 | 0.982 | 0.982 | 0.976 | 0.965 | 0.947 | 0.93 | 0.926 | 0.936 | 0.951 | 0.958 | 0.959 | 0.958 | 0.952 | 0.946 | 0.934 | 0.925 | 0.917 | 0.911 | 0.897 | 0.874 | 0.841 | 0.805 | 0.763 | 0.722 | 0.684 | 0.66 | 0.642 | 0.63 | 0.62 | 0.613 | 0.606 | 0.6 | 0.593 | 0.586 | 0.578 | 0.569 | 0.559 | 0.549 | 0.538 | 0.526 | 0.513 | 0.499 | 0.485 | 0.47 | 0.457 | 0.446 | 0.437 | 0.431 | 0.424 | 0.415 | 0.409 | 0.398 | 0.395 | 0.392 | 0.393 | 0.392 | 0.392 | 0.391 | 0.39 | 0.389 | 0.386 | 0.385 | 0.384 | 0.386 | 0.383 | 0.384 | 0.383 | 0.384 | 0.383 | 0.386 | 0.386 | 0.389 | 0.389 | 0.393 | 0.395 | 0.4 | 0.403 | 0.409 | 0.417 | 0.425 | 0.434 | 0.441 | 0.45 | 0.459 | 0.469 | 0.48 | 0.494 | 0.507 | 0.519 | 0.527 | 0.536 | 0.544 | 0.551 | 0.555 | 0.559 | 0.562 | 0.562 | 0.563 | 0.561 | 0.556 | 0.549 | 0.542 | 0.538 | 0.535 | 0.533 | 0.532 | 0.529 | 0.527 | 0.523 | 0.52 | 0.515 | 0.513 | 0.51 | 0.509 | 0.505 | 0.502 | 0.497 | 0.494 | 0.488 | 0.483 | 0.476 | 0.474 | 0.474 | 0.476 | 0.478 | 0.477 | 0.477 | 0.475 | 0.473 | 0.471 | 0.468 | 0.464 | 0.46 | 0.457 | 0.454 | 0.45 | 0.447 | 0.445 | 0.442 | 0.438 | 0.434 | 0.431 | 0.426 | 0.422 | 0.418 | 0.411 | 0.405 | 0.398 | 0.397 | 0.396 | 0.398 | 0.399 | 0.399 | 0.398 | 0.397 | 0.394 | 0.391 | 0.389 | 0.388 | 0.39 | 0.388 | 0.388 | 0.385 | 0.385 | 0.384 | 0.384 | 0.384 | 0.386 | 0.388 | 0.389 | 0.387 | 0.389 | 0.389 | 0.391 | 0.392 | 0.394 | 0.394 | 0.392 | 0.387 | 0.383 | 0.379 | 0.38 | 0.382 | 0.387 | 0.39 | 0.394 | 0.399 | 0.403 | 0.407 | 0.41 | 0.413 | 0.417 | 0.42 | 0.423 | 0.424 | 0.424 | 0.425 | 0.426 | 0.428 | 0.429 | 0.429 | 0.429 | 0.43 | 0.429 | 0.428 | 0.427 | 0.428 | 0.428 | 0.428 | 0.428 | 0.427 | 0.428 | 0.428 | 0.428 | 0.429 | 0.431 | 0.433 | 0.437 | 0.443 | 0.452 | 0.458 | 0.462 | 0.462 | 0.46 | 0.458 | 0.456 | 0.454 | 0.451 | 0.449 | 0.447 | 0.443 | 0.44 | 0.437 | 0.435 | 0.432 | 0.428 | 0.423 | 0.419 | 0.415 | 0.412 | 0.408 | 0.401 | 0.395 | 0.368 | 0.365 | 0.363 | 0.364 | 0.364 | 0.365 | 0.362 | 0.361 | 0.36 | 0.359 | 0.358 | 0.359 | 0.36 | 0.36 | 0.361 | 0.36 | 0.362 | 0.363 | 0.366 | 0.369 | 0.374 | 0.381 | 0.389 | 0.401 | 0.416 | 0.435 | 0.456 | 0.486 | 0.524 | 0.573 | 0.628 | 0.69 | 0.747 | 0.798 | 0.836 | 0.865 | 0.883 | 0.892 | 0.897 | 0.9 | 0.907 | 0.915 | 0.922 | 0.925 | 0.927 | 0.928 | 0.928 | 0.922 | 0.91 | 0.891 | 0.874 | 0.871 | 0.881 | 0.896 | 0.905 | 0.907 | 0.905 | 0.9 | 0.893 | 0.881 | 0.872 | 0.864 | 0.858 | 0.845 | 0.822 | 0.789 | 0.753 | 0.709 | 0.667 | 0.625 | 0.594 | 0.566 | 0.547 | 0.537 | 0.541 | 0.55 | 0.559 | 0.562 | 0.561 | 0.557 | 0.553 | 0.548 | 0.541 | 0.531 | 0.517 | 0.503 | 0.487 | 0.47 | 0.451 | 0.435 | 0.421 | 0.41 | 0.402 | 0.395 | 0.385 | 0.379 | 0.369 | 0.366 | 0.362 | 0.363 | 0.363 | 0.363 | 0.36 | 0.359 | 0.356 | 0.354 | 0.353 | 0.353 | 0.355 | 0.355 | 0.354 | 0.353 | 0.354 | 0.354 | 0.356 | 0.356 | 0.358 | 0.36 | 0.363 | 0.365 | 0.368 | 0.368 | 0.368 | 0.369 | 0.373 | 0.378 | 0.386 | 0.399 | 0.413 | 0.428 | 0.443 | 0.459 | 0.473 | 0.484 | 0.492 | 0.501 | 0.509 | 0.517 | 0.521 | 0.524 | 0.526 | 0.526 | 0.525 | 0.522 | 0.515 | 0.507 | 0.501 | 0.498 | 0.495 | 0.493 | 0.492 | 0.49 | 0.488 | 0.485 | 0.483 | 0.48 | 0.477 | 0.475 | 0.472 | 0.469 | 0.464 | 0.46 | 0.455 | 0.449 | 0.441 | 0.435 | 0.428 | 0.422 | 0.416 | 0.417 | 0.423 | 0.432 | 0.439 | 0.442 | 0.442 | 0.439 | 0.435 | 0.43 | 0.427 | 0.423 | 0.422 | 0.419 | 0.416 | 0.412 | 0.407 | 0.403 | 0.399 | 0.393 | 0.39 | 0.386 | 0.381 | 0.375 | 0.366 | 0.364 | 0.363 | 0.365 | 0.365 | 0.366 | 0.363 | 0.364 | 0.361 | 0.36 | 0.358 | 0.357 | 0.357 | 0.357 | 0.356 | 0.354 | 0.355 | 0.354 | 0.356 | 0.355 | 0.355 | 0.356 | 0.356 | 0.358 | 0.357 | 0.357 | 0.356 | 0.354 | 0.35 | 0.346 | 0.342 | 0.341 | 0.342 | 0.345 | 0.349 | 0.354 | 0.359 | 0.363 | 0.367 | 0.37 | 0.374 | 0.377 | 0.378 | 0.381 | 0.383 | 0.386 | 0.386 | 0.388 | 0.39 | 0.391 | 0.391 | 0.392 | 0.394 | 0.394 | 0.393 | 0.391 | 0.391 | 0.389 | 0.389 | 0.386 | 0.387 | 0.385 | 0.386 | 0.384 | 0.383 | 0.382 | 0.382 | 0.381 | 0.38 | 0.378 | 0.377 | 0.376 | 0.379 | 0.382 | 0.39 | 0.397 | 0.404 | 0.406 | 0.407 | 0.406 | 0.407 | 0.407 | 0.407 | 0.405 | 0.403 | 0.4 | 0.397 | 0.394 | 0.39 | 0.386 | 0.382 | 0.379 | 0.376 | 0.374 | 0.368 | 0.363 | 0.338 | 0.334 | 0.331 | 0.334 | 0.334 | 0.334 | 0.332 | 0.33 | 0.328 | 0.327 | 0.327 | 0.327 | 0.329 | 0.329 | 0.329 | 0.328 | 0.33 | 0.331 | 0.335 | 0.337 | 0.342 | 0.347 | 0.354 | 0.364 | 0.376 | 0.391 | 0.408 | 0.433 | 0.467 | 0.513 | 0.564 | 0.622 | 0.675 | 0.723 | 0.759 | 0.785 | 0.802 | 0.811 | 0.816 | 0.82 | 0.828 | 0.837 | 0.844 | 0.848 | 0.851 | 0.853 | 0.855 | 0.85 | 0.839 | 0.822 | 0.808 | 0.805 | 0.815 | 0.828 | 0.837 | 0.839 | 0.838 | 0.832 | 0.826 | 0.815 | 0.807 | 0.799 | 0.793 | 0.781 | 0.76 | 0.731 | 0.699 | 0.658 | 0.619 | 0.58 | 0.549 | 0.521 | 0.495 | 0.476 | 0.464 | 0.457 | 0.452 | 0.448 | 0.446 | 0.447 | 0.452 | 0.463 | 0.477 | 0.486 | 0.488 | 0.48 | 0.469 | 0.453 | 0.436 | 0.418 | 0.403 | 0.389 | 0.379 | 0.37 | 0.36 | 0.351 | 0.35 | 0.345 | 0.34 | 0.341 | 0.341 | 0.34 | 0.336 | 0.334 | 0.332 | 0.331 | 0.331 | 0.331 | 0.332 | 0.331 | 0.331 | 0.33 | 0.33 | 0.331 | 0.334 | 0.334 | 0.335 | 0.335 | 0.336 | 0.336 | 0.336 | 0.335 | 0.335 | 0.335 | 0.339 | 0.345 | 0.354 | 0.367 | 0.382 | 0.395 | 0.408 | 0.421 | 0.433 | 0.443 | 0.452 | 0.46 | 0.467 | 0.473 | 0.477 | 0.479 | 0.482 | 0.482 | 0.483 | 0.481 | 0.477 | 0.471 | 0.466 | 0.463 | 0.461 | 0.459 | 0.458 | 0.457 | 0.455 | 0.452 | 0.448 | 0.445 | 0.443 | 0.44 | 0.437 | 0.435 | 0.431 | 0.426 | 0.421 | 0.414 | 0.407 | 0.399 | 0.39 | 0.383 | 0.376 | 0.374 | 0.372 | 0.371 | 0.371 | 0.371 | 0.369 | 0.369 | 0.369 | 0.374 | 0.381 | 0.389 | 0.395 | 0.396 | 0.395 | 0.391 | 0.386 | 0.381 | 0.378 | 0.373 | 0.37 | 0.364 | 0.357 | 0.356 | 0.349 | 0.346 | 0.345 | 0.347 | 0.347 | 0.346 | 0.344 | 0.343 | 0.341 | 0.339 | 0.338 | 0.337 | 0.337 | 0.336 | 0.334 | 0.332 | 0.332 | 0.332 | 0.334 | 0.334 | 0.335 | 0.337 | 0.337 | 0.336 | 0.334 | 0.331 | 0.327 | 0.321 | 0.318 | 0.315 | 0.314 | 0.316 | 0.319 | 0.323 | 0.327 | 0.333 | 0.338 | 0.343 | 0.346 | 0.349 | 0.354 | 0.359 | 0.362 | 0.362 | 0.365 | 0.368 | 0.37 | 0.371 | 0.372 | 0.374 | 0.374 | 0.375 | 0.375 | 0.375 | 0.371 | 0.369 | 0.369 | 0.367 | 0.368 | 0.366 | 0.366 | 0.362 | 0.361 | 0.36 | 0.36 | 0.358 | 0.356 | 0.354 | 0.353 | 0.351 | 0.349 | 0.346 | 0.343 | 0.341 | 0.341 | 0.342 | 0.342 | 0.34 | 0.34 | 0.341 | 0.345 | 0.351 | 0.359 | 0.366 | 0.373 | 0.375 | 0.374 | 0.369 | 0.365 | 0.359 | 0.355 | 0.351 | 0.346 | 0.342 | 0.336 | 0.335 | 0.331 | 0.327 | 0.323 | 0.325 | 0.326 | 0.325 | 0.323 | 0.321 | 0.32 | 0.318 | 0.318 | 0.317 | 0.319 | 0.318 | 0.319 | 0.318 | 0.32 | 0.32 | 0.322 | 0.323 | 0.325 | 0.326 | 0.326 | 0.33 | 0.336 | 0.348 | 0.364 | 0.392 | 0.429 | 0.475 | 0.525 | 0.58 | 0.631 | 0.674 | 0.708 | 0.732 | 0.749 | 0.759 | 0.765 | 0.769 | 0.777 | 0.786 | 0.795 | 0.799 | 0.804 | 0.806 | 0.809 | 0.805 | 0.797 | 0.783 | 0.771 | 0.768 | 0.778 | 0.792 | 0.8 | 0.802 | 0.802 | 0.797 | 0.792 | 0.783 | 0.777 | 0.771 | 0.768 | 0.757 | 0.738 | 0.711 | 0.681 | 0.642 | 0.605 | 0.567 | 0.537 | 0.509 | 0.484 | 0.464 | 0.452 | 0.443 | 0.436 | 0.43 | 0.425 | 0.42 | 0.415 | 0.412 | 0.411 | 0.413 | 0.418 | 0.424 | 0.426 | 0.423 | 0.415 | 0.403 | 0.391 | 0.379 | 0.369 | 0.361 | 0.352 | 0.345 | 0.34 | 0.335 | 0.331 | 0.333 | 0.332 | 0.33 | 0.326 | 0.324 | 0.321 | 0.318 | 0.315 | 0.315 | 0.316 | 0.315 | 0.314 | 0.312 | 0.314 | 0.314 | 0.315 | 0.314 | 0.313 | 0.309 | 0.304 | 0.299 | 0.296 | 0.296 | 0.298 | 0.303 | 0.311 | 0.319 | 0.33 | 0.343 | 0.358 | 0.372 | 0.387 | 0.401 | 0.416 | 0.427 | 0.436 | 0.444 | 0.451 | 0.457 | 0.461 | 0.464 | 0.466 | 0.468 | 0.469 | 0.469 | 0.465 | 0.461 | 0.455 | 0.451 | 0.45 | 0.449 | 0.449 | 0.448 | 0.446 | 0.444 | 0.442 | 0.439 | 0.436 | 0.433 | 0.432 | 0.429 | 0.427 | 0.423 | 0.418 | 0.41 | 0.402 | 0.393 | 0.386 | 0.379 | 0.372 | 0.367 | 0.364 | 0.363 | 0.361 | 0.361 | 0.361 | 0.358 | 0.355 | 0.353 | 0.353 | 0.354 | 0.355 | 0.361 | 0.366 | 0.37 | 0.371 | 0.369 | 0.366 | 0.362 | 0.359 | 0.353 | 0.346 | 0.338 | 0.331 | 0.327 | 0.323 | 0.325 | 0.325 | 0.324 | 0.322 | 0.32 | 0.319 | 0.316 | 0.315 | 0.314 | 0.314 | 0.313 | 0.313 | 0.311 | 0.312 | 0.312 | 0.313 | 0.311 | 0.31 | 0.307 | 0.301 | 0.295 | 0.29 | 0.286 | 0.284 | 0.284 | 0.286 | 0.289 | 0.293 | 0.297 | 0.3 | 0.304 | 0.308 | 0.314 | 0.319 | 0.325 | 0.329 | 0.335 | 0.34 | 0.344 | 0.348 | 0.349 | 0.353 | 0.356 | 0.358 | 0.359 | 0.36 | 0.362 | 0.363 | 0.364 | 0.364 | 0.363 | 0.362 | 0.359 | 0.358 | 0.356 | 0.355 | 0.353 | 0.353 | 0.352 | 0.352 | 0.351 | 0.35 | 0.349 | 0.348 | 0.348 | 0.347 | 0.346 | 0.344 | 0.342 | 0.34 | 0.338 | 0.338 | 0.336 | 0.336 | 0.334 | 0.335 | 0.333 | 0.333 | 0.332 | 0.333 | 0.335 | 0.339 | 0.344 | 0.35 | 0.353 | 0.354 | 0.351 | 0.347 | 0.344 | 0.34 | 0.336 | 0.331 | 0.327 | 0.333 | 0.329 | 0.326 | 0.327 | 0.327 | 0.326 | 0.324 | 0.321 | 0.32 | 0.318 | 0.317 | 0.317 | 0.318 | 0.318 | 0.318 | 0.317 | 0.318 | 0.318 | 0.32 | 0.318 | 0.316 | 0.312 | 0.311 | 0.317 | 0.328 | 0.342 | 0.36 | 0.393 | 0.433 | 0.485 | 0.539 | 0.599 | 0.656 | 0.706 | 0.745 | 0.772 | 0.792 | 0.804 | 0.812 | 0.818 | 0.827 | 0.838 | 0.847 | 0.854 | 0.859 | 0.862 | 0.864 | 0.86 | 0.852 | 0.836 | 0.822 | 0.819 | 0.83 | 0.845 | 0.854 | 0.856 | 0.856 | 0.852 | 0.846 | 0.836 | 0.829 | 0.824 | 0.819 | 0.807 | 0.786 | 0.756 | 0.722 | 0.679 | 0.638 | 0.596 | 0.563 | 0.531 | 0.504 | 0.481 | 0.467 | 0.455 | 0.447 | 0.44 | 0.434 | 0.427 | 0.42 | 0.413 | 0.408 | 0.403 | 0.398 | 0.395 | 0.394 | 0.395 | 0.396 | 0.394 | 0.388 | 0.379 | 0.371 | 0.364 | 0.354 | 0.345 | 0.335 | 0.329 | 0.323 | 0.323 | 0.323 | 0.32 | 0.318 | 0.314 | 0.313 | 0.309 | 0.308 | 0.306 | 0.306 | 0.304 | 0.304 | 0.301 | 0.302 | 0.301 | 0.302 | 0.299 | 0.293 | 0.286 | 0.28 | 0.279 | 0.28 | 0.282 | 0.283 | 0.29 | 0.298 | 0.31 | 0.322 | 0.337 | 0.352 | 0.365 | 0.378 | 0.391 | 0.406 | 0.418 | 0.429 | 0.437 | 0.445 | 0.451 | 0.455 | 0.459 | 0.462 | 0.464 | 0.465 | 0.463 | 0.459 | 0.454 | 0.449 | 0.446 | 0.444 | 0.443 | 0.441 | 0.439 | 0.436 | 0.434 | 0.432 | 0.43 | 0.429 | 0.427 | 0.425 | 0.42 | 0.417 | 0.412 | 0.408 | 0.401 | 0.393 | 0.384 | 0.377 | 0.369 | 0.362 | 0.357 | 0.355 | 0.354 | 0.352 | 0.351 | 0.349 | 0.349 | 0.347 | 0.345 | 0.343 | 0.341 | 0.339 | 0.338 | 0.338 | 0.341 | 0.348 | 0.351 | 0.354 | 0.352 | 0.349 | 0.344 | 0.338 | 0.333 | 0.325 | 0.321 | 0.316 | 0.317 | 0.318 | 0.317 | 0.315 | 0.312 | 0.31 | 0.307 | 0.305 | 0.304 | 0.304 | 0.304 | 0.303 | 0.301 | 0.302 | 0.301 | 0.303 | 0.298 | 0.293 | 0.284 | 0.277 | 0.274 | 0.271 | 0.27 | 0.268 | 0.27 | 0.274 | 0.279 | 0.283 | 0.287 | 0.292 | 0.295 | 0.3 | 0.306 | 0.312 | 0.319 | 0.323 | 0.329 | 0.333 | 0.339 | 0.341 | 0.344 | 0.348 | 0.351 | 0.355 | 0.357 | 0.361 | 0.36 | 0.361 | 0.361 | 0.362 | 0.362 | 0.362 | 0.36 | 0.36 | 0.359 | 0.359 | 0.358 | 0.358 | 0.358 | 0.357 | 0.356 | 0.355 | 0.353 | 0.353 | 0.352 | 0.35 | 0.348 | 0.345 | 0.341 | 0.34 | 0.341 | 0.341 | 0.338 | 0.336 | 0.335 | 0.334 | 0.333 | 0.332 | 0.331 | 0.33 | 0.329 | 0.328 | 0.328 | 0.329 | 0.334 | 0.339 | 0.343 | 0.343 | 0.342 | 0.339 | 0.335 | 0.327 | 0.319 | 0.341 | 0.337 | 0.333 | 0.334 | 0.335 | 0.334 | 0.332 | 0.33 | 0.33 | 0.328 | 0.327 | 0.326 | 0.327 | 0.326 | 0.327 | 0.326 | 0.328 | 0.328 | 0.329 | 0.329 | 0.33 | 0.328 | 0.327 | 0.33 | 0.337 | 0.347 | 0.362 | 0.39 | 0.426 | 0.472 | 0.519 | 0.575 | 0.627 | 0.673 | 0.707 | 0.732 | 0.752 | 0.764 | 0.773 | 0.78 | 0.788 | 0.798 | 0.807 | 0.812 | 0.816 | 0.82 | 0.823 | 0.82 | 0.814 | 0.802 | 0.792 | 0.789 | 0.798 | 0.809 | 0.817 | 0.818 | 0.817 | 0.813 | 0.809 | 0.801 | 0.795 | 0.789 | 0.784 | 0.774 | 0.757 | 0.732 | 0.704 | 0.665 | 0.627 | 0.586 | 0.556 | 0.524 | 0.497 | 0.474 | 0.461 | 0.45 | 0.442 | 0.435 | 0.43 | 0.423 | 0.417 | 0.41 | 0.404 | 0.4 | 0.396 | 0.394 | 0.394 | 0.396 | 0.395 | 0.391 | 0.386 | 0.379 | 0.373 | 0.367 | 0.359 | 0.353 | 0.342 | 0.337 | 0.331 | 0.332 | 0.331 | 0.33 | 0.328 | 0.325 | 0.323 | 0.321 | 0.32 | 0.318 | 0.317 | 0.315 | 0.314 | 0.313 | 0.313 | 0.313 | 0.313 | 0.312 | 0.31 | 0.306 | 0.302 | 0.298 | 0.297 | 0.295 | 0.294 | 0.298 | 0.305 | 0.314 | 0.325 | 0.339 | 0.353 | 0.367 | 0.378 | 0.391 | 0.404 | 0.417 | 0.426 | 0.435 | 0.441 | 0.446 | 0.447 | 0.449 | 0.451 | 0.453 | 0.455 | 0.456 | 0.453 | 0.449 | 0.446 | 0.445 | 0.444 | 0.442 | 0.441 | 0.439 | 0.438 | 0.435 | 0.433 | 0.432 | 0.43 | 0.428 | 0.427 | 0.424 | 0.422 | 0.42 | 0.417 | 0.411 | 0.402 | 0.393 | 0.384 | 0.376 | 0.37 | 0.367 | 0.364 | 0.362 | 0.359 | 0.358 | 0.356 | 0.355 | 0.354 | 0.352 | 0.35 | 0.348 | 0.349 | 0.352 | 0.356 | 0.36 | 0.364 | 0.367 | 0.369 | 0.367 | 0.364 | 0.359 | 0.355 | 0.35 | 0.344 | 0.34 | 0.337 | 0.338 | 0.339 | 0.339 | 0.337 | 0.335 | 0.333 | 0.332 | 0.331 | 0.33 | 0.33 | 0.329 | 0.327 | 0.323 | 0.322 | 0.319 | 0.319 | 0.317 | 0.314 | 0.309 | 0.303 | 0.298 | 0.294 | 0.289 | 0.287 | 0.286 | 0.289 | 0.293 | 0.296 | 0.301 | 0.308 | 0.315 | 0.32 | 0.325 | 0.328 | 0.332 | 0.336 | 0.342 | 0.347 | 0.353 | 0.355 | 0.36 | 0.363 | 0.365 | 0.366 | 0.368 | 0.37 | 0.372 | 0.372 | 0.372 | 0.37 | 0.369 | 0.368 | 0.366 | 0.366 | 0.364 | 0.363 | 0.361 | 0.361 | 0.361 | 0.362 | 0.361 | 0.362 | 0.36 | 0.361 | 0.359 | 0.357 | 0.352 | 0.349 | 0.347 | 0.346 | 0.346 | 0.346 | 0.346 | 0.344 | 0.344 | 0.345 | 0.343 | 0.342 | 0.339 | 0.338 | 0.337 | 0.336 | 0.337 | 0.341 | 0.346 | 0.351 | 0.353 | 0.352 | 0.352 | 0.347 | 0.345 | 0.339 | 0.334 | 0.336 | 0.332 | 0.328 | 0.33 | 0.33 | 0.33 | 0.327 | 0.325 | 0.324 | 0.323 | 0.322 | 0.32 | 0.321 | 0.32 | 0.321 | 0.319 | 0.321 | 0.321 | 0.322 | 0.323 | 0.326 | 0.33 | 0.334 | 0.34 | 0.346 | 0.352 | 0.362 | 0.384 | 0.415 | 0.457 | 0.501 | 0.554 | 0.604 | 0.649 | 0.683 | 0.709 | 0.727 | 0.741 | 0.749 | 0.756 | 0.763 | 0.772 | 0.78 | 0.786 | 0.79 | 0.794 | 0.796 | 0.794 | 0.788 | 0.777 | 0.767 | 0.765 | 0.774 | 0.786 | 0.793 | 0.795 | 0.795 | 0.792 | 0.788 | 0.781 | 0.775 | 0.771 | 0.767 | 0.758 | 0.741 | 0.715 | 0.685 | 0.646 | 0.607 | 0.568 | 0.537 | 0.506 | 0.48 | 0.459 | 0.446 | 0.437 | 0.431 | 0.426 | 0.422 | 0.418 | 0.416 | 0.418 | 0.425 | 0.433 | 0.44 | 0.44 | 0.436 | 0.427 | 0.415 | 0.402 | 0.39 | 0.38 | 0.371 | 0.364 | 0.355 | 0.348 | 0.34 | 0.334 | 0.328 | 0.329 | 0.328 | 0.327 | 0.325 | 0.324 | 0.322 | 0.319 | 0.317 | 0.315 | 0.314 | 0.313 | 0.314 | 0.312 | 0.312 | 0.311 | 0.312 | 0.312 | 0.313 | 0.315 | 0.316 | 0.315 | 0.312 | 0.307 | 0.303 | 0.302 | 0.305 | 0.311 | 0.32 | 0.331 | 0.344 | 0.357 | 0.368 | 0.381 | 0.393 | 0.407 | 0.416 | 0.423 | 0.43 | 0.436 | 0.44 | 0.44 | 0.442 | 0.444 | 0.447 | 0.447 | 0.443 | 0.439 | 0.436 | 0.433 | 0.431 | 0.43 | 0.43 | 0.429 | 0.427 | 0.425 | 0.424 | 0.422 | 0.42 | 0.417 | 0.417 | 0.414 | 0.411 | 0.407 | 0.404 | 0.398 | 0.391 | 0.381 | 0.375 | 0.37 | 0.367 | 0.364 | 0.361 | 0.359 | 0.357 | 0.356 | 0.356 | 0.355 | 0.356 | 0.356 | 0.359 | 0.363 | 0.369 | 0.373 | 0.374 | 0.374 | 0.372 | 0.369 | 0.364 | 0.359 | 0.356 | 0.351 | 0.344 | 0.338 | 0.33 | 0.326 | 0.321 | 0.323 | 0.323 | 0.322 | 0.319 | 0.317 | 0.315 | 0.314 | 0.313 | 0.311 | 0.311 | 0.31 | 0.309 | 0.306 | 0.306 | 0.306 | 0.307 | 0.306 | 0.307 | 0.308 | 0.308 | 0.305 | 0.301 | 0.294 | 0.288 | 0.285 | 0.285 | 0.286 | 0.287 | 0.291 | 0.296 | 0.301 | 0.305 | 0.309 | 0.314 | 0.319 | 0.323 | 0.328 | 0.332 | 0.336 | 0.34 | 0.343 | 0.345 | 0.347 | 0.349 | 0.352 | 0.355 | 0.357 | 0.358 | 0.357 | 0.357 | 0.357 | 0.357 | 0.356 | 0.354 | 0.354 | 0.354 | 0.353 | 0.353 | 0.352 | 0.352 | 0.352 | 0.353 | 0.354 | 0.354 | 0.352 | 0.352 | 0.349 | 0.347 | 0.343 | 0.34 | 0.342 | 0.343 | 0.345 | 0.344 | 0.343 | 0.342 | 0.341 | 0.342 | 0.344 | 0.349 | 0.355 | 0.362 | 0.366 | 0.368 | 0.365 | 0.363 | 0.359 | 0.355 | 0.349 | 0.344 | 0.34 | 0.335 | 0.334 | 0.33 | 0.326 | 0.321 | 0.324 | 0.324 | 0.324 | 0.321 | 0.32 | 0.319 | 0.317 | 0.316 | 0.315 | 0.316 | 0.316 | 0.317 | 0.316 | 0.317 | 0.318 | 0.32 | 0.322 | 0.326 | 0.331 | 0.338 | 0.349 | 0.363 | 0.38 | 0.402 | 0.434 | 0.472 | 0.519 | 0.569 | 0.627 | 0.681 | 0.729 | 0.764 | 0.791 | 0.808 | 0.818 | 0.824 | 0.829 | 0.836 | 0.845 | 0.853 | 0.858 | 0.863 | 0.865 | 0.867 | 0.863 | 0.854 | 0.837 | 0.823 | 0.821 | 0.832 | 0.846 | 0.855 | 0.857 | 0.856 | 0.851 | 0.845 | 0.835 | 0.828 | 0.822 | 0.816 | 0.803 | 0.782 | 0.75 | 0.716 | 0.672 | 0.63 | 0.587 | 0.555 | 0.524 | 0.498 | 0.478 | 0.467 | 0.462 | 0.463 | 0.469 | 0.482 | 0.495 | 0.505 | 0.51 | 0.51 | 0.504 | 0.494 | 0.479 | 0.464 | 0.445 | 0.427 | 0.409 | 0.394 | 0.38 | 0.37 | 0.36 | 0.351 | 0.343 | 0.336 | 0.331 | 0.325 | 0.327 | 0.326 | 0.325 | 0.322 | 0.319 | 0.317 | 0.316 | 0.314 | 0.313 | 0.312 | 0.311 | 0.31 | 0.308 | 0.308 | 0.307 | 0.309 | 0.309 | 0.311 | 0.312 | 0.313 | 0.315 | 0.317 | 0.32 | 0.323 | 0.328 | 0.33 | 0.333 | 0.338 | 0.35 | 0.365 | 0.379 | 0.393 | 0.406 | 0.42 | 0.432 | 0.442 | 0.45 | 0.457 | 0.462 | 0.465 | 0.468 | 0.471 | 0.474 | 0.475 | 0.475 | 0.471 | 0.465 | 0.461 | 0.457 | 0.455 | 0.453 | 0.453 | 0.451 | 0.449 | 0.446 | 0.444 | 0.44 | 0.437 | 0.434 | 0.434 | 0.431 | 0.427 | 0.422 | 0.419 | 0.413 | 0.404 | 0.394 | 0.386 | 0.379 | 0.374 | 0.37 | 0.368 | 0.366 | 0.367 | 0.367 | 0.372 | 0.378 | 0.386 | 0.391 | 0.394 | 0.393 | 0.392 | 0.388 | 0.384 | 0.38 | 0.377 | 0.372 | 0.367 | 0.361 | 0.356 | 0.351 | 0.345 | 0.34 | 0.332 | 0.329 | 0.326 | 0.329 | 0.328 | 0.327 | 0.323 | 0.321 | 0.319 | 0.32 | 0.318 | 0.318 | 0.317 | 0.319 | 0.318 | 0.315 | 0.314 | 0.313 | 0.315 | 0.315 | 0.317 | 0.317 | 0.317 | 0.317 | 0.316 | 0.317 | 0.315 | 0.314 | 0.311 | 0.307 | 0.303 | 0.301 | 0.301 | 0.305 | 0.309 | 0.314 | 0.319 | 0.325 | 0.33 | 0.335 | 0.339 | 0.342 | 0.346 | 0.349 | 0.352 | 0.353 | 0.355 | 0.358 | 0.36 | 0.361 | 0.362 | 0.362 | 0.363 | 0.363 | 0.363 | 0.362 | 0.362 | 0.362 | 0.36 | 0.359 | 0.356 | 0.355 | 0.353 | 0.353 | 0.353 | 0.353 | 0.351 | 0.351 | 0.349 | 0.348 | 0.345 | 0.343 | 0.341 | 0.342 | 0.342 | 0.342 | 0.341 | 0.343 | 0.348 | 0.354 | 0.36 | 0.367 | 0.371 | 0.371 | 0.369 | 0.365 | 0.362 | 0.357 | 0.35 | 0.345 | 0.34 | 0.335 | 0.331 | 0.326 | 0.321 | 0.317 | 0.338 | 0.334 | 0.332 | 0.334 | 0.333 | 0.333 | 0.331 | 0.33 | 0.329 | 0.328 | 0.327 | 0.327 | 0.327 | 0.328 | 0.328 | 0.327 | 0.328 | 0.329 | 0.331 | 0.333 | 0.338 | 0.343 | 0.351 | 0.362 | 0.377 | 0.397 | 0.422 | 0.461 | 0.507 | 0.564 | 0.619 | 0.678 | 0.73 | 0.775 | 0.807 | 0.831 | 0.846 | 0.853 | 0.858 | 0.86 | 0.866 | 0.874 | 0.882 | 0.887 | 0.89 | 0.891 | 0.892 | 0.887 | 0.876 | 0.858 | 0.842 | 0.839 | 0.849 | 0.864 | 0.873 | 0.874 | 0.873 | 0.868 | 0.863 | 0.852 | 0.844 | 0.837 | 0.832 | 0.818 | 0.796 | 0.765 | 0.73 | 0.688 | 0.646 | 0.606 | 0.576 | 0.549 | 0.53 | 0.52 | 0.523 | 0.533 | 0.544 | 0.552 | 0.553 | 0.548 | 0.54 | 0.533 | 0.525 | 0.514 | 0.5 | 0.484 | 0.468 | 0.45 | 0.432 | 0.414 | 0.399 | 0.386 | 0.376 | 0.368 | 0.359 | 0.351 | 0.346 | 0.341 | 0.335 | 0.336 | 0.334 | 0.334 | 0.331 | 0.328 | 0.325 | 0.324 | 0.322 | 0.322 | 0.322 | 0.322 | 0.32 | 0.319 | 0.321 | 0.321 | 0.323 | 0.323 | 0.325 | 0.326 | 0.327 | 0.33 | 0.333 | 0.338 | 0.345 | 0.355 | 0.365 | 0.374 | 0.381 | 0.39 | 0.399 | 0.408 | 0.416 | 0.426 | 0.439 | 0.449 | 0.458 | 0.467 | 0.475 | 0.481 | 0.484 | 0.486 | 0.487 | 0.488 | 0.487 | 0.485 | 0.481 | 0.475 | 0.47 | 0.466 | 0.464 | 0.463 | 0.462 | 0.461 | 0.46 | 0.458 | 0.455 | 0.453 | 0.449 | 0.448 | 0.446 | 0.444 | 0.44 | 0.436 | 0.432 | 0.426 | 0.419 | 0.41 | 0.404 | 0.397 | 0.395 | 0.394 | 0.398 | 0.405 | 0.411 | 0.415 | 0.416 | 0.414 | 0.41 | 0.406 | 0.403 | 0.399 | 0.396 | 0.392 | 0.389 | 0.386 | 0.383 | 0.379 | 0.374 | 0.371 | 0.366 | 0.361 | 0.354 | 0.348 | 0.341 | 0.338 | 0.334 | 0.337 | 0.335 | 0.335 | 0.331 | 0.331 | 0.33 | 0.33 | 0.328 | 0.326 | 0.325 | 0.323 | 0.321 | 0.319 | 0.319 | 0.318 | 0.319 | 0.319 | 0.32 | 0.321 | 0.322 | 0.321 | 0.321 | 0.323 | 0.324 | 0.327 | 0.328 | 0.328 | 0.325 | 0.322 | 0.321 | 0.321 | 0.323 | 0.325 | 0.331 | 0.335 | 0.34 | 0.344 | 0.349 | 0.351 | 0.354 | 0.357 | 0.361 | 0.361 | 0.363 | 0.366 | 0.368 | 0.369 | 0.368 | 0.369 | 0.371 | 0.372 | 0.372 | 0.37 | 0.37 | 0.369 | 0.37 | 0.368 | 0.368 | 0.367 | 0.366 | 0.366 | 0.367 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.367 | 0.368 | 0.37 | 0.374 | 0.379 | 0.384 | 0.387 | 0.39 | 0.389 | 0.388 | 0.387 | 0.385 | 0.383 | 0.38 | 0.376 | 0.372 | 0.367 | 0.363 | 0.359 | 0.355 | 0.35 | 0.346 | 0.343 | 0.337 | 0.331 | 0.35 | 0.347 | 0.345 | 0.348 | 0.348 | 0.347 | 0.346 | 0.345 | 0.344 | 0.342 | 0.34 | 0.34 | 0.341 | 0.341 | 0.342 | 0.342 | 0.345 | 0.346 | 0.349 | 0.351 | 0.356 | 0.363 | 0.371 | 0.383 | 0.4 | 0.422 | 0.448 | 0.488 | 0.536 | 0.595 | 0.652 | 0.712 | 0.767 | 0.814 | 0.849 | 0.875 | 0.891 | 0.899 | 0.903 | 0.905 | 0.912 | 0.919 | 0.927 | 0.932 | 0.934 | 0.935 | 0.935 | 0.929 | 0.918 | 0.9 | 0.884 | 0.881 | 0.891 | 0.906 | 0.916 | 0.918 | 0.917 | 0.912 | 0.906 | 0.895 | 0.887 | 0.881 | 0.876 | 0.865 | 0.847 | 0.821 | 0.798 | 0.769 | 0.742 | 0.711 | 0.686 | 0.659 | 0.636 | 0.616 | 0.604 | 0.595 | 0.589 | 0.582 | 0.575 | 0.567 | 0.557 | 0.547 | 0.536 | 0.524 | 0.511 | 0.495 | 0.479 | 0.461 | 0.443 | 0.425 | 0.41 | 0.398 | 0.39 | 0.383 | 0.373 | 0.363 | 0.361 | 0.358 | 0.355 | 0.357 | 0.356 | 0.354 | 0.351 | 0.349 | 0.348 | 0.345 | 0.344 | 0.344 | 0.344 | 0.344 | 0.343 | 0.343 | 0.344 | 0.344 | 0.345 | 0.345 | 0.347 | 0.35 | 0.352 | 0.356 | 0.359 | 0.363 | 0.369 | 0.378 | 0.388 | 0.399 | 0.407 | 0.416 | 0.426 | 0.434 | 0.445 | 0.457 | 0.469 | 0.479 | 0.487 | 0.495 | 0.503 | 0.508 | 0.514 | 0.518 | 0.52 | 0.52 | 0.519 | 0.517 | 0.514 | 0.509 | 0.505 | 0.501 | 0.499 | 0.496 | 0.495 | 0.494 | 0.493 | 0.489 | 0.486 | 0.482 | 0.481 | 0.48 | 0.481 | 0.482 | 0.485 | 0.488 | 0.496 | 0.501 | 0.502 | 0.495 | 0.487 | 0.476 | 0.467 | 0.459 | 0.456 | 0.451 | 0.447 | 0.443 | 0.439 | 0.435 | 0.43 | 0.426 | 0.424 | 0.421 | 0.417 | 0.413 | 0.409 | 0.405 | 0.401 | 0.396 | 0.391 | 0.385 | 0.381 | 0.378 | 0.371 | 0.364 | 0.357 | 0.355 | 0.355 | 0.357 | 0.357 | 0.355 | 0.352 | 0.35 | 0.348 | 0.347 | 0.344 | 0.343 | 0.342 | 0.341 | 0.339 | 0.336 | 0.337 | 0.335 | 0.337 | 0.336 | 0.338 | 0.339 | 0.338 | 0.339 | 0.34 | 0.34 | 0.342 | 0.346 | 0.349 | 0.351 | 0.349 | 0.347 | 0.345 | 0.344 | 0.344 | 0.348 | 0.352 | 0.355 | 0.358 | 0.361 | 0.366 | 0.369 | 0.373 | 0.376 | 0.379 | 0.381 | 0.384 | 0.387 | 0.39 | 0.392 | 0.392 | 0.392 | 0.394 | 0.395 | 0.395 | 0.395 | 0.396 | 0.396 | 0.397 | 0.397 | 0.398 | 0.397 | 0.398 | 0.399 | 0.402 | 0.405 | 0.413 | 0.422 | 0.43 | 0.434 | 0.434 | 0.431 | 0.427 | 0.424 | 0.422 | 0.419 | 0.418 | 0.415 | 0.412 | 0.41 | 0.408 | 0.406 | 0.403 | 0.4 | 0.396 | 0.394 | 0.39 | 0.386 | 0.381 | 0.375 | 0.371 | 0.365 | 0.361 | 0.357 | 0.351 | 0.344 | 0.388 | 0.385 | 0.383 | 0.385 | 0.386 | 0.386 | 0.383 | 0.381 | 0.381 | 0.379 | 0.38 | 0.379 | 0.38 | 0.379 | 0.38 | 0.379 | 0.382 | 0.383 | 0.385 | 0.387 | 0.39 | 0.397 | 0.404 | 0.415 | 0.43 | 0.45 | 0.473 | 0.507 | 0.548 | 0.599 | 0.652 | 0.713 | 0.767 | 0.811 | 0.84 | 0.86 | 0.874 | 0.88 | 0.885 | 0.886 | 0.892 | 0.898 | 0.904 | 0.908 | 0.909 | 0.91 | 0.909 | 0.904 | 0.896 | 0.881 | 0.868 | 0.863 | 0.871 | 0.88 | 0.886 | 0.885 | 0.884 | 0.88 | 0.875 | 0.865 | 0.857 | 0.851 | 0.846 | 0.837 | 0.824 | 0.806 | 0.789 | 0.764 | 0.735 | 0.7 | 0.671 | 0.643 | 0.621 | 0.602 | 0.59 | 0.579 | 0.571 | 0.563 | 0.557 | 0.549 | 0.541 | 0.531 | 0.523 | 0.514 | 0.504 | 0.491 | 0.48 | 0.466 | 0.455 | 0.444 | 0.436 | 0.43 | 0.424 | 0.418 | 0.409 | 0.398 | 0.391 | 0.386 | 0.384 | 0.385 | 0.384 | 0.383 | 0.38 | 0.377 | 0.375 | 0.373 | 0.372 | 0.372 | 0.373 | 0.371 | 0.371 | 0.369 | 0.373 | 0.374 | 0.376 | 0.376 | 0.378 | 0.38 | 0.384 | 0.387 | 0.393 | 0.398 | 0.405 | 0.415 | 0.425 | 0.438 | 0.451 | 0.47 | 0.486 | 0.498 | 0.505 | 0.512 | 0.522 | 0.532 | 0.54 | 0.545 | 0.551 | 0.556 | 0.561 | 0.563 | 0.566 | 0.566 | 0.565 | 0.561 | 0.556 | 0.55 | 0.544 | 0.539 | 0.536 | 0.533 | 0.532 | 0.529 | 0.527 | 0.524 | 0.52 | 0.515 | 0.511 | 0.509 | 0.508 | 0.506 | 0.505 | 0.506 | 0.511 | 0.515 | 0.511 | 0.502 | 0.491 | 0.481 | 0.474 | 0.468 | 0.464 | 0.459 | 0.455 | 0.452 | 0.45 | 0.447 | 0.444 | 0.44 | 0.438 | 0.434 | 0.432 | 0.428 | 0.424 | 0.42 | 0.416 | 0.412 | 0.408 | 0.404 | 0.402 | 0.399 | 0.392 | 0.392 | 0.386 | 0.383 | 0.382 | 0.382 | 0.382 | 0.381 | 0.378 | 0.377 | 0.375 | 0.373 | 0.371 | 0.371 | 0.37 | 0.369 | 0.368 | 0.368 | 0.37 | 0.371 | 0.372 | 0.372 | 0.371 | 0.372 | 0.372 | 0.373 | 0.374 | 0.375 | 0.378 | 0.381 | 0.384 | 0.386 | 0.386 | 0.39 | 0.391 | 0.39 | 0.386 | 0.384 | 0.385 | 0.386 | 0.39 | 0.393 | 0.397 | 0.401 | 0.405 | 0.408 | 0.411 | 0.414 | 0.416 | 0.421 | 0.423 | 0.424 | 0.424 | 0.423 | 0.424 | 0.425 | 0.426 | 0.426 | 0.426 | 0.425 | 0.425 | 0.425 | 0.425 | 0.425 | 0.426 | 0.428 | 0.433 | 0.44 | 0.451 | 0.461 | 0.464 | 0.463 | 0.458 | 0.455 | 0.454 | 0.452 | 0.452 | 0.448 | 0.447 | 0.443 | 0.443 | 0.44 | 0.438 | 0.435 | 0.432 | 0.429 | 0.427 | 0.425 | 0.421 | 0.416 | 0.41 | 0.405 | 0.402 | 0.399 | 0.396 | 0.393 | 0.384 | 0.377
E3D | -3456 | 0.404 | 0.402 | 0.4 | 0.401 | 0.402 | 0.401 | 0.4 | 0.399 | 0.397 | 0.395 | 0.395 | 0.395 | 0.396 | 0.396 | 0.396 | 0.396 | 0.398 | 0.399 | 0.401 | 0.403 | 0.408 | 0.414 | 0.422 | 0.433 | 0.449 | 0.47 | 0.496 | 0.534 | 0.582 | 0.642 | 0.705 | 0.778 | 0.84 | 0.892 | 0.926 | 0.948 | 0.963 | 0.969 | 0.973 | 0.975 | 0.98 | 0.987 | 0.994 | 0.998 | 1 | 1 | 1 | 0.994 | 0.982 | 0.963 | 0.948 | 0.945 | 0.956 | 0.97 | 0.978 | 0.979 | 0.978 | 0.973 | 0.967 | 0.954 | 0.945 | 0.937 | 0.933 | 0.92 | 0.899 | 0.867 | 0.835 | 0.798 | 0.764 | 0.73 | 0.703 | 0.675 | 0.651 | 0.629 | 0.616 | 0.607 | 0.6 | 0.592 | 0.585 | 0.576 | 0.567 | 0.557 | 0.549 | 0.539 | 0.528 | 0.515 | 0.503 | 0.489 | 0.476 | 0.462 | 0.453 | 0.446 | 0.441 | 0.435 | 0.425 | 0.417 | 0.414 | 0.41 | 0.407 | 0.408 | 0.408 | 0.408 | 0.405 | 0.404 | 0.401 | 0.399 | 0.398 | 0.398 | 0.398 | 0.397 | 0.396 | 0.395 | 0.396 | 0.396 | 0.398 | 0.398 | 0.4 | 0.403 | 0.406 | 0.409 | 0.413 | 0.417 | 0.423 | 0.432 | 0.441 | 0.451 | 0.462 | 0.478 | 0.49 | 0.501 | 0.506 | 0.516 | 0.526 | 0.537 | 0.546 | 0.554 | 0.561 | 0.566 | 0.57 | 0.572 | 0.573 | 0.574 | 0.573 | 0.571 | 0.566 | 0.561 | 0.554 | 0.551 | 0.548 | 0.546 | 0.544 | 0.543 | 0.541 | 0.539 | 0.536 | 0.533 | 0.531 | 0.529 | 0.527 | 0.525 | 0.524 | 0.522 | 0.522 | 0.52 | 0.52 | 0.519 | 0.518 | 0.512 | 0.505 | 0.5 | 0.497 | 0.496 | 0.494 | 0.491 | 0.488 | 0.485 | 0.482 | 0.478 | 0.474 | 0.469 | 0.466 | 0.462 | 0.462 | 0.458 | 0.454 | 0.448 | 0.445 | 0.44 | 0.437 | 0.433 | 0.426 | 0.407 | 0.407 | 0.404 | 0.403 | 0.404 | 0.404 | 0.404 | 0.402 | 0.4 | 0.398 | 0.395 | 0.394 | 0.393 | 0.394 | 0.393 | 0.392 | 0.389 | 0.39 | 0.391 | 0.392 | 0.392 | 0.393 | 0.394 | 0.396 | 0.396 | 0.397 | 0.397 | 0.399 | 0.402 | 0.406 | 0.409 | 0.409 | 0.412 | 0.412 | 0.411 | 0.407 | 0.404 | 0.405 | 0.406 | 0.408 | 0.41 | 0.412 | 0.416 | 0.42 | 0.423 | 0.426 | 0.427 | 0.431 | 0.433 | 0.435 | 0.435 | 0.436 | 0.437 | 0.438 | 0.438 | 0.438 | 0.438 | 0.439 | 0.439 | 0.439 | 0.438 | 0.438 | 0.436 | 0.436 | 0.437 | 0.437 | 0.439 | 0.442 | 0.45 | 0.459 | 0.466 | 0.471 | 0.472 | 0.471 | 0.469 | 0.467 | 0.464 | 0.462 | 0.46 | 0.458 | 0.455 | 0.452 | 0.45 | 0.448 | 0.445 | 0.443 | 0.441 | 0.439 | 0.435 | 0.43 | 0.425 | 0.421 | 0.418 | 0.416 | 0.411 | 0.404 | 0.397 | 0.399 | 0.397 | 0.396 | 0.397 | 0.397 | 0.396 | 0.395 | 0.394 | 0.393 | 0.391 | 0.39 | 0.39 | 0.391 | 0.39 | 0.39 | 0.389 | 0.391 | 0.391 | 0.394 | 0.397 | 0.401 | 0.407 | 0.416 | 0.427 | 0.443 | 0.464 | 0.491 | 0.529 | 0.576 | 0.634 | 0.693 | 0.755 | 0.811 | 0.859 | 0.895 | 0.922 | 0.939 | 0.947 | 0.951 | 0.955 | 0.961 | 0.968 | 0.975 | 0.979 | 0.981 | 0.982 | 0.982 | 0.976 | 0.965 | 0.947 | 0.93 | 0.926 | 0.936 | 0.951 | 0.958 | 0.959 | 0.958 | 0.952 | 0.946 | 0.934 | 0.925 | 0.917 | 0.911 | 0.897 | 0.874 | 0.841 | 0.805 | 0.763 | 0.722 | 0.684 | 0.66 | 0.642 | 0.63 | 0.62 | 0.613 | 0.606 | 0.6 | 0.593 | 0.586 | 0.578 | 0.569 | 0.559 | 0.549 | 0.538 | 0.526 | 0.513 | 0.499 | 0.485 | 0.47 | 0.457 | 0.446 | 0.437 | 0.431 | 0.424 | 0.415 | 0.409 | 0.398 | 0.395 | 0.392 | 0.393 | 0.392 | 0.392 | 0.391 | 0.39 | 0.389 | 0.386 | 0.385 | 0.384 | 0.386 | 0.383 | 0.384 | 0.383 | 0.384 | 0.383 | 0.386 | 0.386 | 0.389 | 0.389 | 0.393 | 0.395 | 0.4 | 0.403 | 0.409 | 0.417 | 0.425 | 0.434 | 0.441 | 0.45 | 0.459 | 0.469 | 0.48 | 0.494 | 0.507 | 0.519 | 0.527 | 0.536 | 0.544 | 0.551 | 0.555 | 0.559 | 0.562 | 0.562 | 0.563 | 0.561 | 0.556 | 0.549 | 0.542 | 0.538 | 0.535 | 0.533 | 0.532 | 0.529 | 0.527 | 0.523 | 0.52 | 0.515 | 0.513 | 0.51 | 0.509 | 0.505 | 0.502 | 0.497 | 0.494 | 0.488 | 0.483 | 0.476 | 0.474 | 0.474 | 0.476 | 0.478 | 0.477 | 0.477 | 0.475 | 0.473 | 0.471 | 0.468 | 0.464 | 0.46 | 0.457 | 0.454 | 0.45 | 0.447 | 0.445 | 0.442 | 0.438 | 0.434 | 0.431 | 0.426 | 0.422 | 0.418 | 0.411 | 0.405 | 0.398 | 0.397 | 0.396 | 0.398 | 0.399 | 0.399 | 0.398 | 0.397 | 0.394 | 0.391 | 0.389 | 0.388 | 0.39 | 0.388 | 0.388 | 0.385 | 0.385 | 0.384 | 0.384 | 0.384 | 0.386 | 0.388 | 0.389 | 0.387 | 0.389 | 0.389 | 0.391 | 0.392 | 0.394 | 0.394 | 0.392 | 0.387 | 0.383 | 0.379 | 0.38 | 0.382 | 0.387 | 0.39 | 0.394 | 0.399 | 0.403 | 0.407 | 0.41 | 0.413 | 0.417 | 0.42 | 0.423 | 0.424 | 0.424 | 0.425 | 0.426 | 0.428 | 0.429 | 0.429 | 0.429 | 0.43 | 0.429 | 0.428 | 0.427 | 0.428 | 0.428 | 0.428 | 0.428 | 0.427 | 0.428 | 0.428 | 0.428 | 0.429 | 0.431 | 0.433 | 0.437 | 0.443 | 0.452 | 0.458 | 0.462 | 0.462 | 0.46 | 0.458 | 0.456 | 0.454 | 0.451 | 0.449 | 0.447 | 0.443 | 0.44 | 0.437 | 0.435 | 0.432 | 0.428 | 0.423 | 0.419 | 0.415 | 0.412 | 0.408 | 0.401 | 0.395 | 0.368 | 0.365 | 0.363 | 0.364 | 0.364 | 0.365 | 0.362 | 0.361 | 0.36 | 0.359 | 0.358 | 0.359 | 0.36 | 0.36 | 0.361 | 0.36 | 0.362 | 0.363 | 0.366 | 0.369 | 0.374 | 0.381 | 0.389 | 0.401 | 0.416 | 0.435 | 0.456 | 0.486 | 0.524 | 0.573 | 0.628 | 0.69 | 0.747 | 0.798 | 0.836 | 0.865 | 0.883 | 0.892 | 0.897 | 0.9 | 0.907 | 0.915 | 0.922 | 0.925 | 0.927 | 0.928 | 0.928 | 0.922 | 0.91 | 0.891 | 0.874 | 0.871 | 0.881 | 0.896 | 0.905 | 0.907 | 0.905 | 0.9 | 0.893 | 0.881 | 0.872 | 0.864 | 0.858 | 0.845 | 0.822 | 0.789 | 0.753 | 0.709 | 0.667 | 0.625 | 0.594 | 0.566 | 0.547 | 0.537 | 0.541 | 0.55 | 0.559 | 0.562 | 0.561 | 0.557 | 0.553 | 0.548 | 0.541 | 0.531 | 0.517 | 0.503 | 0.487 | 0.47 | 0.451 | 0.435 | 0.421 | 0.41 | 0.402 | 0.395 | 0.385 | 0.379 | 0.369 | 0.366 | 0.362 | 0.363 | 0.363 | 0.363 | 0.36 | 0.359 | 0.356 | 0.354 | 0.353 | 0.353 | 0.355 | 0.355 | 0.354 | 0.353 | 0.354 | 0.354 | 0.356 | 0.356 | 0.358 | 0.36 | 0.363 | 0.365 | 0.368 | 0.368 | 0.368 | 0.369 | 0.373 | 0.378 | 0.386 | 0.399 | 0.413 | 0.428 | 0.443 | 0.459 | 0.473 | 0.484 | 0.492 | 0.501 | 0.509 | 0.517 | 0.521 | 0.524 | 0.526 | 0.526 | 0.525 | 0.522 | 0.515 | 0.507 | 0.501 | 0.498 | 0.495 | 0.493 | 0.492 | 0.49 | 0.488 | 0.485 | 0.483 | 0.48 | 0.477 | 0.475 | 0.472 | 0.469 | 0.464 | 0.46 | 0.455 | 0.449 | 0.441 | 0.435 | 0.428 | 0.422 | 0.416 | 0.417 | 0.423 | 0.432 | 0.439 | 0.442 | 0.442 | 0.439 | 0.435 | 0.43 | 0.427 | 0.423 | 0.422 | 0.419 | 0.416 | 0.412 | 0.407 | 0.403 | 0.399 | 0.393 | 0.39 | 0.386 | 0.381 | 0.375 | 0.366 | 0.364 | 0.363 | 0.365 | 0.365 | 0.366 | 0.363 | 0.364 | 0.361 | 0.36 | 0.358 | 0.357 | 0.357 | 0.357 | 0.356 | 0.354 | 0.355 | 0.354 | 0.356 | 0.355 | 0.355 | 0.356 | 0.356 | 0.358 | 0.357 | 0.357 | 0.356 | 0.354 | 0.35 | 0.346 | 0.342 | 0.341 | 0.342 | 0.345 | 0.349 | 0.354 | 0.359 | 0.363 | 0.367 | 0.37 | 0.374 | 0.377 | 0.378 | 0.381 | 0.383 | 0.386 | 0.386 | 0.388 | 0.39 | 0.391 | 0.391 | 0.392 | 0.394 | 0.394 | 0.393 | 0.391 | 0.391 | 0.389 | 0.389 | 0.386 | 0.387 | 0.385 | 0.386 | 0.384 | 0.383 | 0.382 | 0.382 | 0.381 | 0.38 | 0.378 | 0.377 | 0.376 | 0.379 | 0.382 | 0.39 | 0.397 | 0.404 | 0.406 | 0.407 | 0.406 | 0.407 | 0.407 | 0.407 | 0.405 | 0.403 | 0.4 | 0.397 | 0.394 | 0.39 | 0.386 | 0.382 | 0.379 | 0.376 | 0.374 | 0.368 | 0.363 | 0.338 | 0.334 | 0.331 | 0.334 | 0.334 | 0.334 | 0.332 | 0.33 | 0.328 | 0.327 | 0.327 | 0.327 | 0.329 | 0.329 | 0.329 | 0.328 | 0.33 | 0.331 | 0.335 | 0.337 | 0.342 | 0.347 | 0.354 | 0.364 | 0.376 | 0.391 | 0.408 | 0.433 | 0.467 | 0.513 | 0.564 | 0.622 | 0.675 | 0.723 | 0.759 | 0.785 | 0.802 | 0.811 | 0.816 | 0.82 | 0.828 | 0.837 | 0.844 | 0.848 | 0.851 | 0.853 | 0.855 | 0.85 | 0.839 | 0.822 | 0.808 | 0.805 | 0.815 | 0.828 | 0.837 | 0.839 | 0.838 | 0.832 | 0.826 | 0.815 | 0.807 | 0.799 | 0.793 | 0.781 | 0.76 | 0.731 | 0.699 | 0.658 | 0.619 | 0.58 | 0.549 | 0.521 | 0.495 | 0.476 | 0.464 | 0.457 | 0.452 | 0.448 | 0.446 | 0.447 | 0.452 | 0.463 | 0.477 | 0.486 | 0.488 | 0.48 | 0.469 | 0.453 | 0.436 | 0.418 | 0.403 | 0.389 | 0.379 | 0.37 | 0.36 | 0.351 | 0.35 | 0.345 | 0.34 | 0.341 | 0.341 | 0.34 | 0.336 | 0.334 | 0.332 | 0.331 | 0.331 | 0.331 | 0.332 | 0.331 | 0.331 | 0.33 | 0.33 | 0.331 | 0.334 | 0.334 | 0.335 | 0.335 | 0.336 | 0.336 | 0.336 | 0.335 | 0.335 | 0.335 | 0.339 | 0.345 | 0.354 | 0.367 | 0.382 | 0.395 | 0.408 | 0.421 | 0.433 | 0.443 | 0.452 | 0.46 | 0.467 | 0.473 | 0.477 | 0.479 | 0.482 | 0.482 | 0.483 | 0.481 | 0.477 | 0.471 | 0.466 | 0.463 | 0.461 | 0.459 | 0.458 | 0.457 | 0.455 | 0.452 | 0.448 | 0.445 | 0.443 | 0.44 | 0.437 | 0.435 | 0.431 | 0.426 | 0.421 | 0.414 | 0.407 | 0.399 | 0.39 | 0.383 | 0.376 | 0.374 | 0.372 | 0.371 | 0.371 | 0.371 | 0.369 | 0.369 | 0.369 | 0.374 | 0.381 | 0.389 | 0.395 | 0.396 | 0.395 | 0.391 | 0.386 | 0.381 | 0.378 | 0.373 | 0.37 | 0.364 | 0.357 | 0.356 | 0.349 | 0.346 | 0.345 | 0.347 | 0.347 | 0.346 | 0.344 | 0.343 | 0.341 | 0.339 | 0.338 | 0.337 | 0.337 | 0.336 | 0.334 | 0.332 | 0.332 | 0.332 | 0.334 | 0.334 | 0.335 | 0.337 | 0.337 | 0.336 | 0.334 | 0.331 | 0.327 | 0.321 | 0.318 | 0.315 | 0.314 | 0.316 | 0.319 | 0.323 | 0.327 | 0.333 | 0.338 | 0.343 | 0.346 | 0.349 | 0.354 | 0.359 | 0.362 | 0.362 | 0.365 | 0.368 | 0.37 | 0.371 | 0.372 | 0.374 | 0.374 | 0.375 | 0.375 | 0.375 | 0.371 | 0.369 | 0.369 | 0.367 | 0.368 | 0.366 | 0.366 | 0.362 | 0.361 | 0.36 | 0.36 | 0.358 | 0.356 | 0.354 | 0.353 | 0.351 | 0.349 | 0.346 | 0.343 | 0.341 | 0.341 | 0.342 | 0.342 | 0.34 | 0.34 | 0.341 | 0.345 | 0.351 | 0.359 | 0.366 | 0.373 | 0.375 | 0.374 | 0.369 | 0.365 | 0.359 | 0.355 | 0.351 | 0.346 | 0.342 | 0.336 | 0.335 | 0.331 | 0.327 | 0.323 | 0.325 | 0.326 | 0.325 | 0.323 | 0.321 | 0.32 | 0.318 | 0.318 | 0.317 | 0.319 | 0.318 | 0.319 | 0.318 | 0.32 | 0.32 | 0.322 | 0.323 | 0.325 | 0.326 | 0.326 | 0.33 | 0.336 | 0.348 | 0.364 | 0.392 | 0.429 | 0.475 | 0.525 | 0.58 | 0.631 | 0.674 | 0.708 | 0.732 | 0.749 | 0.759 | 0.765 | 0.769 | 0.777 | 0.786 | 0.795 | 0.799 | 0.804 | 0.806 | 0.809 | 0.805 | 0.797 | 0.783 | 0.771 | 0.768 | 0.778 | 0.792 | 0.8 | 0.802 | 0.802 | 0.797 | 0.792 | 0.783 | 0.777 | 0.771 | 0.768 | 0.757 | 0.738 | 0.711 | 0.681 | 0.642 | 0.605 | 0.567 | 0.537 | 0.509 | 0.484 | 0.464 | 0.452 | 0.443 | 0.436 | 0.43 | 0.425 | 0.42 | 0.415 | 0.412 | 0.411 | 0.413 | 0.418 | 0.424 | 0.426 | 0.423 | 0.415 | 0.403 | 0.391 | 0.379 | 0.369 | 0.361 | 0.352 | 0.345 | 0.34 | 0.335 | 0.331 | 0.333 | 0.332 | 0.33 | 0.326 | 0.324 | 0.321 | 0.318 | 0.315 | 0.315 | 0.316 | 0.315 | 0.314 | 0.312 | 0.314 | 0.314 | 0.315 | 0.314 | 0.313 | 0.309 | 0.304 | 0.299 | 0.296 | 0.296 | 0.298 | 0.303 | 0.311 | 0.319 | 0.33 | 0.343 | 0.358 | 0.372 | 0.387 | 0.401 | 0.416 | 0.427 | 0.436 | 0.444 | 0.451 | 0.457 | 0.461 | 0.464 | 0.466 | 0.468 | 0.469 | 0.469 | 0.465 | 0.461 | 0.455 | 0.451 | 0.45 | 0.449 | 0.449 | 0.448 | 0.446 | 0.444 | 0.442 | 0.439 | 0.436 | 0.433 | 0.432 | 0.429 | 0.427 | 0.423 | 0.418 | 0.41 | 0.402 | 0.393 | 0.386 | 0.379 | 0.372 | 0.367 | 0.364 | 0.363 | 0.361 | 0.361 | 0.361 | 0.358 | 0.355 | 0.353 | 0.353 | 0.354 | 0.355 | 0.361 | 0.366 | 0.37 | 0.371 | 0.369 | 0.366 | 0.362 | 0.359 | 0.353 | 0.346 | 0.338 | 0.331 | 0.327 | 0.323 | 0.325 | 0.325 | 0.324 | 0.322 | 0.32 | 0.319 | 0.316 | 0.315 | 0.314 | 0.314 | 0.313 | 0.313 | 0.311 | 0.312 | 0.312 | 0.313 | 0.311 | 0.31 | 0.307 | 0.301 | 0.295 | 0.29 | 0.286 | 0.284 | 0.284 | 0.286 | 0.289 | 0.293 | 0.297 | 0.3 | 0.304 | 0.308 | 0.314 | 0.319 | 0.325 | 0.329 | 0.335 | 0.34 | 0.344 | 0.348 | 0.349 | 0.353 | 0.356 | 0.358 | 0.359 | 0.36 | 0.362 | 0.363 | 0.364 | 0.364 | 0.363 | 0.362 | 0.359 | 0.358 | 0.356 | 0.355 | 0.353 | 0.353 | 0.352 | 0.352 | 0.351 | 0.35 | 0.349 | 0.348 | 0.348 | 0.347 | 0.346 | 0.344 | 0.342 | 0.34 | 0.338 | 0.338 | 0.336 | 0.336 | 0.334 | 0.335 | 0.333 | 0.333 | 0.332 | 0.333 | 0.335 | 0.339 | 0.344 | 0.35 | 0.353 | 0.354 | 0.351 | 0.347 | 0.344 | 0.34 | 0.336 | 0.331 | 0.327 | 0.333 | 0.329 | 0.326 | 0.327 | 0.327 | 0.326 | 0.324 | 0.321 | 0.32 | 0.318 | 0.317 | 0.317 | 0.318 | 0.318 | 0.318 | 0.317 | 0.318 | 0.318 | 0.32 | 0.318 | 0.316 | 0.312 | 0.311 | 0.317 | 0.328 | 0.342 | 0.36 | 0.393 | 0.433 | 0.485 | 0.539 | 0.599 | 0.656 | 0.706 | 0.745 | 0.772 | 0.792 | 0.804 | 0.812 | 0.818 | 0.827 | 0.838 | 0.847 | 0.854 | 0.859 | 0.862 | 0.864 | 0.86 | 0.852 | 0.836 | 0.822 | 0.819 | 0.83 | 0.845 | 0.854 | 0.856 | 0.856 | 0.852 | 0.846 | 0.836 | 0.829 | 0.824 | 0.819 | 0.807 | 0.786 | 0.756 | 0.722 | 0.679 | 0.638 | 0.596 | 0.563 | 0.531 | 0.504 | 0.481 | 0.467 | 0.455 | 0.447 | 0.44 | 0.434 | 0.427 | 0.42 | 0.413 | 0.408 | 0.403 | 0.398 | 0.395 | 0.394 | 0.395 | 0.396 | 0.394 | 0.388 | 0.379 | 0.371 | 0.364 | 0.354 | 0.345 | 0.335 | 0.329 | 0.323 | 0.323 | 0.323 | 0.32 | 0.318 | 0.314 | 0.313 | 0.309 | 0.308 | 0.306 | 0.306 | 0.304 | 0.304 | 0.301 | 0.302 | 0.301 | 0.302 | 0.299 | 0.293 | 0.286 | 0.28 | 0.279 | 0.28 | 0.282 | 0.283 | 0.29 | 0.298 | 0.31 | 0.322 | 0.337 | 0.352 | 0.365 | 0.378 | 0.391 | 0.406 | 0.418 | 0.429 | 0.437 | 0.445 | 0.451 | 0.455 | 0.459 | 0.462 | 0.464 | 0.465 | 0.463 | 0.459 | 0.454 | 0.449 | 0.446 | 0.444 | 0.443 | 0.441 | 0.439 | 0.436 | 0.434 | 0.432 | 0.43 | 0.429 | 0.427 | 0.425 | 0.42 | 0.417 | 0.412 | 0.408 | 0.401 | 0.393 | 0.384 | 0.377 | 0.369 | 0.362 | 0.357 | 0.355 | 0.354 | 0.352 | 0.351 | 0.349 | 0.349 | 0.347 | 0.345 | 0.343 | 0.341 | 0.339 | 0.338 | 0.338 | 0.341 | 0.348 | 0.351 | 0.354 | 0.352 | 0.349 | 0.344 | 0.338 | 0.333 | 0.325 | 0.321 | 0.316 | 0.317 | 0.318 | 0.317 | 0.315 | 0.312 | 0.31 | 0.307 | 0.305 | 0.304 | 0.304 | 0.304 | 0.303 | 0.301 | 0.302 | 0.301 | 0.303 | 0.298 | 0.293 | 0.284 | 0.277 | 0.274 | 0.271 | 0.27 | 0.268 | 0.27 | 0.274 | 0.279 | 0.283 | 0.287 | 0.292 | 0.295 | 0.3 | 0.306 | 0.312 | 0.319 | 0.323 | 0.329 | 0.333 | 0.339 | 0.341 | 0.344 | 0.348 | 0.351 | 0.355 | 0.357 | 0.361 | 0.36 | 0.361 | 0.361 | 0.362 | 0.362 | 0.362 | 0.36 | 0.36 | 0.359 | 0.359 | 0.358 | 0.358 | 0.358 | 0.357 | 0.356 | 0.355 | 0.353 | 0.353 | 0.352 | 0.35 | 0.348 | 0.345 | 0.341 | 0.34 | 0.341 | 0.341 | 0.338 | 0.336 | 0.335 | 0.334 | 0.333 | 0.332 | 0.331 | 0.33 | 0.329 | 0.328 | 0.328 | 0.329 | 0.334 | 0.339 | 0.343 | 0.343 | 0.342 | 0.339 | 0.335 | 0.327 | 0.319 | 0.341 | 0.337 | 0.333 | 0.334 | 0.335 | 0.334 | 0.332 | 0.33 | 0.33 | 0.328 | 0.327 | 0.326 | 0.327 | 0.326 | 0.327 | 0.326 | 0.328 | 0.328 | 0.329 | 0.329 | 0.33 | 0.328 | 0.327 | 0.33 | 0.337 | 0.347 | 0.362 | 0.39 | 0.426 | 0.472 | 0.519 | 0.575 | 0.627 | 0.673 | 0.707 | 0.732 | 0.752 | 0.764 | 0.773 | 0.78 | 0.788 | 0.798 | 0.807 | 0.812 | 0.816 | 0.82 | 0.823 | 0.82 | 0.814 | 0.802 | 0.792 | 0.789 | 0.798 | 0.809 | 0.817 | 0.818 | 0.817 | 0.813 | 0.809 | 0.801 | 0.795 | 0.789 | 0.784 | 0.774 | 0.757 | 0.732 | 0.704 | 0.665 | 0.627 | 0.586 | 0.556 | 0.524 | 0.497 | 0.474 | 0.461 | 0.45 | 0.442 | 0.435 | 0.43 | 0.423 | 0.417 | 0.41 | 0.404 | 0.4 | 0.396 | 0.394 | 0.394 | 0.396 | 0.395 | 0.391 | 0.386 | 0.379 | 0.373 | 0.367 | 0.359 | 0.353 | 0.342 | 0.337 | 0.331 | 0.332 | 0.331 | 0.33 | 0.328 | 0.325 | 0.323 | 0.321 | 0.32 | 0.318 | 0.317 | 0.315 | 0.314 | 0.313 | 0.313 | 0.313 | 0.313 | 0.312 | 0.31 | 0.306 | 0.302 | 0.298 | 0.297 | 0.295 | 0.294 | 0.298 | 0.305 | 0.314 | 0.325 | 0.339 | 0.353 | 0.367 | 0.378 | 0.391 | 0.404 | 0.417 | 0.426 | 0.435 | 0.441 | 0.446 | 0.447 | 0.449 | 0.451 | 0.453 | 0.455 | 0.456 | 0.453 | 0.449 | 0.446 | 0.445 | 0.444 | 0.442 | 0.441 | 0.439 | 0.438 | 0.435 | 0.433 | 0.432 | 0.43 | 0.428 | 0.427 | 0.424 | 0.422 | 0.42 | 0.417 | 0.411 | 0.402 | 0.393 | 0.384 | 0.376 | 0.37 | 0.367 | 0.364 | 0.362 | 0.359 | 0.358 | 0.356 | 0.355 | 0.354 | 0.352 | 0.35 | 0.348 | 0.349 | 0.352 | 0.356 | 0.36 | 0.364 | 0.367 | 0.369 | 0.367 | 0.364 | 0.359 | 0.355 | 0.35 | 0.344 | 0.34 | 0.337 | 0.338 | 0.339 | 0.339 | 0.337 | 0.335 | 0.333 | 0.332 | 0.331 | 0.33 | 0.33 | 0.329 | 0.327 | 0.323 | 0.322 | 0.319 | 0.319 | 0.317 | 0.314 | 0.309 | 0.303 | 0.298 | 0.294 | 0.289 | 0.287 | 0.286 | 0.289 | 0.293 | 0.296 | 0.301 | 0.308 | 0.315 | 0.32 | 0.325 | 0.328 | 0.332 | 0.336 | 0.342 | 0.347 | 0.353 | 0.355 | 0.36 | 0.363 | 0.365 | 0.366 | 0.368 | 0.37 | 0.372 | 0.372 | 0.372 | 0.37 | 0.369 | 0.368 | 0.366 | 0.366 | 0.364 | 0.363 | 0.361 | 0.361 | 0.361 | 0.362 | 0.361 | 0.362 | 0.36 | 0.361 | 0.359 | 0.357 | 0.352 | 0.349 | 0.347 | 0.346 | 0.346 | 0.346 | 0.346 | 0.344 | 0.344 | 0.345 | 0.343 | 0.342 | 0.339 | 0.338 | 0.337 | 0.336 | 0.337 | 0.341 | 0.346 | 0.351 | 0.353 | 0.352 | 0.352 | 0.347 | 0.345 | 0.339 | 0.334 | 0.336 | 0.332 | 0.328 | 0.33 | 0.33 | 0.33 | 0.327 | 0.325 | 0.324 | 0.323 | 0.322 | 0.32 | 0.321 | 0.32 | 0.321 | 0.319 | 0.321 | 0.321 | 0.322 | 0.323 | 0.326 | 0.33 | 0.334 | 0.34 | 0.346 | 0.352 | 0.362 | 0.384 | 0.415 | 0.457 | 0.501 | 0.554 | 0.604 | 0.649 | 0.683 | 0.709 | 0.727 | 0.741 | 0.749 | 0.756 | 0.763 | 0.772 | 0.78 | 0.786 | 0.79 | 0.794 | 0.796 | 0.794 | 0.788 | 0.777 | 0.767 | 0.765 | 0.774 | 0.786 | 0.793 | 0.795 | 0.795 | 0.792 | 0.788 | 0.781 | 0.775 | 0.771 | 0.767 | 0.758 | 0.741 | 0.715 | 0.685 | 0.646 | 0.607 | 0.568 | 0.537 | 0.506 | 0.48 | 0.459 | 0.446 | 0.437 | 0.431 | 0.426 | 0.422 | 0.418 | 0.416 | 0.418 | 0.425 | 0.433 | 0.44 | 0.44 | 0.436 | 0.427 | 0.415 | 0.402 | 0.39 | 0.38 | 0.371 | 0.364 | 0.355 | 0.348 | 0.34 | 0.334 | 0.328 | 0.329 | 0.328 | 0.327 | 0.325 | 0.324 | 0.322 | 0.319 | 0.317 | 0.315 | 0.314 | 0.313 | 0.314 | 0.312 | 0.312 | 0.311 | 0.312 | 0.312 | 0.313 | 0.315 | 0.316 | 0.315 | 0.312 | 0.307 | 0.303 | 0.302 | 0.305 | 0.311 | 0.32 | 0.331 | 0.344 | 0.357 | 0.368 | 0.381 | 0.393 | 0.407 | 0.416 | 0.423 | 0.43 | 0.436 | 0.44 | 0.44 | 0.442 | 0.444 | 0.447 | 0.447 | 0.443 | 0.439 | 0.436 | 0.433 | 0.431 | 0.43 | 0.43 | 0.429 | 0.427 | 0.425 | 0.424 | 0.422 | 0.42 | 0.417 | 0.417 | 0.414 | 0.411 | 0.407 | 0.404 | 0.398 | 0.391 | 0.381 | 0.375 | 0.37 | 0.367 | 0.364 | 0.361 | 0.359 | 0.357 | 0.356 | 0.356 | 0.355 | 0.356 | 0.356 | 0.359 | 0.363 | 0.369 | 0.373 | 0.374 | 0.374 | 0.372 | 0.369 | 0.364 | 0.359 | 0.356 | 0.351 | 0.344 | 0.338 | 0.33 | 0.326 | 0.321 | 0.323 | 0.323 | 0.322 | 0.319 | 0.317 | 0.315 | 0.314 | 0.313 | 0.311 | 0.311 | 0.31 | 0.309 | 0.306 | 0.306 | 0.306 | 0.307 | 0.306 | 0.307 | 0.308 | 0.308 | 0.305 | 0.301 | 0.294 | 0.288 | 0.285 | 0.285 | 0.286 | 0.287 | 0.291 | 0.296 | 0.301 | 0.305 | 0.309 | 0.314 | 0.319 | 0.323 | 0.328 | 0.332 | 0.336 | 0.34 | 0.343 | 0.345 | 0.347 | 0.349 | 0.352 | 0.355 | 0.357 | 0.358 | 0.357 | 0.357 | 0.357 | 0.357 | 0.356 | 0.354 | 0.354 | 0.354 | 0.353 | 0.353 | 0.352 | 0.352 | 0.352 | 0.353 | 0.354 | 0.354 | 0.352 | 0.352 | 0.349 | 0.347 | 0.343 | 0.34 | 0.342 | 0.343 | 0.345 | 0.344 | 0.343 | 0.342 | 0.341 | 0.342 | 0.344 | 0.349 | 0.355 | 0.362 | 0.366 | 0.368 | 0.365 | 0.363 | 0.359 | 0.355 | 0.349 | 0.344 | 0.34 | 0.335 | 0.334 | 0.33 | 0.326 | 0.321 | 0.324 | 0.324 | 0.324 | 0.321 | 0.32 | 0.319 | 0.317 | 0.316 | 0.315 | 0.316 | 0.316 | 0.317 | 0.316 | 0.317 | 0.318 | 0.32 | 0.322 | 0.326 | 0.331 | 0.338 | 0.349 | 0.363 | 0.38 | 0.402 | 0.434 | 0.472 | 0.519 | 0.569 | 0.627 | 0.681 | 0.729 | 0.764 | 0.791 | 0.808 | 0.818 | 0.824 | 0.829 | 0.836 | 0.845 | 0.853 | 0.858 | 0.863 | 0.865 | 0.867 | 0.863 | 0.854 | 0.837 | 0.823 | 0.821 | 0.832 | 0.846 | 0.855 | 0.857 | 0.856 | 0.851 | 0.845 | 0.835 | 0.828 | 0.822 | 0.816 | 0.803 | 0.782 | 0.75 | 0.716 | 0.672 | 0.63 | 0.587 | 0.555 | 0.524 | 0.498 | 0.478 | 0.467 | 0.462 | 0.463 | 0.469 | 0.482 | 0.495 | 0.505 | 0.51 | 0.51 | 0.504 | 0.494 | 0.479 | 0.464 | 0.445 | 0.427 | 0.409 | 0.394 | 0.38 | 0.37 | 0.36 | 0.351 | 0.343 | 0.336 | 0.331 | 0.325 | 0.327 | 0.326 | 0.325 | 0.322 | 0.319 | 0.317 | 0.316 | 0.314 | 0.313 | 0.312 | 0.311 | 0.31 | 0.308 | 0.308 | 0.307 | 0.309 | 0.309 | 0.311 | 0.312 | 0.313 | 0.315 | 0.317 | 0.32 | 0.323 | 0.328 | 0.33 | 0.333 | 0.338 | 0.35 | 0.365 | 0.379 | 0.393 | 0.406 | 0.42 | 0.432 | 0.442 | 0.45 | 0.457 | 0.462 | 0.465 | 0.468 | 0.471 | 0.474 | 0.475 | 0.475 | 0.471 | 0.465 | 0.461 | 0.457 | 0.455 | 0.453 | 0.453 | 0.451 | 0.449 | 0.446 | 0.444 | 0.44 | 0.437 | 0.434 | 0.434 | 0.431 | 0.427 | 0.422 | 0.419 | 0.413 | 0.404 | 0.394 | 0.386 | 0.379 | 0.374 | 0.37 | 0.368 | 0.366 | 0.367 | 0.367 | 0.372 | 0.378 | 0.386 | 0.391 | 0.394 | 0.393 | 0.392 | 0.388 | 0.384 | 0.38 | 0.377 | 0.372 | 0.367 | 0.361 | 0.356 | 0.351 | 0.345 | 0.34 | 0.332 | 0.329 | 0.326 | 0.329 | 0.328 | 0.327 | 0.323 | 0.321 | 0.319 | 0.32 | 0.318 | 0.318 | 0.317 | 0.319 | 0.318 | 0.315 | 0.314 | 0.313 | 0.315 | 0.315 | 0.317 | 0.317 | 0.317 | 0.317 | 0.316 | 0.317 | 0.315 | 0.314 | 0.311 | 0.307 | 0.303 | 0.301 | 0.301 | 0.305 | 0.309 | 0.314 | 0.319 | 0.325 | 0.33 | 0.335 | 0.339 | 0.342 | 0.346 | 0.349 | 0.352 | 0.353 | 0.355 | 0.358 | 0.36 | 0.361 | 0.362 | 0.362 | 0.363 | 0.363 | 0.363 | 0.362 | 0.362 | 0.362 | 0.36 | 0.359 | 0.356 | 0.355 | 0.353 | 0.353 | 0.353 | 0.353 | 0.351 | 0.351 | 0.349 | 0.348 | 0.345 | 0.343 | 0.341 | 0.342 | 0.342 | 0.342 | 0.341 | 0.343 | 0.348 | 0.354 | 0.36 | 0.367 | 0.371 | 0.371 | 0.369 | 0.365 | 0.362 | 0.357 | 0.35 | 0.345 | 0.34 | 0.335 | 0.331 | 0.326 | 0.321 | 0.317 | 0.338 | 0.334 | 0.332 | 0.334 | 0.333 | 0.333 | 0.331 | 0.33 | 0.329 | 0.328 | 0.327 | 0.327 | 0.327 | 0.328 | 0.328 | 0.327 | 0.328 | 0.329 | 0.331 | 0.333 | 0.338 | 0.343 | 0.351 | 0.362 | 0.377 | 0.397 | 0.422 | 0.461 | 0.507 | 0.564 | 0.619 | 0.678 | 0.73 | 0.775 | 0.807 | 0.831 | 0.846 | 0.853 | 0.858 | 0.86 | 0.866 | 0.874 | 0.882 | 0.887 | 0.89 | 0.891 | 0.892 | 0.887 | 0.876 | 0.858 | 0.842 | 0.839 | 0.849 | 0.864 | 0.873 | 0.874 | 0.873 | 0.868 | 0.863 | 0.852 | 0.844 | 0.837 | 0.832 | 0.818 | 0.796 | 0.765 | 0.73 | 0.688 | 0.646 | 0.606 | 0.576 | 0.549 | 0.53 | 0.52 | 0.523 | 0.533 | 0.544 | 0.552 | 0.553 | 0.548 | 0.54 | 0.533 | 0.525 | 0.514 | 0.5 | 0.484 | 0.468 | 0.45 | 0.432 | 0.414 | 0.399 | 0.386 | 0.376 | 0.368 | 0.359 | 0.351 | 0.346 | 0.341 | 0.335 | 0.336 | 0.334 | 0.334 | 0.331 | 0.328 | 0.325 | 0.324 | 0.322 | 0.322 | 0.322 | 0.322 | 0.32 | 0.319 | 0.321 | 0.321 | 0.323 | 0.323 | 0.325 | 0.326 | 0.327 | 0.33 | 0.333 | 0.338 | 0.345 | 0.355 | 0.365 | 0.374 | 0.381 | 0.39 | 0.399 | 0.408 | 0.416 | 0.426 | 0.439 | 0.449 | 0.458 | 0.467 | 0.475 | 0.481 | 0.484 | 0.486 | 0.487 | 0.488 | 0.487 | 0.485 | 0.481 | 0.475 | 0.47 | 0.466 | 0.464 | 0.463 | 0.462 | 0.461 | 0.46 | 0.458 | 0.455 | 0.453 | 0.449 | 0.448 | 0.446 | 0.444 | 0.44 | 0.436 | 0.432 | 0.426 | 0.419 | 0.41 | 0.404 | 0.397 | 0.395 | 0.394 | 0.398 | 0.405 | 0.411 | 0.415 | 0.416 | 0.414 | 0.41 | 0.406 | 0.403 | 0.399 | 0.396 | 0.392 | 0.389 | 0.386 | 0.383 | 0.379 | 0.374 | 0.371 | 0.366 | 0.361 | 0.354 | 0.348 | 0.341 | 0.338 | 0.334 | 0.337 | 0.335 | 0.335 | 0.331 | 0.331 | 0.33 | 0.33 | 0.328 | 0.326 | 0.325 | 0.323 | 0.321 | 0.319 | 0.319 | 0.318 | 0.319 | 0.319 | 0.32 | 0.321 | 0.322 | 0.321 | 0.321 | 0.323 | 0.324 | 0.327 | 0.328 | 0.328 | 0.325 | 0.322 | 0.321 | 0.321 | 0.323 | 0.325 | 0.331 | 0.335 | 0.34 | 0.344 | 0.349 | 0.351 | 0.354 | 0.357 | 0.361 | 0.361 | 0.363 | 0.366 | 0.368 | 0.369 | 0.368 | 0.369 | 0.371 | 0.372 | 0.372 | 0.37 | 0.37 | 0.369 | 0.37 | 0.368 | 0.368 | 0.367 | 0.366 | 0.366 | 0.367 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.368 | 0.367 | 0.368 | 0.37 | 0.374 | 0.379 | 0.384 | 0.387 | 0.39 | 0.389 | 0.388 | 0.387 | 0.385 | 0.383 | 0.38 | 0.376 | 0.372 | 0.367 | 0.363 | 0.359 | 0.355 | 0.35 | 0.346 | 0.343 | 0.337 | 0.331 | 0.35 | 0.347 | 0.345 | 0.348 | 0.348 | 0.347 | 0.346 | 0.345 | 0.344 | 0.342 | 0.34 | 0.34 | 0.341 | 0.341 | 0.342 | 0.342 | 0.345 | 0.346 | 0.349 | 0.351 | 0.356 | 0.363 | 0.371 | 0.383 | 0.4 | 0.422 | 0.448 | 0.488 | 0.536 | 0.595 | 0.652 | 0.712 | 0.767 | 0.814 | 0.849 | 0.875 | 0.891 | 0.899 | 0.903 | 0.905 | 0.912 | 0.919 | 0.927 | 0.932 | 0.934 | 0.935 | 0.935 | 0.929 | 0.918 | 0.9 | 0.884 | 0.881 | 0.891 | 0.906 | 0.916 | 0.918 | 0.917 | 0.912 | 0.906 | 0.895 | 0.887 | 0.881 | 0.876 | 0.865 | 0.847 | 0.821 | 0.798 | 0.769 | 0.742 | 0.711 | 0.686 | 0.659 | 0.636 | 0.616 | 0.604 | 0.595 | 0.589 | 0.582 | 0.575 | 0.567 | 0.557 | 0.547 | 0.536 | 0.524 | 0.511 | 0.495 | 0.479 | 0.461 | 0.443 | 0.425 | 0.41 | 0.398 | 0.39 | 0.383 | 0.373 | 0.363 | 0.361 | 0.358 | 0.355 | 0.357 | 0.356 | 0.354 | 0.351 | 0.349 | 0.348 | 0.345 | 0.344 | 0.344 | 0.344 | 0.344 | 0.343 | 0.343 | 0.344 | 0.344 | 0.345 | 0.345 | 0.347 | 0.35 | 0.352 | 0.356 | 0.359 | 0.363 | 0.369 | 0.378 | 0.388 | 0.399 | 0.407 | 0.416 | 0.426 | 0.434 | 0.445 | 0.457 | 0.469 | 0.479 | 0.487 | 0.495 | 0.503 | 0.508 | 0.514 | 0.518 | 0.52 | 0.52 | 0.519 | 0.517 | 0.514 | 0.509 | 0.505 | 0.501 | 0.499 | 0.496 | 0.495 | 0.494 | 0.493 | 0.489 | 0.486 | 0.482 | 0.481 | 0.48 | 0.481 | 0.482 | 0.485 | 0.488 | 0.496 | 0.501 | 0.502 | 0.495 | 0.487 | 0.476 | 0.467 | 0.459 | 0.456 | 0.451 | 0.447 | 0.443 | 0.439 | 0.435 | 0.43 | 0.426 | 0.424 | 0.421 | 0.417 | 0.413 | 0.409 | 0.405 | 0.401 | 0.396 | 0.391 | 0.385 | 0.381 | 0.378 | 0.371 | 0.364 | 0.357 | 0.355 | 0.355 | 0.357 | 0.357 | 0.355 | 0.352 | 0.35 | 0.348 | 0.347 | 0.344 | 0.343 | 0.342 | 0.341 | 0.339 | 0.336 | 0.337 | 0.335 | 0.337 | 0.336 | 0.338 | 0.339 | 0.338 | 0.339 | 0.34 | 0.34 | 0.342 | 0.346 | 0.349 | 0.351 | 0.349 | 0.347 | 0.345 | 0.344 | 0.344 | 0.348 | 0.352 | 0.355 | 0.358 | 0.361 | 0.366 | 0.369 | 0.373 | 0.376 | 0.379 | 0.381 | 0.384 | 0.387 | 0.39 | 0.392 | 0.392 | 0.392 | 0.394 | 0.395 | 0.395 | 0.395 | 0.396 | 0.396 | 0.397 | 0.397 | 0.398 | 0.397 | 0.398 | 0.399 | 0.402 | 0.405 | 0.413 | 0.422 | 0.43 | 0.434 | 0.434 | 0.431 | 0.427 | 0.424 | 0.422 | 0.419 | 0.418 | 0.415 | 0.412 | 0.41 | 0.408 | 0.406 | 0.403 | 0.4 | 0.396 | 0.394 | 0.39 | 0.386 | 0.381 | 0.375 | 0.371 | 0.365 | 0.361 | 0.357 | 0.351 | 0.344 | 0.388 | 0.385 | 0.383 | 0.385 | 0.386 | 0.386 | 0.383 | 0.381 | 0.381 | 0.379 | 0.38 | 0.379 | 0.38 | 0.379 | 0.38 | 0.379 | 0.382 | 0.383 | 0.385 | 0.387 | 0.39 | 0.397 | 0.404 | 0.415 | 0.43 | 0.45 | 0.473 | 0.507 | 0.548 | 0.599 | 0.652 | 0.713 | 0.767 | 0.811 | 0.84 | 0.86 | 0.874 | 0.88 | 0.885 | 0.886 | 0.892 | 0.898 | 0.904 | 0.908 | 0.909 | 0.91 | 0.909 | 0.904 | 0.896 | 0.881 | 0.868 | 0.863 | 0.871 | 0.88 | 0.886 | 0.885 | 0.884 | 0.88 | 0.875 | 0.865 | 0.857 | 0.851 | 0.846 | 0.837 | 0.824 | 0.806 | 0.789 | 0.764 | 0.735 | 0.7 | 0.671 | 0.643 | 0.621 | 0.602 | 0.59 | 0.579 | 0.571 | 0.563 | 0.557 | 0.549 | 0.541 | 0.531 | 0.523 | 0.514 | 0.504 | 0.491 | 0.48 | 0.466 | 0.455 | 0.444 | 0.436 | 0.43 | 0.424 | 0.418 | 0.409 | 0.398 | 0.391 | 0.386 | 0.384 | 0.385 | 0.384 | 0.383 | 0.38 | 0.377 | 0.375 | 0.373 | 0.372 | 0.372 | 0.373 | 0.371 | 0.371 | 0.369 | 0.373 | 0.374 | 0.376 | 0.376 | 0.378 | 0.38 | 0.384 | 0.387 | 0.393 | 0.398 | 0.405 | 0.415 | 0.425 | 0.438 | 0.451 | 0.47 | 0.486 | 0.498 | 0.505 | 0.512 | 0.522 | 0.532 | 0.54 | 0.545 | 0.551 | 0.556 | 0.561 | 0.563 | 0.566 | 0.566 | 0.565 | 0.561 | 0.556 | 0.55 | 0.544 | 0.539 | 0.536 | 0.533 | 0.532 | 0.529 | 0.527 | 0.524 | 0.52 | 0.515 | 0.511 | 0.509 | 0.508 | 0.506 | 0.505 | 0.506 | 0.511 | 0.515 | 0.511 | 0.502 | 0.491 | 0.481 | 0.474 | 0.468 | 0.464 | 0.459 | 0.455 | 0.452 | 0.45 | 0.447 | 0.444 | 0.44 | 0.438 | 0.434 | 0.432 | 0.428 | 0.424 | 0.42 | 0.416 | 0.412 | 0.408 | 0.404 | 0.402 | 0.399 | 0.392 | 0.392 | 0.386 | 0.383 | 0.382 | 0.382 | 0.382 | 0.381 | 0.378 | 0.377 | 0.375 | 0.373 | 0.371 | 0.371 | 0.37 | 0.369 | 0.368 | 0.368 | 0.37 | 0.371 | 0.372 | 0.372 | 0.371 | 0.372 | 0.372 | 0.373 | 0.374 | 0.375 | 0.378 | 0.381 | 0.384 | 0.386 | 0.386 | 0.39 | 0.391 | 0.39 | 0.386 | 0.384 | 0.385 | 0.386 | 0.39 | 0.393 | 0.397 | 0.401 | 0.405 | 0.408 | 0.411 | 0.414 | 0.416 | 0.421 | 0.423 | 0.424 | 0.424 | 0.423 | 0.424 | 0.425 | 0.426 | 0.426 | 0.426 | 0.425 | 0.425 | 0.425 | 0.425 | 0.425 | 0.426 | 0.428 | 0.433 | 0.44 | 0.451 | 0.461 | 0.464 | 0.463 | 0.458 | 0.455 | 0.454 | 0.452 | 0.452 | 0.448 | 0.447 | 0.443 | 0.443 | 0.44 | 0.438 | 0.435 | 0.432 | 0.429 | 0.427 | 0.425 | 0.421 | 0.416 | 0.41 | 0.405 | 0.402 | 0.399 | 0.396 | 0.393 | 0.384 | 0.377
E4A | -3456 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.941 | 0.589 | 0.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011 | 0.205 | 0.536 | 0.83 | 0.987 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.915 | 0.513 | 0.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.128 | 0.46 | 0.768 | 0.979 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.912 | 0.576 | 0.103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025 | 0.247 | 0.539 | 0.787 | 0.972 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.991 | 0.859 | 0.603 | 0.321 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.133 | 0.406 | 0.693 | 0.937 | 0.999 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.989 | 0.805 | 0.545 | 0.263 | 0.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081 | 0.346 | 0.636 | 0.91 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.976 | 0.769 | 0.509 | 0.229 | 0.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.059 | 0.31 | 0.598 | 0.882 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.995 | 0.879 | 0.679 | 0.473 | 0.18 | 0.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041 | 0.245 | 0.51 | 0.752 | 0.826 | 0.826 | 0.826 | 0.851 | 0.971 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.964 | 0.754 | 0.524 | 0.29 | 0.063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019 | 0.226 | 0.527 | 0.832 | 0.995 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.954 | 0.738 | 0.504 | 0.231 | 0.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.192 | 0.494 | 0.721 | 0.75 | 0.75 | 0.75 | 0.827 | 0.988 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.988 | 0.837 | 0.61 | 0.38 | 0.135 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0.094 | 0.383 | 0.676 | 0.926 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.956 | 0.762 | 0.558 | 0.363 | 0.174 | 0.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0.124 | 0.37 | 0.616 | 0.864 | 0.996 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.909 | 0.662 | 0.418 | 0.182 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.123 | 0.427 | 0.737 | 0.969 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.97 | 0.733 | 0.386 | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.032 | 0.266 | 0.606 | 0.897 | 0.997 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.963 | 0.645 | 0.276 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0.166 | 0.501 | 0.858 | 0.999 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.962 | 0.687 | 0.394 | 0.152 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.063 | 0.299 | 0.574 | 0.865 | 0.998 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.984 | 0.411 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041 | 0.504 | 0.979 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.983 | 0.396 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.041 | 0.527 | 0.981 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.983 | 0.388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031 | 0.505 | 0.98 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.92 | 0.53 | 0.156 | 0.003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.038 | 0.313 | 0.784 | 0.997 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.9 | 0.532 | 0.206 | 0.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.073 | 0.35 | 0.77 | 0.995 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.914 | 0.562 | 0.234 | 0.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.094 | 0.379 | 0.789 | 0.996 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.991 | 0.822 | 0.537 | 0.252 | 0.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061 | 0.247 | 0.467 | 0.704 | 0.932 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.892 | 0.57 | 0.246 | 0.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034 | 0.241 | 0.495 | 0.765 | 0.975 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.917 | 0.607 | 0.279 | 0.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.054 | 0.277 | 0.53 | 0.8 | 0.986 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.927 | 0.669 | 0.372 | 0.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029 | 0.199 | 0.406 | 0.614 | 0.823 | 0.973 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.904 | 0.589 | 0.265 | 0.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.082 | 0.305 | 0.533 | 0.764 | 0.965 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.927 | 0.628 | 0.298 | 0.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.113 | 0.341 | 0.569 | 0.8 | 0.981 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.998 | 0.946 | 0.731 | 0.438 | 0.153 | 0.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.031 | 0.048 | 0.048 | 0.048 | 0.09 | 0.297 | 0.537 | 0.766 | 0.959 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.937 | 0.701 | 0.45 | 0.21 | 0.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.087 | 0.295 | 0.497 | 0.69 | 0.878 | 0.996 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.981 | 0.788 | 0.532 | 0.28 | 0.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0.108 | 0.2 | 0.2 | 0.2 | 0.204 | 0.325 | 0.526 | 0.718 | 0.905 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.999 | 0.901 | 0.646 | 0.368 | 0.097 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.088 | 0.436 | 0.766 | 0.969 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.938 | 0.671 | 0.36 | 0.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074 | 0.439 | 0.798 | 0.989 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.957 | 0.706 | 0.399 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.473 | 0.831 | 0.996 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.965 | 0.65 | 0.113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.022 | 0.556 | 0.99 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.965 | 0.669 | 0.132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018 | 0.514 | 0.979 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.958 | 0.521 | 0.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.631 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Privaat, 17:00 thuis | -288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Privaat, 18:00 thuis | -288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Privaat, 19:00 thuis | -288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Privaat, 17:00 thuis+zat | -288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Privaat, 18:00 thuis+zat | -288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Privaat, 19:00 thuis+zat | -288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Privaat, 17:00 thuis+zon | -288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Privaat, 18:00 thuis+zon | -288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Privaat, 19:00 thuis+zon | -288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Publiek 1 | -288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.9 | 0.5 | 0.25 | 0.15 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Publiek 2 | -288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 1.8 | 1 | 0.5 | 0.3 | 0.2 | 0 | 0 | 2 | 2 | 2 | 2 | 1.8 | 1 | 0.5 | 0.3 | 0.2 | 0 | 0 | 2 | 2 | 2 | 2 | 1.8 | 1 | 0.5 | 0.3 | 0.2 | 0 | 0 | 2 | 2 | 2 | 2 | 1.8 | 1 | 0.5 | 0.3 | 0.2 | 0 | 0 | 2 | 2 | 2 | 2 | 1.8 | 1 | 0.5 | 0.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 1.8 | 1 | 0.5 | 0.3 | 0.2 | 0 | 0 | 2 | 2 | 2 | 2 | 1.8 | 1 | 0.5 | 0.3 | 0.2 | 0 | 0 | 2 | 2 | 2 | 2 | 1.8 | 1 | 0.5 | 0.3 | 0.2 | 0 | 0 | 2 | 2 | 2 | 2 | 1.8 | 1 | 0.5 | 0.3 | 0.2 | 0 | 0 | 2 | 2 | 2 | 2 | 1.8 | 1 | 0.5 | 0.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 1.8 | 1 | 0.5 | 0.3 | 0.2 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 1.8 | 1 | 0.5 | 0.3 | 0.2 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 1.8 | 1 | 0.5 | 0.3 | 0.2 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 1.8 | 1 | 0.5 | 0.3 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Windstil h=100m v=30m/s | -168 | 0.007 | 0.007 | 0.007 | 0.005 | 0.007 | 0.007 | 0.009 | 0.009 | 0.007 | 0.009 | 0.005 | 0.002 | 0.002 | 0.002 | 0.002 | 0.005 | 0.005 | 0.005 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0 | 0 | 0 | 0.002 | 0.005 | 0.005 | 0.005 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0 | 0 | 0.002 | 0.002 | 0 | 0 | 0 | 0 | 0 | 0.002 | 0 | 0 | 0 | 0.002 | 0.002 | 0.005 | 0.005 | 0.007 | 0.005 | 0.005 | 0.002 | 0.002 | 0.002 | 0.002 | 0.005 | 0.002 | 0.005 | 0.005 | 0.002 | 0.002 | 0.005 | 0.002 | 0.002 | 0.002 | 0.002 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.007 | 0.007 | 0.005 | 0.005 | 0.002 | 0.005 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0 | 0.002 | 0.005 | 0.005 | 0.005 | 0.007 | 0.005 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.005 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0.002 | 0 | 0.002 | 0.002 | 0.002 | 0.002 | 0.005 | 0.005 | 0.002 | 0.005 | 0.005 | 0.007 | 0.007 | 0.007 | 0.007 | 0.007 | 0.005 | 0.005 | 0.002 | 0.002 | 0.005 | 0.002 | 0.002 | 0.002 | 0.002 | 0.005 | 0.005 | 0.005 | 0.002 | 0.005 | 0.005 | 0.007 | 0.009 | 0.007 | 0.007 | 0.007 | 0.009 | 0.007 | 0.009 | 0.009 | 0.005 | 0.002 | 0.002 | 0.002 | 0.002 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.005 | 0.002 | 0.005
Veel wind h=100m v=30m/s | -168 | 0.63 | 0.7 | 0.77 | 0.77 | 0.7 | 0.7 | 0.63 | 0.63 | 0.56 | 0.56 | 0.56 | 0.49 | 0.42 | 0.49 | 0.35 | 0.42 | 0.49 | 0.63 | 0.63 | 0.56 | 0.63 | 0.7 | 0.63 | 0.56 | 0.63 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.77 | 0.7 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.42 | 0.42 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.42 | 0.42 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.49 | 0.56 | 0.49 | 0.56 | 0.49 | 0.42 | 0.42 | 0.49 | 0.49 | 0.35 | 0.35 | 0.42 | 0.49 | 0.42 | 0.42 | 0.42 | 0.42 | 0.49 | 0.56 | 0.56 | 0.56 | 0.56 | 0.63 | 0.56 | 0.56 | 0.56 | 0.56 | 0.63 | 0.7 | 0.63 | 0.63 | 0.63 | 0.56 | 0.63 | 0.56 | 0.63 | 0.56 | 0.56 | 0.63 | 0.56 | 0.56 | 0.63 | 0.63 | 0.63 | 0.56 | 0.56 | 0.49 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.42 | 0.49 | 0.42 | 0.35 | 0.35 | 0.35 | 0.35 | 0.42 | 0.35 | 0.49 | 0.42 | 0.49 | 0.63 | 0.42 | 0.42 | 0.42 | 0.35 | 0.49 | 0.49 | 0.42 | 0.35 | 0.35 | 0.28 | 0.28 | 0.28 | 0.35 | 0.28 | 0.35 | 0.42 | 0.42 | 0.49 | 0.56 | 0.56 | 0.56 | 0.56 | 0.63 | 0.63 | 0.63 | 0.56 | 0.7 | 0.77 | 0.7 | 0.49 | 0.35 | 0.35 | 0.35 | 0.49 | 0.49 | 0.63 | 0.56 | 0.56 | 0.56 | 0.49 | 0.49 | 0.63 | 0.63 | 0.56 | 0.49

## Harmonic
Name | I2 | I3 | I4 | I5 | I6 | I7 | I8 | I9 | I10 | I11 | I12 | I13 | I14 | I15 | I16 | I17 | I18 | I19 | I20 | I21 | I22 | I23 | I24 | I25 | I26 | I27 | I28 | I29 | I30 | I31 | I32 | I33 | I34 | I35 | I36 | I37 | I38 | I39 | I40 | I41 | I42 | I43 | I44 | I45 | I46 | I47 | I48 | I49 | I50 | I51 | I52 | I53 | I54 | I55 | I56 | I57 | I58 | I59 | I60 | I61 | I62 | I63 | I64 | I65 | I66 | I67 | I68 | I69 | I70 | I71 | I72 | I73 | I74 | I75 | I76 | I77 | I78 | I79 | I80 | I81 | I82 | I83 | I84 | I85 | I86 | I87 | I88 | I89 | I90 | I91 | I92 | I93 | I94 | I95 | I96 | I97 | I98 | I99 | I100 | Angle2 | Angle3 | Angle4 | Angle5 | Angle6 | Angle7 | Angle8 | Angle9 | Angle10 | Angle11 | Angle12 | Angle13 | Angle14 | Angle15 | Angle16 | Angle17 | Angle18 | Angle19 | Angle20 | Angle21 | Angle22 | Angle23 | Angle24 | Angle25 | Angle26 | Angle27 | Angle28 | Angle29 | Angle30 | Angle31 | Angle32 | Angle33 | Angle34 | Angle35 | Angle36 | Angle37 | Angle38 | Angle39 | Angle40 | Angle41 | Angle42 | Angle43 | Angle44 | Angle45 | Angle46 | Angle47 | Angle48 | Angle49 | Angle50 | Angle51 | Angle52 | Angle53 | Angle54 | Angle55 | Angle56 | Angle57 | Angle58 | Angle59 | Angle60 | Angle61 | Angle62 | Angle63 | Angle64 | Angle65 | Angle66 | Angle67 | Angle68 | Angle69 | Angle70 | Angle71 | Angle72 | Angle73 | Angle74 | Angle75 | Angle76 | Angle77 | Angle78 | Angle79 | Angle80 | Angle81 | Angle82 | Angle83 | Angle84 | Angle85 | Angle86 | Angle87 | Angle88 | Angle89 | Angle90 | Angle91 | Angle92 | Angle93 | Angle94 | Angle95 | Angle96 | Angle97 | Angle98 | Angle99 | Angle100
| % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | ° | °
Rectifier single phase |  | 33.33 |  | 20 |  | 14.29 |  | 11.11 |  | 9.09 |  | 7.69 |  | 6.67 |  | 5.88 |  | 5.26 |  | 4.76 |  | 4.35 |  | 4 |  | 3.7 |  | 3.45 |  | 3.23 |  | 3.03 |  | 2.86 |  | 2.7 |  | 2.56 |  | 2.44 |  | 2.33 |  | 2.22 |  | 2.13 |  | 2.04 |  | 1.96 |  | 1.9 |  | 1.82 |  | 1.75 |  | 1.7 |  | 1.64 |  | 1.59 |  | 1.55 |  | 1.49 |  | 1.45 |  | 1.42 |  | 1.37 |  | 1.33 |  | 1.31 |  | 1.26 |  | 1.23 |  | 1.21 |  | 1.17 |  | 1.15 |  | 1.13 |  | 1.09 |  | 1.08 |  | 1.06 |  | 1.03 |  | 1.01
Rectifier 6-pulse (diode) |  |  |  | 20 |  | 14.29 |  |  |  | 9.09 |  | 7.69 |  |  |  | 5.88 |  | 5.26 |  |  |  | 4.35 |  | 4 |  |  |  | 3.45 |  | 3.23 |  |  |  | 2.86 |  | 2.7 |  |  |  | 2.44 |  | 2.33 |  |  |  | 2.13 |  | 2.04 |  |  |  | 1.9 |  | 1.82 |  |  |  | 1.7 |  | 1.64 |  |  |  | 1.55 |  | 1.49 |  |  |  | 1.42 |  | 1.37 |  |  |  | 1.31 |  | 1.26 |  |  |  | 1.21 |  | 1.17 |  |  |  | 1.13 |  | 1.09 |  |  |  | 1.06 |  | 1.03 | [6 empty] | 180 |  | 180 | [9 empty] | 180 |  | 180 | [9 empty] | 180 |  | 180 | [9 empty] | 180 |  | 180 | [9 empty] | 180 |  | 180 | [9 empty] | 180 |  | 180 | [9 empty] | 180 |  | 180 | [9 empty] | 180 |  | 180
Rectifier 12-pulse (diode) | [9 empty] | 9.09 |  | 7.69 | [9 empty] | 4.35 |  | 4 | [9 empty] | 2.86 |  | 2.7 | [9 empty] | 2.13 |  | 2.04 | [9 empty] | 1.7 |  | 1.64 | [9 empty] | 1.42 |  | 1.37 | [9 empty] | 1.21 |  | 1.17 | [9 empty] | 1.06 |  | 1.03
Rectifier 18-pulse (diode) | [15 empty] | 5.88 |  | 5.26 | [15 empty] | 2.86 |  | 2.7 | [15 empty] | 1.9 |  | 1.82 | [15 empty] | 1.42 |  | 1.37 | [15 empty] | 1.13 |  | 1.09 | [24 empty] | 180 |  | 180 | [33 empty] | 180 |  | 180 | [33 empty] | 180 |  | 180
Rectifier 24-pulse (diode) | [21 empty] | 4.35 |  | 4 | [21 empty] | 2.13 |  | 2.04 | [21 empty] | 1.42 |  | 1.37 | [21 empty] | 1.06 |  | 1.03
Fluorescent magnetic |  | 15.8 |  | 8.6 |  | 2.9 |  | 2 |  | 1.4 |  | 0.8 |  | 0.4 |  | 0.2 |  | 0.5 |  | 0.4 |  | 0.2 |  |  |  | 0.1 | [7 empty] | 0.1 | [11 empty] | 0.1 | [54 empty] | 216 |  | 242 |  | 301 |  | 346 |  | 28 |  | 55 |  | 62 |  | 17 |  | 342 |  | 353 |  | 341 |  |  |  | 216 | [7 empty] | 28 | [11 empty] | 317
Fluorescent electronic |  | 7.3 |  | 8 |  | 3 |  | 0.2 |  | 1.4 |  | 1.1 |  | 0.9 |  | 0.4 |  | 0.3 |  | 0.7 |  | 0.3 |  | 0.4 |  | 0.2 |  | 0.2 |  | 0.3 |  | 0.6 |  | 0.4 |  | 0.3 |  | 0.2 |  | 0.5 |  | 0.4 |  | 0.6 |  | 0.3 |  | 0.3 | [52 empty] | 182 |  | 339 |  | 329 |  | 239 |  | 151 |  | 124 |  | 132 |  | 128 |  | 225 |  | 244 |  | 229 |  | 206 |  | 213 |  | 171 |  | 100 |  | 100 |  | 94 |  | 63 |  | 92 |  | 66 |  | 48 |  | 336 |  | 349 |  | 341
HPS 150 W inductive gear control |  | 20.7 |  | 12.6 |  | 18.2 |  | 4.6 |  | 4.7 |  | 3.8 |  | 11.3 |  | 4.3 |  | 3.9 |  | 2.1 |  | 2.2 |  | 1.9 |  | 0.2 |  | 0.5 |  | 0.7 |  | 0.7 |  | 0.5 |  | 0.5 |  | 0.1 |  | 0.1 |  | 0.2 |  | 0.1 |  | 0.1 |  | 0.1 | [54 empty] | 180
Transformer magnetizing current |  | 63.5 |  | 35.9 |  | 18.3 |  | 10.1 |  | 5.4 |  | 2.1 |  | 0.9 |  | 0.4 |  | 0.1 |  |  |  | 0.2 |  | 0.2 |  | 0.1 |  |  |  | 0.2 |  | 0.2 |  |  |  | 0.1 | [5 empty] | 0.3 |  |  |  | 0.4 |  | 0.2 | [52 empty] | 129 |  | 260 |  | 33 |  | 161 |  | 288 |  | 58 |  | 169 |  | 306 |  | 84 |  |  |  | 347 |  | 36 |  | 108 |  |  |  | 267 |  | 117 |  |  |  | 238 | [5 empty] | 228 |  |  |  | 286 |  | 189
Residential air conditioner |  | 8 |  | 6.8 |  | 0.5 |  | 0.6 |  | 0.3 | [5 empty] | 0.2 | [84 empty] | 179 |  | 173 |  | 326 |  | 289 |  | 50 | [5 empty] | 118
3rd harmonic |  | 33.3
5th harmonic |  |  |  | 20
PV inverter |  | 10 |  | 2 |  | 0.8 |  | 1 |  | 0.05 |  | 0.08 |  | 0.06 |  | 0.05 |  | 0.05 |  | 0.04 |  | 0.04 |  | 0.03 |  | 0.02 |  | 0.02 |  | 0.02 |  | 0.02 |  | 0.01 | [9 empty] | 0.01 |  | 0.02

## Harmonic norm
Name | THDmaxLV | THDmaxMV | THDmaxHV | UmaxLV2 | UmaxLV3 | UmaxLV4 | UmaxLV5 | UmaxLV6 | UmaxLV7 | UmaxLV8 | UmaxLV9 | UmaxLV10 | UmaxLV11 | UmaxLV12 | UmaxLV13 | UmaxLV14 | UmaxLV15 | UmaxLV16 | UmaxLV17 | UmaxLV18 | UmaxLV19 | UmaxLV20 | UmaxLV21 | UmaxLV22 | UmaxLV23 | UmaxLV24 | UmaxLV25 | UmaxLV26 | UmaxLV27 | UmaxLV28 | UmaxLV29 | UmaxLV30 | UmaxLV31 | UmaxLV32 | UmaxLV33 | UmaxLV34 | UmaxLV35 | UmaxLV36 | UmaxLV37 | UmaxLV38 | UmaxLV39 | UmaxLV40 | UmaxLV41 | UmaxLV42 | UmaxLV43 | UmaxLV44 | UmaxLV45 | UmaxLV46 | UmaxLV47 | UmaxLV48 | UmaxLV49 | UmaxLV50 | UmaxMV2 | UmaxMV3 | UmaxMV4 | UmaxMV5 | UmaxMV6 | UmaxMV7 | UmaxMV8 | UmaxMV9 | UmaxMV10 | UmaxMV11 | UmaxMV12 | UmaxMV13 | UmaxMV14 | UmaxMV15 | UmaxMV16 | UmaxMV17 | UmaxMV18 | UmaxMV19 | UmaxMV20 | UmaxMV21 | UmaxMV22 | UmaxMV23 | UmaxMV24 | UmaxMV25 | UmaxMV26 | UmaxMV27 | UmaxMV28 | UmaxMV29 | UmaxMV30 | UmaxMV31 | UmaxMV32 | UmaxMV33 | UmaxMV34 | UmaxMV35 | UmaxMV36 | UmaxMV37 | UmaxMV38 | UmaxMV39 | UmaxMV40 | UmaxMV41 | UmaxMV42 | UmaxMV43 | UmaxMV44 | UmaxMV45 | UmaxMV46 | UmaxMV47 | UmaxMV48 | UmaxMV49 | UmaxMV50 | UmaxHV2 | UmaxHV3 | UmaxHV4 | UmaxHV5 | UmaxHV6 | UmaxHV7 | UmaxHV8 | UmaxHV9 | UmaxHV10 | UmaxHV11 | UmaxHV12 | UmaxHV13 | UmaxHV14 | UmaxHV15 | UmaxHV16 | UmaxHV17 | UmaxHV18 | UmaxHV19 | UmaxHV20 | UmaxHV21 | UmaxHV22 | UmaxHV23 | UmaxHV24 | UmaxHV25 | UmaxHV26 | UmaxHV27 | UmaxHV28 | UmaxHV29 | UmaxHV30 | UmaxHV31 | UmaxHV32 | UmaxHV33 | UmaxHV34 | UmaxHV35 | UmaxHV36 | UmaxHV37 | UmaxHV38 | UmaxHV39 | UmaxHV40 | UmaxHV41 | UmaxHV42 | UmaxHV43 | UmaxHV44 | UmaxHV45 | UmaxHV46 | UmaxHV47 | UmaxHV48 | UmaxHV49 | UmaxHV50
| % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | % | %
IEC 61000-3-6 Compatibiliteit | 8 | 8 | 3 | 2 | 5 | 1 | 6 | 0.5 | 5 | 0.5 | 1.5 | 0.5 | 3.5 | 0.5 | 3 | 0.4 | 0.4 | 0.4 | 2 | 0.4 | 1.8 | 0.4 | 0.3 | 0.4 | 1.4 | 0.4 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 4 | 1 | 5 | 0.5 | 4 | 0.5 | 1.2 | 0.5 | 3 | 0.4 | 2.5 | 0.4 | 0.3 | 0.4 | 1.7 | 0.4 | 1.5 | 0.3 | 0.2 | 0.3 | 1.2 | 0.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IEC 61000-3-6 Planning | 8 | 6.5 | 3 | 1.8 | 4 | 1 | 5 | 0.5 | 4 | 0.5 | 1.2 | 0.5 | 3 | 0.4 | 2.5 | 0.4 | 0.3 | 0.4 | 1.7 | 0.4 | 1.5 | 0.3 | 0.2 | 0.3 | 1.2 | 0.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 4 | 1 | 5 | 0.5 | 4 | 0.5 | 1.2 | 0.5 | 3 | 0.4 | 2.5 | 0.4 | 0.3 | 0.4 | 1.7 | 0.4 | 1.5 | 0.3 | 0.2 | 0.3 | 1.2 | 0.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 2 | 0.8 | 2 | 0.4 | 2 | 0.4 | 1 | 0.4 | 1.5 | 0.3 | 1.5 | 0.3 | 0.3 | 0.3 | 1.2 | 0.3 | 1.1 | 0.3 | 0.2 | 0.2 | 0.9 | 0.2 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Netcode (2007-09) | 8 | 8 | 5 | 2 | 5 | 1 | 6 | 0.5 | 5 | 0.5 | 1.5 | 0.5 | 3.5 | 0.5 | 3 | 0.5 | 0.5 | 0.5 | 2 | 0.5 | 1.5 | 0.5 | 0.5 | 0.5 | 1.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 1 | 6 | 0.5 | 5 | 0.5 | 1.5 | 0.5 | 3.5 | 0.5 | 3 | 0.5 | 0.5 | 0.5 | 2 | 0.5 | 1.5 | 0.5 | 0.5 | 0.5 | 1.5 | 0.5 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LS-planning | 6.4 | 0 | 0 | 1.6 | 4 | 0.8 | 4.8 | 0.4 | 4 | 0.4 | 1.2 | 0.4 | 2.8 | 0.4 | 2.4 | 0.4 | 0.4 | 0.4 | 1.6 | 0.4 | 1.2 | 0.4 | 0.4 | 0.4 | 1.2 | 0.4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IEEE Std 519-2014 | 8 | 5 | 2.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5

## Efficiency
Name | Input1 | Output1 | Input2 | Output2 | Input3 | Output3 | Input4 | Output4 | Input5 | Output5
| pu | % | pu | % | pu | % | pu | % | pu | %
0,1 pu: 93 %; 1 pu: 97 % | 0.05 | 0 | 0.1 | 93 | 0.2 | 95 | 0.3 | 96 | 1 | 97
0,1..1 pu: 95 % | 0 | 10 | 0.1 | 95 | 1 | 95
100 % | 0 | 100 | 1 | 100

## Lineconductor
Name | Unom | Inom | R | Lint | d_ext | d_int
| kV | A | Ohm/km | mH/km | mm | mm
400 Ams | 110 | 828 | 0.0854 | 0.053 | 26.14 | 0
95CU | 1 | 420 | 0.19256 | 0.25 | 12.5 | 0
32AW | 1 | 100 | 2.7465 | 0.342 | 7.9 | 0
ACSR50/30Sural | 110 | 100 | 0.5643 | 0.05 | 11.7 | 0
ACSR240/40Sural | 110 | 100 | 0.1188 | 0.05 | 21.9 | 0
ACSR435/55Sural | 110 | 100 | 0.06656 | 0.05 | 28.8 | 0
ACSR450/40Sural | 110 | 100 | 0.06434 | 0.05 | 28.7 | 0
AACSR50/30Sural | 110 | 100 | 0.6547 | 0.05 | 11.7 | 0
BR50 | 1 | 100 | 33 | 0.05 | 9 | 0
Raven ACSR 6/1 50gr | 1 | 243 | 0.647 | 0.1912 | 10.1092 | 0
Phlox AAC 7 50gr | 1 | 100 | 0.385 | 0.05 | 11.79 | 0
AMKA 3x120+95 | 1 | 100 | 0.2834 | 0.05 | 12.7 | 0
120/20 Aldrey/Steel 115kV | 115 | 385 | 0.276 | 0.045 | 15.5 | 0
125/30 Aldrey/Steel 115kV | 115 | 400 | 0.262 | 0.045 | 16.1 | 0

## Cable alias
Alias | Name

## Trafo alias
Alias | Name

## Coil alias
Alias | Name

## Rail alias
Alias | Name

## Fuse alias
Alias | Name

## Cable geometry
Versie 1 | [16 empty] | nominal voltage (V) | cross-section (mm²) | diameter of conductor (mm) | internal diameter of hollow conductor (mm) | major diameter of oval conductor | minor diameter of oval conductor | Overrule Rdc (Ohm/km) | Overrule ks | Overruls kp | distance between isolation material between conductor and sheath (mm) | distance between conductor screen of a three-core cable with screen (mm) | conductive surface of sheath (mm²) | external diameter of sheath (mm) | external diameter over top of corrugated sheath (mm) | external diameter over valley of corrugated sheath (mm) | major diameter of sheath of an oval conductor (mm) | minor diameter of sheath of an oval conductor (mm) | thickness of sheath (mm) | thickness of bedding (mm) | internal diameter of arm (mm) | external diameter of arm (mm) | major diameter of arm of an oval conductor (pipe-type cable) (mm) | minor diameter of arm of an oval conductor (pipe-type cable) (mm) | diameter of steel wires (mm) | conductive surface of arm tape (mm²) | number of steel wires | internal diameter of pipe of a pipe-type cable (mm) | external diameter of pipe of a pipe-type cable (mm) | external diameter of the cable (mm) | diameter over the cores (mm) | Wire type
Name | Number of conductors | Shape | Type | Material | Isolation material | Conductor/isolation screen | Sheath material | Sheath/cable type | Bedding material | Arm material | Arm configuration | Arm type | Lay of wire tapes | Cable serving material | Oil duct | Pipe material | U_0 | A_cond | d_cond | d_int_cond | d_cond_ma | d_cond_mi | My_Rdc | My_ks | My_kp | t1 | delta_1 | A_she | D_she_ext | D_oc | D_ot | d_she_ma | d_she_mi | t_she | t_2 | D_arm_int | D_arm_ext | d_arm_ma | d_arm_mi | d_wire | A_tape | n_wireOrTape | D_pipe_int | D_pipe_ext | D_ext | Doga | Wiretype
YMeKrvas 6/10 kV 1x 50 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 50 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 1.455 | 25 | 21 | 0 | 0 | 0 | 0 | 0.39 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0
YMeKrvas 6/10 kV 1x 95 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 95 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 1.585 | 25 | 24.5 | 0 | 0 | 0 | 0 | 0.33 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0
YMeKrvas 6/10 kV 1x150 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 150 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 1.55 | 25 | 27 | 0 | 0 | 0 | 0 | 0.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0
YMeKrvas 6/10 kV 1x240 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 240 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 1.595 | 25 | 30.8 | 0 | 0 | 0 | 0 | 0.26 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0
YMeKrvas 6/10 kV 1x400 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 400 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 1.495 | 50 | 35.4 | 0 | 0 | 0 | 0 | 0.46 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0
YMeKrvas 6/10 kV 1x630 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 630 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 1.53 | 48 | 41.6 | 0 | 0 | 0 | 0 | 0.39 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0
YMeKrvas 6/10 kV 1x800 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 800 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 1.545 | 48 | 45.2 | 0 | 0 | 0 | 0 | 0.36 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0
YMeKrvas 8,7/15 kV 1x 50 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 8700 | 50 | 7.6 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 1.68 | 25 | 24 | 0 | 0 | 0 | 0 | 0.34 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0
YMeKrvas 8,7/15 kV 1x 95 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 8700 | 95 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 1.625 | 25 | 26.8 | 0 | 0 | 0 | 0 | 0.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0
YMeKrvas 8,7/15 kV 1x150 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 8700 | 150 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 1.59 | 25 | 29.3 | 0 | 0 | 0 | 0 | 0.27 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0
YMeKrvas 8,7/15 kV 1x240 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 8700 | 240 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 1.63 | 25 | 33.1 | 0 | 0 | 0 | 0 | 0.24 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0
YMeKrvas 8,7/15 kV 1x400 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 8700 | 400 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 1.535 | 50 | 37.7 | 0 | 0 | 0 | 0 | 0.43 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0
YMeKrvas 8,7/15 kV 1x630 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 8700 | 630 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 1.565 | 50 | 43.9 | 0 | 0 | 0 | 0 | 0.37 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0
YMeKrvas 8,7/15 kV 1x800 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 8700 | 800 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 1.6 | 44 | 47.5 | 0 | 0 | 0 | 0 | 0.3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0
YMeKrvas 12/20 kV 1x 95 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 12000 | 95 | 10.7 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 1.685 | 25 | 29 | 0 | 0 | 0 | 0 | 0.28 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0
YMeKrvas 12/20 kV 1x150 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 12000 | 150 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 1.65 | 25 | 31.5 | 0 | 0 | 0 | 0 | 0.25 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0
YMeKrvas 12/20 kV 1x240 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 12000 | 240 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 1.685 | 25 | 35.3 | 0 | 0 | 0 | 0 | 0.23 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0
YMeKrvas 12/20 kV 1x400 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 12000 | 400 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 1.6 | 50 | 39.9 | 0 | 0 | 0 | 0 | 0.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0
YMeKrvas 12/20 kV 1x630 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 12000 | 630 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 1.625 | 50 | 46.1 | 0 | 0 | 0 | 0 | 0.35 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0
YMeKrvas 12/20 kV 1x800 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 12000 | 800 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 1.64 | 50 | 49.7 | 0 | 0 | 0 | 0 | 0.32 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0
YMeKrvas 18/30 kV 1x150 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 18000 | 150 | 13.4 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1.74 | 25 | 36.8 | 0 | 0 | 0 | 0 | 0.22 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0
YMeKrvas 18/30 kV 1x240 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 18000 | 240 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1.775 | 25 | 40.6 | 0 | 0 | 0 | 0 | 0.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0
YMeKrvas 18/30 kV 1x400 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 18000 | 400 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1.695 | 50 | 45.2 | 0 | 0 | 0 | 0 | 0.36 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0
YMeKrvas 18/30 kV 1x630 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 18000 | 630 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1.72 | 50 | 51.4 | 0 | 0 | 0 | 0 | 0.31 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0
YMeKrvas 18/30 kV 1x800 Al | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 18000 | 800 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1.73 | 50 | 55 | 0 | 0 | 0 | 0 | 0.29 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0
YMeKrvaslqwd 6/10 kV 1x630 Alrm as70 | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 630 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 1.355 | 70 | 41.6 | 0 | 0 | 0 | 0 | 0.54 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0
YMeKrvaslqwd 6/10 kV 1x400 Alrm as70 | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 400 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 1.405 | 70 | 35.4 | 0 | 0 | 0 | 0 | 0.64 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0
YMeKrvaslwd 36/50 kV 1x400 Alrm as95 TKF | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmNone | 36000 | 400 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1.14 | 95 | 49.5 | 0 | 0 | 0 | 0 | 0.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.2 | 0 | 0
YMeKrvaslwd 8,7/15 kV 1x240 Curs as25 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imXLPEUnfilled | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 8700 | 240 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 1.66 | 25 | 35 | 0 | 0 | 0 | 0 | 0.23 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0
YMeKrvaslwd 8,7/15 kV 1x630 Curs as50 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 8700 | 630 | 31.1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 1.3 | 50 | 46 | 0 | 0 | 0 | 0 | 0.35 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0
YMeKrvaslwd 36/50 kV 1x400 Alrm as95 NKF | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmNone | 36000 | 400 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1.475 | 95 | 52 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 0 | 0
YMeKrvaslwd 36/50 kV 1x630 Alrm as95 NKF | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmNone | 36000 | 630 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1.675 | 95 | 59 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0
YMeKrvaslwd 36/50 kV 1x800 Alrm as95 NKF | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmNone | 36000 | 400 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 2.525 | 95 | 66 | 0 | 0 | 0 | 0 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0
VGYMvKrvasmb 6/10 kV 3x 25 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 6000 | 25 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0.95 | 5 | 16.9 | 0 | 0 | 0 | 0 | 0.1 | 3 | 42 | 47 | 0 | 0 | 2.5 | 0 | 60 | 0 | 0 | 51 | 36.5 | 0
VGYMvKrvasmb 6/10 kV 3x 35 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 6000 | 35 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0.95 | 6 | 18 | 0 | 0 | 0 | 0 | 0.1 | 3 | 45 | 50 | 0 | 0 | 2.5 | 0 | 60 | 0 | 0 | 54 | 39 | 0
VGYMvKrvasmb 6/10 kV 3x 50 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 6000 | 50 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0.95 | 6 | 19.1 | 0 | 0 | 0 | 0 | 0.1 | 3 | 48 | 53 | 0 | 0 | 2.5 | 0 | 60 | 0 | 0 | 57 | 41.5 | 0
VGYMvKrvasmb 6/10 kV 3x 70 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 6000 | 70 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0.95 | 6 | 20.8 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 52 | 57 | 0 | 0 | 2.5 | 0 | 60 | 0 | 0 | 61 | 45 | 0
VGYMvKrvasmb 6/10 kV 3x 95 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 6000 | 95 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0.95 | 7 | 22.5 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 55 | 60 | 0 | 0 | 2.5 | 0 | 69 | 0 | 0 | 65 | 49 | 0
VGYMvKrvasmb 6/10 kV 3x120 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 6000 | 120 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0.95 | 7 | 23.9 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 59 | 64 | 0 | 0 | 2.5 | 0 | 69 | 0 | 0 | 69 | 52 | 0
VGYMvKrvasmb 6/10 kV 3x150 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 6000 | 150 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0.95 | 8 | 25.4 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 61 | 66 | 0 | 0 | 2.5 | 0 | 76 | 0 | 0 | 72 | 55 | 0
VGYMvKrvasmb 6/10 kV 3x185 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 6000 | 185 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 0.95 | 8 | 27.1 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 65 | 71 | 0 | 0 | 2.5 | 0 | 81 | 0 | 0 | 76 | 58.5 | 0
VGYMvKrvasmb 6/10 kV 3x240 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 6000 | 240 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 1 | 9 | 29.7 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 71 | 76 | 0 | 0 | 2.5 | 0 | 88 | 0 | 0 | 82 | 64.2 | 0
VGYMvKrvasmb 8,7/15 kV 3x 35 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 8700 | 35 | 7.2 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0.95 | 6 | 20.2 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 50.6 | 55.1 | 0 | 0 | 2.5 | 0 | 65 | 0 | 0 | 59 | 44 | 0
VGYMvKrvasmb 8,7/15 kV 3x 50 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 8700 | 50 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0.95 | 7 | 21.3 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 53.6 | 58.1 | 0 | 0 | 2.5 | 0 | 68 | 0 | 0 | 62 | 46.5 | 0
VGYMvKrvasmb 8,7/15 kV 3x 70 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 8700 | 70 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0.95 | 7 | 23 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 56.6 | 61.1 | 0 | 0 | 2.5 | 0 | 71 | 0 | 0 | 65 | 50 | 0
VGYMvKrvasmb 8,7/15 kV 3x 95 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 8700 | 95 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0.95 | 8 | 24.7 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 60.2 | 64.7 | 0 | 0 | 2.5 | 0 | 76 | 0 | 0 | 70 | 54 | 0
VGYMvKrvasmb 8,7/15 kV 3x120 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 8700 | 120 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0.95 | 8 | 26.1 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 63.8 | 68.3 | 0 | 0 | 2.5 | 0 | 76 | 0 | 0 | 73 | 57 | 0
VGYMvKrvasmb 8,7/15 kV 3x150 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 8700 | 150 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0.95 | 9 | 27.6 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 67.4 | 71.9 | 0 | 0 | 2.5 | 0 | 76 | 0 | 0 | 77 | 60 | 0
VGYMvKrvasmb 8,7/15 kV 3x185 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 8700 | 185 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0.95 | 9 | 29.3 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 71.4 | 75.9 | 0 | 0 | 2.5 | 0 | 76 | 0 | 0 | 81 | 64 | 0
VGYMvKrvasmb 8,7/15 kV 3x240 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 8700 | 240 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 0.375 | 9 | 29.3 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 71.4 | 74.5 | 0 | 0 | 1.5 | 0 | 76 | 0 | 0 | 81.7 | 64.5 | 0
VGYMvKrvasmb 12/20 kV 3x 50 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 12000 | 50 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0.95 | 7 | 23.3 | 0 | 0 | 0 | 0 | 0.1 | 2 | 55 | 60.4 | 0 | 0 | 2.5 | 0 | 60 | 0 | 0 | 67 | 50.5 | 0
VGYMvKrvasmb 12/20 kV 3x 70 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 12000 | 70 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0.95 | 8 | 25 | 0 | 0 | 0 | 0 | 0.1 | 2.5 | 60 | 64.5 | 0 | 0 | 2.5 | 0 | 65 | 0 | 0 | 70 | 54 | 0
VGYMvKrvasmb 12/20 kV 3x 95 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 12000 | 95 | 11.7 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0.95 | 8 | 26.7 | 0 | 0 | 0 | 0 | 0.1 | 3.5 | 65.3 | 69.7 | 0 | 0 | 2.5 | 0 | 69 | 0 | 0 | 75 | 58.3 | 0
VGYMvKrvasmb 12/20 kV 3x120 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 12000 | 120 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0.95 | 9 | 28.1 | 0 | 0 | 0 | 0 | 0.1 | 4 | 68.3 | 72.7 | 0 | 0 | 2.5 | 0 | 69 | 0 | 0 | 78 | 61 | 0
VGYMvKrvasmb 12/20 kV 3x150 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 12000 | 150 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0.95 | 9 | 29.6 | 0 | 0 | 0 | 0 | 0.1 | 4.5 | 72.3 | 76.8 | 0 | 0 | 2.5 | 0 | 71 | 0 | 0 | 82 | 64 | 0
VGYMvKrvasmb 12/20 kV 3x185 as50 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSL | imPVC | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 12000 | 185 | 16.3 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0.95 | 10 | 31.3 | 0 | 0 | 0 | 0 | 0.1 | 4.5 | 76.3 | 80.8 | 0 | 0 | 2.5 | 0 | 76 | 0 | 0 | 86 | 68 | 0
YMeKrvasdlwd 8,7/15 kV 1x400 Curs + as50 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 8700 | 400 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 1.37 | 50 | 39.3 | 0 | 0 | 0 | 0 | 0.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0
YMeKrvaslqwd 6/12 kV 3 x 95 Alrm Kudi | 3 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scCommon | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 95 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 7.54 | 50 | 50 | 0 | 0 | 0 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 46 | 0
YMeKrvaslqwd 6/12 kV 3 x 150 Alrm Kudi | 3 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scCommon | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 150 | 13.3 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 7.8 | 50 | 53.5 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 49 | 0
YMeKrvaslqwd 6/12 kV 3 x 240 Alrm Kudi | 3 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scCommon | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 240 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 9.195 | 70 | 63 | 0 | 0 | 0 | 0 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 58 | 0
YMeKrvaslqwd 12/20 kV 3 x 240 Alrm Kudi | 3 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scCommon | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 12000 | 240 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 11.04 | 70 | 70.3 | 0 | 0 | 0 | 0 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 67 | 0
XLPE 64/110 1x 185 Cu Str | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrNone | samLead | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 64000 | 185 | 17.1 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 2.075 | 489.18 | 70 | 0 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0
XLPE 64/110 1x 300 Al Sol | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrNone | samLead | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 64000 | 300 | 19.1 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 2.075 | 474.73 | 68 | 0 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77 | 0 | 0
XLPE 64/110 1x 300 Al Str | 1 | ccRound | ctStranded | cmAl | imXLPEUnfilled | scrNone | samLead | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 64000 | 300 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1.925 | 489 | 70 | 0 | 0 | 0 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 0
XLPE 64/110 1x1000 Cu Mil | 1 | ccRound | ctMilliken | cmCu | imXLPEUnfilled | scrNone | samLead | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 64000 | 1000 | 39.5 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 3.075 | 689.39 | 87 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0
XLPE 87/150 1x 300 Cu Str | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrNone | samLead | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 87000 | 300 | 21.7 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 2.075 | 632.25 | 83 | 0 | 0 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0
XLPE 87/150 1x 500 Al Sol | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrNone | samLead | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 87000 | 500 | 24.6 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2.1 | 608.68 | 80 | 0 | 0 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0
XLPE 87/150 1x1000 Cu Mil | 1 | ccRound | ctMilliken | cmCu | imXLPEUnfilled | scrNone | samLead | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 87000 | 1000 | 39.5 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 2.975 | 811 | 95 | 0 | 0 | 0 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0
XLPE 127/220 1x 500 Cu Str | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrNone | samLead | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 127000 | 500 | 27.4 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 2.95 | 875.53 | 99 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 0
XLPE 127/220 1x 800 Al Sol | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrNone | samLead | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 127000 | 800 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 2.675 | 866.42 | 98 | 0 | 0 | 0 | 0 | 2.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 0 | 0
GPLK(h) 1 kV 3x150 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 1000 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 290 | 46 | 0 | 0 | 0 | 0 | 2.1 | 3 | 52 | 54 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 61 | 40 | 0
GPLK(h) 1 kV 3x185 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 1000 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1 | 0 | 359 | 52 | 0 | 0 | 0 | 0 | 2.3 | 3 | 58 | 60 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 67 | 46 | 0
GPLK(h) 1 kV 3x240 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 1000 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 404 | 56 | 0 | 0 | 0 | 0 | 2.4 | 3 | 62 | 64 | 0 | 0 | 0 | 198 | 0 | 0 | 0 | 72 | 50 | 0
GPLK 8/10 kV 3x 25 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 156.48 | 31 | 0 | 0 | 0 | 0 | 1.7 | 0.75 | 32.5 | 37 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 40 | 23 | 0
GPLK 8/10 kV 3x 35 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 156.48 | 31 | 0 | 0 | 0 | 0 | 1.7 | 0.75 | 32.5 | 37 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 40 | 23 | 0
GPLK 8/10 kV 3x 50 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 193.4 | 36 | 0 | 0 | 0 | 0 | 1.8 | 0.75 | 37.5 | 42 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 45 | 28 | 0
GPLK 8/10 kV 3x 70 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 215.48 | 38 | 0 | 0 | 0 | 0 | 1.9 | 1.75 | 41.5 | 46 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 50 | 30 | 0
GPLK 8/10 kV 3x 95 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 238.76 | 40 | 0 | 0 | 0 | 0 | 2 | 2.75 | 45.5 | 50 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 54 | 32 | 0
GPLK 8/10 kV 3x120 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 263.23 | 42 | 0 | 0 | 0 | 0 | 2.1 | 2.75 | 47.5 | 52 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 56 | 34 | 0
GPLK 8/10 kV 3x150 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 302.72 | 46 | 0 | 0 | 0 | 0 | 2.2 | 2.25 | 50.5 | 55 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 61 | 38 | 0
GPLK 8/10 kV 3x185 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 330.21 | 48 | 0 | 0 | 0 | 0 | 2.3 | 1.75 | 51.5 | 56 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 64 | 39 | 0
GPLK 8/10 kV 3x240 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 389.05 | 54 | 0 | 0 | 0 | 0 | 2.4 | 2.25 | 58.5 | 63 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 67 | 45 | 0
GPLK 8/10 kV 3x300 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 404 | 56 | 0 | 0 | 0 | 0 | 2.4 | 2.5 | 61 | 66 | 0 | 0 | 0 | 499 | 0 | 0 | 0 | 70 | 47 | 0
GPLK 8/10 kV 3x400 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 457 | 63 | 0 | 0 | 0 | 0 | 2.4 | 3.5 | 70 | 75 | 0 | 0 | 0 | 569 | 0 | 0 | 0 | 80 | 54 | 0
GPLK 8/10 kV 3x 25 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 156.48 | 31 | 0 | 0 | 0 | 0 | 1.7 | 0.75 | 32.5 | 37 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 40 | 23 | 0
GPLK 8/10 kV 3x 35 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 156.48 | 31 | 0 | 0 | 0 | 0 | 1.7 | 0.75 | 32.5 | 37 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 40 | 23 | 0
GPLK 8/10 kV 3x 50 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 193.4 | 36 | 0 | 0 | 0 | 0 | 1.8 | 0.75 | 37.5 | 42 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 45 | 28 | 0
GPLK 8/10 kV 3x 70 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 215.48 | 38 | 0 | 0 | 0 | 0 | 1.9 | 1.75 | 41.5 | 46 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 50 | 30 | 0
GPLK 8/10 kV 3x 95 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 238.76 | 40 | 0 | 0 | 0 | 0 | 2 | 2.75 | 45.5 | 50 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 54 | 32 | 0
GPLK 8/10 kV 3x120 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 263.23 | 42 | 0 | 0 | 0 | 0 | 2.1 | 2.75 | 47.5 | 52 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 56 | 34 | 0
GPLK 8/10 kV 3x150 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 302.72 | 46 | 0 | 0 | 0 | 0 | 2.2 | 2.25 | 50.5 | 55 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 61 | 38 | 0
GPLK 8/10 kV 3x185 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 330.21 | 48 | 0 | 0 | 0 | 0 | 2.3 | 1.75 | 51.5 | 56 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 64 | 39 | 0
GPLK 8/10 kV 3x240 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 389.05 | 54 | 0 | 0 | 0 | 0 | 2.4 | 2.25 | 58.5 | 63 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 67 | 45 | 0
GPLK 8/10 kV 3x300 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 404 | 56 | 0 | 0 | 0 | 0 | 2.4 | 2.5 | 61 | 66 | 0 | 0 | 0 | 499 | 0 | 0 | 0 | 70 | 47 | 0
GPLK 8/10 kV 3x400 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 0 | 457 | 63 | 0 | 0 | 0 | 0 | 2.4 | 3.5 | 70 | 75 | 0 | 0 | 0 | 569 | 0 | 0 | 0 | 80 | 54 | 0
GPLK 10/10 kV 3x 25 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 178.69 | 33.4 | 0 | 0 | 0 | 0 | 1.8 | 1.9 | 37.2 | 41 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 49 | 24 | 0
GPLK 10/10 kV 3x 35 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 196.38 | 34.8 | 0 | 0 | 0 | 0 | 1.9 | 1.8 | 38.4 | 42 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 51 | 26 | 0
GPLK 10/10 kV 3x 50 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 226.19 | 38 | 0 | 0 | 0 | 0 | 2 | 2.25 | 42.5 | 47 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 54 | 29 | 0
GPLK 10/10 kV 3x 70 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 263.23 | 42 | 0 | 0 | 0 | 0 | 2.1 | 2.25 | 46.5 | 51 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 58 | 32 | 0
GPLK 10/10 kV 3x 95 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 288.9 | 44 | 0 | 0 | 0 | 0 | 2.2 | 2.25 | 48.5 | 53 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 59 | 33 | 0
GPLK 10/10 kV 3x120 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 315.76 | 46 | 0 | 0 | 0 | 0 | 2.3 | 2.25 | 50.5 | 55 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 61 | 35 | 0
GPLK 10/10 kV 3x150 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 351.36 | 49 | 0 | 0 | 0 | 0 | 2.4 | 2.25 | 53.5 | 58 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 65 | 38 | 0
GPLK 10/10 kV 3x185 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 373.98 | 52 | 0 | 0 | 0 | 0 | 2.4 | 2.25 | 56.5 | 61 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 68 | 41 | 0
GPLK 10/10 kV 3x240 Al | 3 | ccSector | ctStranded | cmAl | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 444.35 | 57 | 0 | 0 | 0 | 0 | 2.6 | 2.25 | 61.5 | 66 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 72 | 45 | 0
GPLK 10/10 kV 3x 25 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 178.69 | 33.4 | 0 | 0 | 0 | 0 | 1.8 | 1.9 | 37.2 | 41 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 49 | 24 | 0
GPLK 10/10 kV 3x 35 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 196.38 | 34.8 | 0 | 0 | 0 | 0 | 1.9 | 1.8 | 38.4 | 42 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 51 | 26 | 0
GPLK 10/10 kV 3x 50 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 226.19 | 38 | 0 | 0 | 0 | 0 | 2 | 2.25 | 42.5 | 47 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 54 | 29 | 0
GPLK 10/10 kV 3x 70 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 264.55 | 42.2 | 0 | 0 | 0 | 0 | 2.1 | 2.2 | 46.6 | 51 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 57 | 32 | 0
GPLK 10/10 kV 3x 95 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 286.14 | 43.6 | 0 | 0 | 0 | 0 | 2.2 | 2.35 | 48.3 | 53 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 61 | 33 | 0
GPLK 10/10 kV 3x120 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 314.32 | 45.8 | 0 | 0 | 0 | 0 | 2.3 | 2.3 | 50.4 | 55 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 64 | 35 | 0
GPLK 10/10 kV 3x150 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 351.36 | 49 | 0 | 0 | 0 | 0 | 2.4 | 2.25 | 53.5 | 58 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 66 | 38 | 0
GPLK 10/10 kV 3x185 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 388.77 | 52 | 0 | 0 | 0 | 0 | 2.5 | 2.25 | 56.5 | 61 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 70 | 41 | 0
GPLK 10/10 kV 3x240 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 10000 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 441.08 | 56.6 | 0 | 0 | 0 | 0 | 2.6 | 2.35 | 61.3 | 66 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 74 | 45 | 0
VGPLK 8/10 kV 3x70 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcBitumenJute | odNone | pmSteel | 8000 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9 | 0 | 215 | 38 | 0 | 0 | 0 | 0 | 1.9 | 2 | 42 | 46 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 50 | 30 | 0
VGPLK 10/10 kV 3x 25 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcPVC | odNone | pmSteel | 10000 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 269.17 | 33.4 | 0 | 0 | 0 | 0 | 2.8 | 1.9 | 37.2 | 41 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | 47 | 24 | 0
VGPLK 10/10 kV 3x 35 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcPVC | odNone | pmSteel | 10000 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 196.38 | 34.8 | 0 | 0 | 0 | 0 | 1.9 | 1.8 | 38.4 | 42 | 0 | 0 | 0 | 125 | 0 | 0 | 0 | 49 | 26 | 0
VGPLK 10/10 kV 3x 50 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcPVC | odNone | pmSteel | 10000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 226.19 | 38 | 0 | 0 | 0 | 0 | 2 | 2.25 | 42.5 | 47 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 54 | 29 | 0
VGPLK 10/10 kV 3x 70 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcPVC | odNone | pmSteel | 10000 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 264.55 | 42.2 | 0 | 0 | 0 | 0 | 2.1 | 2.2 | 46.6 | 51 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 57 | 32 | 0
VGPLK 10/10 kV 3x 95 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcPVC | odNone | pmSteel | 10000 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 286.14 | 43.6 | 0 | 0 | 0 | 0 | 2.2 | 2.35 | 48.3 | 53 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 59 | 33 | 0
VGPLK 10/10 kV 3x120 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcPVC | odNone | pmSteel | 10000 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 314.32 | 45.8 | 0 | 0 | 0 | 0 | 2.3 | 2.3 | 50.4 | 55 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 61 | 35 | 0
VGPLK 10/10 kV 3x150 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcPVC | odNone | pmSteel | 10000 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 351.36 | 49 | 0 | 0 | 0 | 0 | 2.4 | 2.25 | 53.5 | 58 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 65 | 38 | 0
VGPLK 10/10 kV 3x185 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcPVC | odNone | pmSteel | 10000 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 388.77 | 52 | 0 | 0 | 0 | 0 | 2.5 | 2.25 | 56.5 | 61 | 0 | 0 | 0 | 230 | 0 | 0 | 0 | 68 | 41 | 0
VGPLK 10/10 kV 3x240 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrMetalizedPaper | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atTape | alContactLay | pcPVC | odNone | pmSteel | 10000 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 441.08 | 56.6 | 0 | 0 | 0 | 0 | 2.6 | 2.35 | 61.3 | 66 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 72 | 45 | 0
EDPLK 10/10 kV 3x185 Cu | 3 | ccSector | ctStranded | cmCu | imPaperMassImpregnated | scrNone | samLead | scBelted | imPaperMassImpregnated | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 10000 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 378 | 52.5 | 0 | 0 | 0 | 0 | 2.4 | 1.25 | 55 | 57 | 0 | 0 | 2 | 0 | 60 | 0 | 0 | 64 | 42 | 0
Oil filled 3x70 mm 36/66 kV | 3 | ccRound | ctStranded | cmCu | imPaperOilPressure | scrMetalizedPaper | samLead | scCommon | imBitumenJute | samStainlessSteel | acCommon | atTape | alShortLay | pcPVC | odExternal | pmSteel | 36000 | 70 | 9.9 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0.5 | 349 | 55 | 0 | 0 | 0 | 0 | 2.1 | 1 | 59 | 60 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 65 | 50 | 0
Oil filled 3x120 mm 36/66 kV | 3 | ccRound | ctStranded | cmCu | imPaperOilPressure | scrMetalizedPaper | samLead | scCommon | imBitumenJute | samStainlessSteel | acCommon | atTape | alShortLay | pcPVC | odExternal | pmSteel | 36000 | 120 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0.5 | 431 | 62 | 0 | 0 | 0 | 0 | 2.3 | 1 | 66 | 67 | 0 | 0 | 0 | 104 | 0 | 0 | 0 | 72 | 57 | 0
EGPLKod 40/70 kV 3x120 Cu | 3 | ccRound | ctCompact | cmCu | imPaperOFSelfContained | scrMetalizedPaper | samLead | scCommon | imBitumenJute | samSteel | acCommon | atTape | alContactLay | pcPE | odExternal | pmNone | 40000 | 120 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0.01 | 621 | 65 | 0 | 0 | 0 | 0 | 3.2 | 5 | 75 | 77 | 0 | 0 | 0 | 239 | 0 | 0 | 0 | 86 | 60 | 0
EGPLKod 40/70 kV 3x150 Cu | 3 | ccRound | ctCompact | cmCu | imPaperOFSelfContained | scrMetalizedPaper | samLead | scCommon | imBitumenJute | samSteel | acCommon | atTape | alContactLay | pcPE | odExternal | pmNone | 40000 | 150 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0.01 | 671 | 68 | 0 | 0 | 0 | 0 | 3.3 | 5 | 78 | 80 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 89 | 60 | 0
EGPLKod 40/70 kV 3x240 Cu | 3 | ccRound | ctCompact | cmCu | imPaperOFSelfContained | scrMetalizedPaper | samLead | scCommon | imBitumenJute | samSteel | acCommon | atTape | alContactLay | pcPE | odExternal | pmNone | 40000 | 240 | 18.9 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0.01 | 819 | 78 | 0 | 0 | 0 | 0 | 3.5 | 4.5 | 87 | 89 | 0 | 0 | 0 | 276 | 0 | 0 | 0 | 98 | 70 | 0
ESPLKod 115/200 kV 1x800 mm2 | 1 | ccRound | ctStranded | cmCu | imPaperOFSelfContained | scrMetalizedPaper | samLead | scSeparate | imBitumenJute | samSteel | acSeparate | atTape | alContactLay | pcPE | odInternal | pmNone | 115000 | 800 | 36.5 | 17.71 | 0 | 0 | 0 | 0 | 0 | 14.5 | 0 | 917 | 73.5 | 0 | 0 | 0 | 0 | 4 | 0.4 | 77.8 | 78 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 87 | 0 | 0
UGD 87/150 3x300 Cu | 3 | ccRound | ctStranded | cmCu | imPaperPreIntGasPressure | scrMetalizedPaper | samLead | scPipeType | imPaperPreIntGasPressure | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmStainlessSteel | 87000 | 300 | 19.35 | 0 | 0 | 0 | 0 | 0 | 0 | 12.55 | 0.5375 | 289 | 50.4 | 0 | 0 | 0 | 0 | 1.9 | 0.9 | 117.8 | 0 | 0 | 0 | 1.4 | 0 | 320 | 151 | 159 | 164 | 114.7 | 0
ABB 10 kV 1x240 Cu as 35 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 6000 | 240 | 18.1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 1.3825 | 35 | 31.15 | 0 | 0 | 0 | 0 | 0.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0
ABB 10 kV 1x1000 Cu as 35 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samCopper | acSeparate | atWire | alLongLay | pcPVC | odNone | pmSteel | 6000 | 1000 | 37.9 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 1.8575 | 35 | 52.55 | 0 | 0 | 0 | 0 | 0.21 | 0 | 52.2 | 52.55 | 0 | 0 | 0.7 | 0 | 40 | 0 | 0 | 58 | 0 | 0
ABB 70 kV 1x1000 Cu as 35 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samCopper | acSeparate | atWire | alLongLay | pcPE | odNone | pmSteel | 6000 | 1000 | 37.9 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1.8275 | 35 | 65.55 | 0 | 0 | 0 | 0 | 0.17 | 0 | 65.2 | 65.55 | 0 | 0 | 0.7 | 0 | 60 | 0 | 0 | 72 | 0 | 0
ABB 64/110 kV 1x300 Al as 95 | 1 | ccRound | ctStranded | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 64000 | 300 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 1.5 | 95 | 55.6 | 0 | 0 | 0 | 0 | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0
ABB 87/150 kV 1x240 Cu as 95 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 87000 | 240 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 1.695 | 95 | 67.68 | 0 | 0 | 0 | 0 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0
ABB 87/150 kV 1x300 Cu as 95 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 87000 | 300 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 1.565 | 95 | 67.66 | 0 | 0 | 0 | 0 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0
ABB 87/150 kV 1x400 Cu as 95 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 87000 | 400 | 23.1 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 1.655 | 95 | 68.6 | 0 | 0 | 0 | 0 | 0.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0
ABB 87/150 kV 1x500 Cu as 95 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 87000 | 500 | 26.4 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 1.5525 | 95 | 69.49 | 0 | 0 | 0 | 0 | 0.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0
ABB 87/150 kV 1x630 Cu as 95 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 87000 | 630 | 30.2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1.58 | 95 | 71.38 | 0 | 0 | 0 | 0 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0
ABB 87/150 kV 1x800 Cu as 95 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 87000 | 800 | 33.7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1.9025 | 95 | 76.11 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 0
ABB 87/150 kV 1x1000 Cu as 95 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 87000 | 1000 | 37.9 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1.7875 | 95 | 79.81 | 0 | 0 | 0 | 0 | 0.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
ABB 87/150 kV 1x1200 Cu as 95 | 1 | ccRound | ctMilliken | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 87000 | 1200 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 1.89 | 95 | 86.26 | 0 | 0 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 0 | 0
ABB 87/150 kV 1x1400 Cu as 95 | 1 | ccRound | ctMilliken | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 87000 | 1400 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 2.3125 | 95 | 92.91 | 0 | 0 | 0 | 0 | 0.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0
ABB 87/150 kV 1x1600 Al scr 95 | 1 | ccRound | ctMilliken | cmAl | imXLPEFilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 87000 | 1600 | 47.4 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 3.645 | 95 | 96.6 | 0 | 0 | 0 | 0 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0
ABB 87/150 kV 1x1600 Cu as 95 | 1 | ccRound | ctMilliken | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 87000 | 1600 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 2.52 | 95 | 96.7 | 0 | 0 | 0 | 0 | 0.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 0
ABB 87/150 kV 1x2000 Cu as 95 | 1 | ccRound | ctMilliken | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 87000 | 2000 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 2.455 | 95 | 100.42 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0
ABB 87/150 kV 1x2500 Cu as 95 | 1 | ccRound | ctMilliken | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 87000 | 2500 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 2.545 | 95 | 110.72 | 0 | 0 | 0 | 0 | 0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0
ABB 87/150 kV 1x3000 Cu as 95 | 1 | ccRound | ctMilliken | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 87000 | 3000 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 2.445 | 95 | 116.3 | 0 | 0 | 0 | 0 | 0.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 0 | 0
ABB 230/400 kV 1x3000 Cu as 185 | 1 | ccRound | ctMilliken | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 230000 | 3000 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 2.51 | 185 | 136.9 | 0 | 0 | 0 | 0 | 0.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 0
ABB 20 kV 3x95 Cu as 25 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scCommon | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmNone | 11550 | 95 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 6.87 | 25 | 50 | 0 | 0 | 0 | 0 | 0.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 49 | 0
ABB 20 kV 3x240 Cu as 35 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scCommon | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmNone | 11550 | 240 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 9.165 | 35 | 66 | 0 | 0 | 0 | 0 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 64 | 0
NAYY 1x150 | 1 | ccRound | ctStranded | cmAl | imPVC | scrNone | samSteel | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmNone | 600 | 150 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0.05 | 0.1 | 19 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0
NAYY 1x240 | 1 | ccRound | ctStranded | cmAl | imPVC | scrNone | samStainlessSteel | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmNone | 600 | 240 | 17.48 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0.03 | 34 | 23 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.48 | 0 | 0
NAYY 1x300 | 1 | ccRound | ctStranded | cmAl | imPVC | scrNone | samSteel | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmNone | 600 | 300 | 20.5 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0.05 | 0.1 | 26.5 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30.6 | 0 | 0
NAYY 3x95/50 | 3 | ccRound | ctStranded | cmAl | imPVC | scrNone | samSteel | scCommon | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmNone | 600 | 95 | 11.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4.45 | 1 | 33 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 28.3 | 0
NAYY 3x240/120 | 3 | ccRound | ctStranded | cmAl | imPVC | scrNone | samSteel | scCommon | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmNone | 600 | 240 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 6.4 | 120 | 52 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.3 | 48 | 0
BMvKas 3.6/6 1x500 Cu | 1 | ccRound | ctStranded | cmCu | imEPR | scrCuTape | samCopper | scSeparate | imNone | samCopper | acSeparate | atWire | alLongLay | pcPVC | odNone | pmSteel | 3600 | 500 | 30.8 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2 | 0.125 | 15 | 39.8 | 0 | 0 | 0 | 0 | 0.05 | 0 | 39.84 | 41.9 | 0 | 0 | 1.03 | 0 | 29 | 0 | 0 | 49.1 | 0 | 3
VULTA mb 3x300 sv | 3 | ccSector | ctStranded | cmCu | imXLPEUnfilled | scrNone | samCopper | scCommon | imRubber | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 1000 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 150 | 51.3 | 0 | 0 | 0 | 0 | 1.4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.4 | 47 | 0
VULTA mb 3x 95 sv | 3 | ccSector | ctStranded | cmCu | imXLPEUnfilled | scrNone | samCopper | scCommon | imRubber | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 1000 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 50 | 30.8 | 0 | 0 | 0 | 0 | 1.4 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.2 | 28 | 0
VULTA mb 3x35 sv | 3 | ccSector | ctStranded | cmCu | imXLPEUnfilled | scrNone | samCopper | scCommon | imRubber | samNone | acNone | atNone | alNone | pcPVC | odNone | pmSteel | 1000 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 0 | 16 | 21.1 | 0 | 0 | 0 | 0 | 1.13 | 1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.8 | 19 | 0
V-VMvKsas 0.6/1 kV - 4x95 Alsvm + sas35 | 3 | ccSector | ctSolid | cmAl | imPVC | scrNone | samCopper | scCommon | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmNone | 1000 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0 | 35 | 38 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 31 | 0
V-VMvKsas 0.6/1 kV - 4x50 Alsvm + sas25 | 3 | ccSector | ctSolid | cmAl | imPVC | scrNone | samCopper | scCommon | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmNone | 1000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | 0 | 25 | 29 | 0 | 0 | 0 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 23 | 0
V-VMvKsas 0.6/1 kV - 4x150 Alsvm + sas50 | 3 | ccSector | ctSolid | cmAl | imPVC | scrNone | samCopper | scCommon | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmNone | 1000 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 50 | 44 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 37 | 0
V-VMvKsas 0.6/1 kV - 4x240 Alsvm + sas70 | 3 | ccSector | ctSolid | cmAl | imPVC | scrNone | samCopper | scCommon | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmNone | 1000 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0 | 70 | 57.2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63.2 | 45.7 | 0
EYLKrvlwd 87/150kV 1x1200Cu | 1 | ccRound | ctMilliken | cmCu | imXLPEUnfilled | scrXLPE | samLead | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 87000 | 1200 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 18.25 | 1.825 | 444 | 90 | 0 | 0 | 0 | 0 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0
CC 132 kV 3x500 Cu 1 | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samAluminium | scSeparate | imPE | samSteel | acCommon | atWire | alLongLay | pcPE | odNone | pmNone | 76000 | 500 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 11.25 | 1 | 289 | 57 | 0 | 0 | 0 | 0 | 2 | 0.5 | 127 | 129 | 0 | 0 | 2 | 0 | 50 | 0 | 0 | 133 | 125 | 0
CC 132 kV 3x500 Cu 2 UGD | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samAluminium | scPipeType | imRubber | samSteel | acCommon | atWire | alLongLay | pcPE | odNone | pmAluminium | 76000 | 500 | 26.5 | 0 | 0 | 0 | 0 | 0 | 0 | 11.25 | 1 | 289 | 57 | 0 | 0 | 0 | 0 | 2 | 0.01 | 127 | 0 | 0 | 0 | 2 | 0 | 50 | 129 | 129 | 133 | 125 | 0
CC 132 kV 3x95 Cu 3 UGD | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samAluminium | scPipeType | imRubber | samSteel | acCommon | atWire | alLongLay | pcPE | odNone | pmAluminium | 76000 | 95 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 1.125 | 0.01 | 46 | 0 | 0 | 0 | 0 | 1 | 1 | 106 | 0 | 0 | 0 | 2 | 0 | 50 | 130 | 133 | 138 | 110.9 | 0
Twenpower 6/10 kV 1x800 Al | 1 | ccRound | ctStranded | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 800 | 31.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1.25 | 50 | 45.2 | 0 | 0 | 0 | 0 | 0.35 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0
Twenpower 6/10 kV 1x630 Al | 1 | ccRound | ctStranded | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 630 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1.25 | 50 | 41.6 | 0 | 0 | 0 | 0 | 0.35 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0
IEC 853 testkabel | 1 | ccRound | ctMilliken | cmCu | imPaperOFSelfContained | scrMetalizedPaper | samLead | scCommon | imNone | samNone | acNone | atNone | alNone | pcPE | odInternal | pmNone | 230000 | 2000 | 57.5 | 26.62 | 0 | 0 | 0 | 0 | 0 | 23 | 0.625 | 1382 | 114 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 0 | 0
Pirelli 18/30 kV 1*185/25mm2 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samAluminium | acSeparate | atTape | alLongLay | pcPE | odNone | pmNone | 18000 | 185 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 0.5 | 25 | 37 | 0 | 0 | 0 | 0 | 1 | 1 | 37.3 | 37.6 | 0 | 0 | 0 | 18 | 32 | 0 | 0 | 43 | 0 | 0
VPE 18/30kV 1*185/25mm2 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samCopper | acSeparate | atWire | alLongLay | pcPE | odNone | pmNone | 18000 | 185 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 25 | 38 | 0 | 0 | 0 | 0 | 1 | 1 | 36 | 38 | 0 | 0 | 1 | 0 | 32 | 0 | 0 | 43 | 0 | 0
Corus 87/150 1x800 Al | 1 | ccRound | ctSolid | cmAl | imXLPEFilled | scrXLPE | samLead | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPVC | odNone | pmNone | 1000 | 800 | 31.3 | 0 | 0 | 0 | 0 | 0 | 0 | 18.8 | 1.475 | 632 | 80 | 0 | 0 | 0 | 0 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0
XDMZ-MONO | 1 | ccRound | ctSolid | cmCu | imXLPEUnfilled | scrXLPE | samAluminium | scSeparate | imNone | samNone | acNone | atNone | alNone | pcPE | odNone | pmNone | 12 | 300 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 0.9 | 41 | 35 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.8 | 0 | 0
XMT 15kV 3x350MCM | 3 | ccRound | ctStranded | cmCu | imPE | scrNone | samCopper | scSeparate | imPVC | samCopper | acCommon | atTape | alLongLay | pcPVC | odNone | pmNone | 8700 | 177 | 15.54 | 0 | 0 | 0 | 0 | 0 | 0 | 4.29 | 0.625 | 16 | 27 | 0 | 0 | 0 | 0 | 0.19 | 0.7 | 59.59 | 59.6 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 64.87 | 58.19 | 0
XMT 15kV 1x350MCM | 1 | ccRound | ctStranded | cmCu | imPE | scrNone | samCopper | scSL | imPVC | samCopper | acCommon | atTape | alLongLay | pcPVC | odNone | pmNone | 8700 | 177 | 15.54 | 0 | 0 | 0 | 0 | 0 | 0 | 4.29 | 0.625 | 16 | 27 | 0 | 0 | 0 | 0 | 0.19 | 0.7 | 30 | 30.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0
YMeKrvaslwd 8.7/15 kV - 1x630 as50 | 1 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 8700 | 630 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 1.47 | 50 | 45 | 0 | 0 | 0 | 0 | 0.36 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0
Prysmian 87/150 kV 1x630 | 1 | ccRound | ctCompact | cmCu | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 8700 | 630 | 29.4 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 3 | 75 | 80 | 0 | 0 | 0 | 0 | 0.3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 0 | 0
1x630 in pipe | 1 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samNone | acNone | atNone | alNone | pcPE | odNone | pmSteel | 6000 | 630 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 1.355 | 70 | 41.6 | 0 | 0 | 0 | 0 | 0.54 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0
3x630 in pipe | 3 | ccRound | ctSolid | cmAl | imXLPEUnfilled | scrXLPE | samCopper | scSeparate | imRubber | samSteel | acCommon | atNone | alNone | pcRubber | odNone | pmSteel | 6000 | 630 | 27.9 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 1.355 | 70 | 41.6 | 0 | 0 | 0 | 0 | 0.54 | 1 | 95 | 96 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 140 | 100 | 0
3x500RM 87/150kV City cable staal | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samAluminium | scPipeType | imPE | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 87000 | 500 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5 | 2.225 | 29 | 61 | 0 | 0 | 0 | 0 | 0.15 | 1 | 133 | 0 | 0 | 0 | 1.2 | 0 | 56 | 150 | 159 | 160 | 133 | 0
3x500RM 87/150kV City cable PE | 3 | ccRound | ctStranded | cmCu | imXLPEUnfilled | scrXLPE | samAluminium | scSeparate | imPE | samSteel | acCommon | atWire | alLongLay | pcPVC | odNone | pmSteel | 87000 | 500 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5 | 2.225 | 29 | 61 | 0 | 0 | 0 | 0 | 0.15 | 1 | 133 | 137 | 0 | 0 | 1.2 | 0 | 56 | 0 | 0 | 138 | 133 | 0

## Cable mapping
Cable name | Cable geometry name
3* 25 AL GPLK 8/10 | GPLK 8/10 kV 3x 25 Al
3* 35 AL GPLK 8/10 | GPLK 8/10 kV 3x 35 Al
3* 50 AL GPLK 8/10 | GPLK 8/10 kV 3x 50 Al
3* 70 AL GPLK 8/10 | GPLK 8/10 kV 3x 70 Al
3* 95 AL GPLK 8/10 | GPLK 8/10 kV 3x 95 Al
3*120 AL GPLK 8/10 | GPLK 8/10 kV 3x120 Al
3*150 AL GPLK 8/10 | GPLK 8/10 kV 3x150 Al
3*185 AL GPLK 8/10 | GPLK 8/10 kV 3x185 Al
3*240 AL GPLK 8/10 | GPLK 8/10 kV 3x240 Al
3*300 AL GPLK 8/10 | GPLK 8/10 kV 3x300 Al
3*400 AL GPLK 8/10 | GPLK 8/10 kV 3x400 Al
3* 25 AL GPLK 10/10 | GPLK 10/10 kV 3x 25 Al
3* 35 AL GPLK 10/10 | GPLK 10/10 kV 3x 35 Al
3* 50 AL GPLK 10/10 | GPLK 10/10 kV 3x 50 Al
3* 70 AL GPLK 10/10 | GPLK 10/10 kV 3x 70 Al
3* 95 AL GPLK 10/10 | GPLK 10/10 kV 3x 95 Al
3*120 AL GPLK 10/10 | GPLK 10/10 kV 3x120 Al
3*150 AL GPLK 10/10 | GPLK 10/10 kV 3x150 Al
3*185 AL GPLK 10/10 | GPLK 10/10 kV 3x185 Al
3*240 AL GPLK 10/10 | GPLK 10/10 kV 3x240 Al
3* 25 CU GPLK 8/10 | GPLK 8/10 kV 3x 25 Cu
3* 35 CU GPLK 8/10 | GPLK 8/10 kV 3x 35 Cu
3* 50 CU GPLK 8/10 | GPLK 8/10 kV 3x 50 Cu
3* 70 CU GPLK 8/10 | GPLK 8/10 kV 3x 70 Cu
3* 95 CU GPLK 8/10 | GPLK 8/10 kV 3x 95 Cu
3*120 CU GPLK 8/10 | GPLK 8/10 kV 3x120 Cu
3*150 CU GPLK 8/10 | GPLK 8/10 kV 3x150 Cu
3*185 CU GPLK 8/10 | GPLK 8/10 kV 3x185 Cu
3*240 CU GPLK 8/10 | GPLK 8/10 kV 3x240 Cu
3*300 CU GPLK 8/10 | GPLK 8/10 kV 3x300 Cu
3*400 CU GPLK 8/10 | GPLK 8/10 kV 3x400 Cu
3* 25 CU GPLK 10/10 | GPLK 10/10 kV 3x 25 Cu
3* 35 CU GPLK 10/10 | GPLK 10/10 kV 3x 35 Cu
3* 50 CU GPLK 10/10 | GPLK 10/10 kV 3x 50 Cu
3* 70 CU GPLK 10/10 | GPLK 10/10 kV 3x 70 Cu
3* 95 CU GPLK 10/10 | GPLK 10/10 kV 3x 95 Cu
3*120 CU GPLK 10/10 | GPLK 10/10 kV 3x120 Cu
3*150 CU GPLK 10/10 | GPLK 10/10 kV 3x150 Cu
3*185 CU GPLK 10/10 | GPLK 10/10 kV 3x185 Cu
3*240 CU GPLK 10/10 | GPLK 10/10 kV 3x240 Cu
3x1* 50 AL XLPE 6/10 trefoil | YMeKrvas 6/10 kV 1x 50 Al
3x1* 50 AL XLPE 6/10 flat | YMeKrvas 6/10 kV 1x 50 Al
3x1* 95 AL XLPE 6/10 trefoil | YMeKrvas 6/10 kV 1x 95 Al
3x1* 95 AL XLPE 6/10 flat | YMeKrvas 6/10 kV 1x 95 Al
3x1*150 AL XLPE 6/10 trefoil | YMeKrvas 6/10 kV 1x150 Al
3x1*150 AL XLPE 6/10 flat | YMeKrvas 6/10 kV 1x150 Al
3x1*240 AL XLPE 6/10 trefoil | YMeKrvas 6/10 kV 1x240 Al
3x1*240 AL XLPE 6/10 flat | YMeKrvas 6/10 kV 1x240 Al
3x1*400 AL XLPE 6/10 trefoil | YMeKrvas 6/10 kV 1x400 Al
3x1*400 AL XLPE 6/10 flat | YMeKrvas 6/10 kV 1x400 Al
3x1*630 AL XLPE 6/10 trefoil | YMeKrvas 6/10 kV 1x630 Al
3x1*630 AL XLPE 6/10 flat | YMeKrvas 6/10 kV 1x630 Al
3x1* 50 AL XLPE 8,7/15 trefoil | YMeKrvas 8,7/15 kV 1x 50 Al
3x1* 50 AL XLPE 8,7/15 flat | YMeKrvas 8,7/15 kV 1x 50 Al
3x1* 95 AL XLPE 8,7/15 trefoil | YMeKrvas 8,7/15 kV 1x 95 Al
3x1* 95 AL XLPE 8,7/15 flat | YMeKrvas 8,7/15 kV 1x 95 Al
3x1*150 AL XLPE 8,7/15 trefoil | YMeKrvas 8,7/15 kV 1x150 Al
3x1*150 AL XLPE 8,7/15 flat | YMeKrvas 8,7/15 kV 1x150 Al
3x1*240 AL XLPE 8,7/15 trefoil | YMeKrvas 8,7/15 kV 1x240 Al
3x1*240 AL XLPE 8,7/15 flat | YMeKrvas 8,7/15 kV 1x240 Al
3x1*400 AL XLPE 8,7/15 trefoil | YMeKrvas 8,7/15 kV 1x400 Al
3x1*400 AL XLPE 8,7/15 flat | YMeKrvas 8,7/15 kV 1x400 Al
3x1*630 AL XLPE 8,7/15 trefoil | YMeKrvas 8,7/15 kV 1x630 Al
3x1*630 AL XLPE 8,7/15 flat | YMeKrvas 8,7/15 kV 1x630 Al
3x1* 95 AL XLPE 12/20 trefoil | YMeKrvas 12/20 kV 1x 95 Al
3x1* 95 AL XLPE 12/20 flat | YMeKrvas 12/20 kV 1x 95 Al
3x1*150 AL XLPE 12/20 trefoil | YMeKrvas 12/20 kV 1x150 Al
3x1*150 AL XLPE 12/20 flat | YMeKrvas 12/20 kV 1x150 Al
3x1*240 AL XLPE 12/20 trefoil | YMeKrvas 12/20 kV 1x240 Al
3x1*240 AL XLPE 12/20 flat | YMeKrvas 12/20 kV 1x240 Al
3x1*400 AL XLPE 12/20 trefoil | YMeKrvas 12/20 kV 1x400 Al
3x1*400 AL XLPE 12/20 flat | YMeKrvas 12/20 kV 1x400 Al
3x1*630 AL XLPE 12/20 trefoil | YMeKrvas 12/20 kV 1x630 Al
3x1*630 AL XLPE 12/20 flat | YMeKrvas 12/20 kV 1x630 Al
3x1*800 AL XLPE 12/20 trefoil | YMeKrvas 12/20 kV 1x800 Al
3x1*800 AL XLPE 12/20 flat | YMeKrvas 12/20 kV 1x800 Al
3x1*150 AL XLPE 18/30 trefoil | YMeKrvas 18/30 kV 1x150 Al
3x1*150 AL XLPE 18/30 flat | YMeKrvas 18/30 kV 1x150 Al
3x1*240 AL XLPE 18/30 trefoil | YMeKrvas 18/30 kV 1x240 Al
3x1*240 AL XLPE 18/30 flat | YMeKrvas 18/30 kV 1x240 Al
3x1*400 AL XLPE 18/30 trefoil | YMeKrvas 18/30 kV 1x400 Al
3x1*400 AL XLPE 18/30 flat | YMeKrvas 18/30 kV 1x400 Al
3x1*630 AL XLPE 18/30 trefoil | YMeKrvas 18/30 kV 1x630 Al
3x1*630 AL XLPE 18/30 flat | YMeKrvas 18/30 kV 1x630 Al
3* 50 CU XLPE 6/10 | VGYMvKrvasmb 6/10 kV 3x 50 as50
3* 95 CU XLPE 6/10 | VGYMvKrvasmb 6/10 kV 3x 95 as50
3*150 CU XLPE 6/10 | VGYMvKrvasmb 6/10 kV 3x150 as50
3*185 CU XLPE 6/10 | VGYMvKrvasmb 6/10 kV 3x185 as50
3*240 CU XLPE 6/10 | VGYMvKrvasmb 6/10 kV 3x240 as50
3* 50 CU XLPE 8,7/15 | VGYMvKrvasmb 8,7/15 kV 3x 50 as50
3* 95 CU XLPE 8,7/15 | VGYMvKrvasmb 8,7/15 kV 3x 95 as50
3*150 CU XLPE 8,7/15 | VGYMvKrvasmb 8,7/15 kV 3x150 as50
3* 50 CU XLPE 12/20 | VGYMvKrvasmb 12/20 kV 3x 50 as50
3* 95 CU XLPE 12/20 | VGYMvKrvasmb 12/20 kV 3x 95 as50
3*150 CU XLPE 12/20 | VGYMvKrvasmb 12/20 kV 3x150 as50